WO-11290116 | 104176765 | 2023-09-21 13:20 | 2023-09-21 |  | 2023-09-21 12:27 | Leonardo EV,DX,R22,EC Fan,TDAV0511A,Downflow Without Heater & Humidifier | TDAV0511AN001 | TDAV0511AN001 | ZK1331002746 | Wo request Under AMC P:EVD issue S:AMC | 2023-09-21 | 2023-09-24 09:11 | No | Contract | Reliance Jio Infocomm Ltd. | AG1 Metro Chinna Chowk | Kadapa | 516001 | Andhra Pradesh | India FS South1 Cooling CSP RK Cooling Enterprises Hyderabad | Kalakoti Manik_RK Cooling Enterprises Hyderabad | RK Cooling Enterprises | found the thermostatic valve not connect alarm found the that EVD problem new evd replaced now unit working fine, | Repair |  | 8- Service Completed | 2023-09-24 09:24 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 300 | INR | 300 | ENM SECURE POWER
WO-11154441 | 103475577 | 2023-08-25 12:47 | 2023-08-23 |  | 2023-08-23 15:11 | LC1E120M5 | LC1E120M5 | LC1E120M5 | 9008513544 | COMPLAINT--PLASMA--23.08.2023 LC1E120M5 operation issue Site Address: Reliance Smart Point, GF Village Ballabpur, Agartala Mouza Madhupur, Dist. W Tripura, Tehsil Surjamaninagar, Agartala- 799001 Mr. Shubham Rai- 6003901308 9287957175 | 2023-08-23 | 2023-09-15 01:30 | No | Warranty | Reliance Smart Point | GF Village Ballabpur, Agartala Mouza Madhupur, Dist. W Tripura, Tehsil Surjamaninagar | Agartala | 799001 | Tripura | India FS ED&I CSP East Team SHIV ELECTRICALS Guwahati | Parwez Alam SHIV ELECTRICALS GUWAHATI | SHIV ELECTRICALS | Replace the Contactor coil and now the contactor is working satisfactorily. | Repair |  | 9- Service Validated | 2023-09-15 13:43 |  |  | 560 | INR | 560 | ENM POWER PRODUCTS
WO-11290144 | 104177438 | 2023-09-21 14:50 | 2023-09-21 |  | 2023-09-21 12:40 | APC Symmetra RM 4kVA Scalable to 6kVA N+1 220-240V | SYH4K6RMI | SYH4K6RMI | JD0828023316 | ups is faulty Serial# JD0828023316 P:ups is faulty S:AMC | 2023-09-21 | 2023-09-27 14:56 | No | Contract | Central Board of Excise & Customs-CBEC | 02 E/01 Subhash Enclave In Front Of Air Force Central School | Jodhpur | 342011 | Rajasthan | India FS North1 HBN CSP EL-TRONICS Jodhpur | Sukhdev Bhati EL-TRONICS Jodhpur | EL-TRONIC | Power replaced successfully and UPS is working ok. | Repair |  | 10- Closed | 2023-09-27 15:04 |  |  | 25 | INR | 25 | ENM SECURE POWER
WO-11290224 | 104178165 | 2023-09-23 12:18 | 2023-09-21 |  | 2023-09-21 12:58 | APC Easy UPS Online 6000VA Indian Outlet Rackmount 230V India | SRV6KL-IN | SRV6KL-IN | 9S2018A43376 | FW: RR : IM15482444 ¦ Store Code : TGV7 ¦ SCHNEIDER ¦ KERALA -TRENDS Under AMC P: UPS not working S:AMC | 2023-09-21 | 2023-09-23 13:29 | No | Contract | Reliance Retail Limited | RRL TST Vadakkanchery, Veeva Tower, Vadakkanchery, Near police Station | Palakkad | 678683 | Kerala | India FS South2 HBN CSP AutopowerSystems&Solutions Kochi | JITHIN CHANDRAN AutopowerSystems&Solutions Kochi | AUTOPOWER SYSTEMS & SERVICES | need to battery pack | Repair |  | 10- Closed | 2023-09-23 13:44 |  |  | 110 | INR | 110 | ENM SECURE POWER
WO-11290225 | 104177947 | 2023-09-27 12:18 | 2023-09-21 |  | 2023-09-21 12:59 | APC Smart-UPS RC 6000VA 230V for India - No Batteries | SRC6000UXI | SRC6000UXI | 6S1251Z00017 | FW: CALL ID:INC0004427182 P: Chargeable basis case logged for 1time UPS checking (mention serial number of 6S1251Z00017) No Spares support APC will Pay the charges S: Chargeable basis case logged for 1time UPS checking : (mention serial number of 6S1251Z00017) | 2023-09-21 | 2023-09-27 16:51 | No | Commercial Action - Sales | HDFC Bank Ltd | Shop No 101 to 103, First Floor, Shree Shankheshwar Complex | Amalsad | 396310 | Gujarat | India FS West2 HBN CSP_Nutech Sales & Support Surat | Amit Parmar Nutech Sales & Support Surat | Nutech Sales & Support | Checked and found ups working ok online to battery teat on load with remaining 2Hour and 20min approx. backup no issue found in ups. | Repair |  | 10- Closed | 2023-09-27 16:54 |  |  | 70 | INR | 70 | ENM SECURE POWER
WO-11284040 |  | 2023-09-20 11:15 | 2023-09-20 |  | 2023-09-20 10:47 | Leonardo EVDXR407cEC FanTUAV0611AUpflow With Heater Humidifier & Damper | TUAV0611AN004 | TUAV0611AN004 | JK2313001530 | PM | 2023-09-20 | 2023-09-20 11:17 | No | Commercial Action - Sales | Orient Fashion Exports India Pvt Ltd | E-45/14, PHASE-II, OKHLA INDUSTRIAL AREA null | New Delhi | 110020 | Delhi | India FS North1 Cooling CSP Hitech solutions New Delhi | Ashwani Kumar_Hitech solutions New Delhi | Hitech Solutions-New Delhi-Delhi | Preventive Maintenance done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-20 11:45 |  |  | 39 | INR | 39 | ENM SECURE POWER
WO-11290253 | 104176970 | 2023-09-21 13:46 | 2023-09-21 |  | 2023-09-21 13:13 | SRCE6KUXIQ | SRCE6KUXIQ | SRCE6KUXI | BQ1919007503 | Call id INC0004532568 1. Asset Code : 2985-4002 2. Serial Number : BQ1919007503 3. Type : UPS / UPS-Battery 4. Make & Model : APC-Schneider / APC 6 KVA UPS 5. WSD : May 2, 2013, 10:00 AM 6. WED : May 1, 2016, 10:00 AM 7. Asset status as per SCCD : Activ P:UPS Battery Backup issue S:AMC | 2023-09-21 | 2023-09-25 17:15 | No | Contract | HDFC Bank Ltd | HDFC Bank Khasra No-1340 Village Sherpur Opp Syndicate Bank Hathras Road Sadabad Location Code 2985 Pragtipuram Murshan Road | Sadabad | 281306 | Uttar Pradesh | India FS North2 HBN CSP MUKUL COMPUTERS Agra | Faizan F_Mukul Computers Agra | MUKUL COMPUTERS - AGRA - LUCKNOW | ups proper working in mains mode , two number battery faulty 26 ah 12 | Repair |  | 10- Closed | 2023-09-25 17:33 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11290283 | 104178810 | 2023-09-23 11:39 | 2023-09-21 |  | 2023-09-21 13:18 | APC Symmetra LX 16kVA N+1 Tower Frame, 220/230/240V or 380/400/415V | SYAF16KI | SYAF16KI | QD0813180005 | FW: IM03026428 TN-CBE-03 UPS BATTERY ISSUE Site code: IM03026428 TN-CBE-03 UPS BATTERY ISSUE Serial# QD0813180005 P: Battery module issue in ups S: AMC | 2023-09-21 | 2023-09-26 18:10 | No | Contract | Central Board of Excise & Customs-CBEC | Office of the Assistant Commissioner of customes Inland container Depot RACECOURSE ROAD | Coimbatore | 641018 | Tamil Nadu | India FS South2 HBN CSP GRControlSystems Coimbatore | Edison V GRControlSystems Coimbatore | GR Control Systems-Coimbatore | Battery Module Connector loose connection rectified now unit working fine call closed | Repair |  | 10- Closed | 2023-09-26 18:17 |  |  | 19 | INR | 19 | ENM SECURE POWER
WO-11290291 | 104179057 | 2023-09-21 15:25 | 2023-09-21 |  | 2023-09-21 13:22 | Leonardo EV,DX,R410a,EC Fan,TDAV0921A,Downflow With Heater & Hum | TDAV0921AN003 | TDAV0921AN003 | NUCX4942 | Cooling Issue S:AMC | 2023-09-21 | 2023-09-21 19:48 | No | Contract | TCS E-Serve Ltd | TEK Tower | Chennai | 600032 | Tamil Nadu | India FS South4 Cooling CSP Unity Air conditioning Engineers Chennai | V Ramkumar_ Unity Air conditioning Engineers Chennai | UNITY AIRCONDITIONING ENGINEERS | L.P alarm : Now we checked and found gas leakage near the dryer. We arrested the leakage N2 pressure holding, Vacuuming and recommissioning the unit. | Repair |  | 10- Closed | 2023-09-21 19:55 |  |  | 25 | INR | 25 | ENM SECURE POWER
WO-11285452 |  | 2023-09-25 11:43 | 2023-09-20 |  | 2023-09-20 14:04 | InRow RD 300mm Air Cooled 220-240V 50Hz | ACRD101 | ACRD101 | JK2308000443 | Assessment & Inspection | 2023-09-20 | 2023-09-25 11:54 | No | Warranty | Johnson & Johnson Private Limited | Helios Business Park, Tower E, 9th Floor Sarjaupra Marathahalli Outer Ring Road, Varthur Hobli null | Bangalore | 560103 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Diwakar J_UCS Projects and services Bangalore | UCS Projects & Services | Unit pm successfully | Assessment/ Inspection | Data Collection | 8- Service Completed | 2023-09-25 11:56 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11290304 | 104179125 | 2023-09-21 15:43 | 2023-09-21 |  | 2023-09-21 13:25 | APC Symmetra LX 16kVA Scalable to 16kVA N+1 Rack-mount, 220/230/240V or 380/400/ | SYA16K16RMI | SYA16K16RMI | QD0824160089 | FW: IM03026431 AP-GNT-01 UPS BATTERY AND POWER MODULE ISSUE Site code: IM03026431 AP-GNT-01 UPS BATTERY AND POWER MODULE ISSUE Serial# QD0824160089 P: UPS battery and power module issue S: AMC | 2023-09-21 | 2023-09-27 15:44 | No | Contract | Central Board of Excise & Customs-CBEC | P.B.NO. 331 C.R.BUILDING KANNAVARI THOTA GUNTUR COLLECTORATE | Guntur | 522001 | Andhra Pradesh | India FS South3 HBN CSP LaserSystemsPvtLtd Vijayawada | Venakt Ram LaserSystemsPvtLtd Vijayawada | Laser Systems Limited - Vijayawada - Hyderabad | BATTERY MODULES REPLACED,NOW UNIT WORKING FINE ON BOTH MODES REPLACED SYBT5-IN-5D233T38790,5D2330T59586 | Repair |  | 10- Closed | 2023-09-27 17:00 |  |  | 55 | INR | 55 | ENM SECURE POWER
WO-11285453 |  | 2023-09-25 11:46 | 2023-09-20 |  | 2023-09-20 14:06 | InRow RD 300mm Air Cooled 220-240V 50Hz | ACRD101 | ACRD101 | JK2308000446 | Assessment & Inspection | 2023-09-20 | 2023-09-25 11:58 | No | Warranty | Johnson & Johnson Private Limited | Helios Business Park, Tower E, 9th Floor Sarjaupra Marathahalli Outer Ring Road, Varthur Hobli null | Bangalore | 560103 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Diwakar J_UCS Projects and services Bangalore | UCS Projects & Services | Unit observation done | Assessment/ Inspection | Data Collection | 8- Service Completed | 2023-09-25 12:00 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11290325 | 104179386 | 2023-09-22 09:53 | 2023-09-21 |  | 2023-09-21 13:32 | APC SYMMETRA RM 6KVA N+1 FRAME 220-240V EXCLUDING RAIL KIT | SYHF6KI-D | SYHF6KI-D | JD0826009330 | FW: IM03026969 TN/ARI/01 UPS NOT WORKING Site code: IM03026969 TN/ARI/01 UPS NOT WORKING Serial# JD0826009330 Standby unit: BQ1309000445 P: UPS is not working- Service needed for standby unit S: AMC | 2023-09-21 | 2023-09-26 00:54 | No | Contract | Central Board of Excise & Customs-CBEC | No 5 Opillatha Amman Koil St | Ariyalur | 608703 | Tamil Nadu | India FS South2 HBN CSP UpservePowerSystems Trichy | K RAJA UpservePowerSystems Trichy | Upserve Powersystems-Tirchy | battery module replacement ups working fine | Repair |  | 10- Closed | 2023-09-26 15:59 |  |  | 110 | INR | 110 | ENM SECURE POWER
WO-11158218 | 103411725 | 2023-08-24 11:41 | 2023-08-24 |  | 2023-08-24 11:29 |  |  |  |  | RMA_103411725 RO_ 61342458 | 2023-08-24 | 2023-09-27 12:00 | No | Warranty | Om Prakash Power System Pvt. Ltd.(992) | Shop No. 12,Harivansh Parawati Complex, Jamal Road, | Patna | 800001 | Bihar | India FS ED&I CSP East Team Vidya Enterprises Lucknow | Shubrat Shukla_Vidya Enterprises Lucknow | Vidya Enterprises | As per customer complaint dealer is send the faulty material at office against the assessment and inspection of work order. e check the material found faulty. So as disuses with internal team all material is faulty so need to book at dealer stock. =S= Free Order 226085005 has been saved | Assessment/ Inspection | Data Collection | 8- Service Completed | 2023-09-27 21:31 | =S= Free Order 226085005 has been saved |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11285459 |  | 2023-09-25 11:47 | 2023-09-20 |  | 2023-09-20 14:07 | InRow RD 300mm Air Cooled 220-240V 50Hz | ACRD101 | ACRD101 | JK2308000452 | Assessment & Inspection | 2023-09-20 | 2023-09-25 12:00 | No | Warranty | Johnson & Johnson Private Limited | Helios Business Park, Tower E, 9th Floor Sarjaupra Marathahalli Outer Ring Road, Varthur Hobli null | Bangalore | 560103 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Diwakar J_UCS Projects and services Bangalore | UCS Projects & Services | Unit observation done | Assessment/ Inspection | Data Collection | 8- Service Completed | 2023-09-25 12:03 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11290347 | 104179654 | 2023-09-22 11:53 | 2023-09-22 | INSTALLATION | 2023-09-21 13:40 | APC Smart-UPS VT 40kVA 400V, Internal Maintenance Bypass | SUVT40KH | SUVT40KH | PS0636340415 | FW: UPS: BPE ll Br code: 123 ll Br name: MADURAI ¦¦ Call id: INC0004547411 ll UPS Issue P:UPS Issue S:AMC | 2023-09-21 | 2023-09-22 14:19 | No | Contract | HDFC Bank Ltd | HDFC Bank 7A Ground FloorNo-34 KrishnarayarTank Street West Velli Street Srinath Kalyani Tower Opp Railway Junction | Madurai | 625001 | Tamil Nadu | India FS South2 HBN CSP TechQPowerControls Madurai | M.S.Karthik TechQPowerControls Madurai | Tech Q Power Controls-Madhurai | POWER MODULE INSTALLATION DONE, UPS GOOD WORKING, S.R.NO.QS2324150322. | Repair |  | 10- Closed | 2023-09-22 14:22 |  |  | 15 | INR | 15 | ENM SECURE POWER
WO-11158857 | 103512580 | 2023-08-25 10:21 | 2023-08-24 |  | 2023-08-24 15:49 | C25B3TM250 | C25B3TM250 | C25B3TM250 | 10-2022-W37 5-9523L3 | service complient C25B3TM250 - 10-2022-W37 5-9523L3 total 3 no's having pole continuity issue please visit on per-intimation Site Address: Hindustan Shipyard Limited. DDSR ? Purchase, HSL, Vizag 530005 Andhra Pradesh Mr. P siva phanindra ph no 9848523264 | 2023-08-24 | 2023-09-01 10:58 | No | Warranty | Hindustan Shipyard Limited. | DDSR ? Purchase, HSL, Gandhipuram | Vizag | 530005 | Andhra Pradesh | India FS ED&I CSP South Team Voltamp Electrical Works Visakhapatnam | Chinni SaiKumar_VOLT AMP ELECTRICAL WORKS Visakhapatnam | Voltamp Electrical Works | Visited the site and found above the compact NSX250A 3P 25KA MCCB tripping issue so today we have observed the problem of MCCB on load time generating spark and same time MCCB is tripped. so we observed the MCCB out side is ok but MCCB in side out put terminal in side flash moisture identified so we collect the motor details so zvo material replaced so close issue | Repair |  | 9- Service Validated | 2023-09-01 11:02 |  |  | 20 | INR | 20 | ENM POWER PRODUCTS
WO-11290395 | 104180353 | 2023-09-21 14:13 | 2023-09-21 |  | 2023-09-21 14:01 | SURT6000XLI-CC | SURT6000XLI-CC | SURT6000XLI-CC | B21943003182 | FW: [External] RE: RR ID : IM15480515 ¦ Store Code : TCT2 ¦ Schneider Under AMC P:UPS not powering on S:AMC | 2023-09-21 | 2023-09-21 19:25 | No | Contract | Reliance Retail Limited | , TRENDS EXPRESS, MVS BUILDING TOWN HALL JUNCTION HARIPAD MUNICIPAL OFFICE, HARIPAD | HARIPAD | 690514 | Kerala | India FS South3 HBN CSP SpectraElectronics Alappuzha | Siji Oommen SpectraElectronics Alappuzha | Spectra Electronics-Alleppy | Battery issue informed customer to replace battery | Repair |  | 10- Closed | 2023-09-22 10:56 |  |  | 15 | INR | 15 | ENM SECURE POWER
WO-11286152 | 104155584 | 2023-09-20 18:31 | 2023-09-20 |  | 2023-09-20 17:24 | Easy UPS 3S 20 kVA 400 V 3:1 UPS for external batteries | E3SUPS20K3I | E3SUPS20K3I | 9E2114T12350 | DOP : AMC P : High DC BUS Voltage T: Checked UPS and tray to clear alarm however alarm is not clearing. S : AMC/SIB | 2023-09-20 | 2023-09-22 10:37 | No | Contract | Apollo Pipes Ltd | A- 140, Sector 136. Noida, Uttar Pradesh- 201301 | Noida | 201301 | Uttar Pradesh | India FS North1 HBN CSP Martech Systems & Services Noida | Uttam Yadav_Martech Systems & Services Noida | Martech Systems & Services-Noida | 0J-12029-00820 9E2215T12713 Part replaced at site so call closed | Repair |  | 10- Closed | 2023-09-22 10:40 |  |  | 22 | INR | 22 | ENM SECURE POWER
WO-11290427 | 104180946 | 2023-09-21 16:27 | 2023-09-21 |  | 2023-09-21 14:18 | APC Smart-UPS RT 10000VA 230V Harsh Environment | SURT10000XLI | SURT10000XLI | B21317000619 | FW: [External]RE: RR : IM15481077 ¦ Store Code : 8332 ¦ SCHNEIDER ¦ TELANGANA -TRENDS Under AMC P: UPS not Powering on S:AMC | 2023-09-21 | 2023-09-21 18:33 | No | Contract | Reliance Retail Ltd | SURVEY NO 1508&1509 PRASHANTH¿ NAGAR MAIN ROAD BESIDE SIDDEPET BUS STAND SIDDEPET | Medak | 502103 | Telangana | India FS South3 HBN CSP CENTRALDATASYSTEMS HYDERABAD | Nagesh CENTRALDATASYSTEMS HYDERABAD | Central Data Systems Pvt Ltd | Visited site and found battery issue battery need to replace RBC44-4 nos | Repair |  | 10- Closed | 2023-09-21 18:40 |  |  | 26 | INR | 26 | ENM SECURE POWER
WO-11288800 |  | 2023-09-29 09:33 | 2023-09-02 |  | 2023-09-21 05:24 | APC Symmetra LX 16kVA N+1 Ext. Run Tower Frame, 220/230/240V or 380/400/415V | SYAF16KXR9I | SYAF16KXR9I | QD0827360113 | Preventive Maintenance/Regular Preventive Maintenance | 2023-09-21 | 2023-09-29 13:00 | No | Contract | Central Board of Excise & Customs-CBEC | C R Building The Mall Amritsar HO null | Amritsar | 143502 | Punjab | India FS North2 HBN CSP Crest & Company Chandigarh | Pavittar Singh_Crest & Company Jalandhar | Crest & Company - Jalandhar - Chandigarh | ups Preventive maintenance is done at site during PM checked ups all parameters after PM ups working fine on main and batteries mode checked by customer call closed | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-29 13:48 |  |  | 85 | INR | 85 | ENM SECURE POWER
WO-11288787 |  | 2023-09-29 10:28 | 2023-09-02 |  | 2023-09-21 05:20 | APC Symmetra LX 16kVA N+1 Ext. Run Tower Frame, 220/230/240V or 380/400/415V | SYAF16KXR9I | SYAF16KXR9I | QD0824160102 | Preventive Maintenance/Regular Preventive Maintenance | 2023-09-21 | 2023-09-29 13:47 | No | Contract | Central Board of Excise & Customs-CBEC | O/o Asst.Commissioner Pacific City Center 3rd Floor Near Jat Bhawan Norhtem Bye Pass null | Rohtak | 124001 | Haryana | India FS North2 HBN CSP Microvolt Communication Pvt Ltd Rohtak | Naveen N_Microvolt Communication Pvt Ltd Rohtak | Microvolt Communication Pvt. Ltd. - Rohtak - Chandigarh | pm service was done and working ok | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-29 13:49 |  |  | 3 | INR | 3 | ENM SECURE POWER
WO-11288790 |  | 2023-09-29 11:11 | 2023-09-02 |  | 2023-09-21 05:21 | APC Symmetra LX 16kVA N+1 Tower Frame, 220/230/240V or 380/400/415V | SYAF16KI | SYAF16KI | QD0824160083 | Preventive Maintenance/Regular Preventive Maintenance | 2023-09-21 | 2023-09-29 11:14 | No | Contract | Central Board of Excise & Customs-CBEC | 32 OB Real Head Complex null | Jammu | 180012 | Jammu and Kashmir | India FS North2 HBN CSP S & S Computers_Jammu | Vivek Kumar S & S Computers_Jammu | S & S Computer Services | Site visit and PM Activity done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-29 11:39 |  |  | 6 | INR | 6 | ENM SECURE POWER
WO-11159064 | 103519352 | 2023-08-25 10:55 | 2023-08-24 |  | 2023-08-24 17:30 | NA06304V | NA06304V | NA06304V | 2221390057 | Dear Sir, 630A ATS does not work in auto mode. Cat. No. : WATSN630/4AV MANUFACTURING NO: 2221390057 Supplier Name: Global Incorporates Invoice No. : 1602/22-23 Invoice date: 16-03-2023 We request to send a person as soon as possible to the following address. Reliance smart up, Near Reliance jewels, Shokat ali road, Rampur, Uttar Pradesh -332719 Site Contact person: Mr . Pradeep Choudhary 99719 71568 Thanks & Regards Machhindranath Parkar Address- Unit No. 9/10/11 Ankit Ind. Estate, Sativali, Vasai(E), Pin- 401208, | 2023-08-24 | 2023-09-01 10:19 | No | Warranty | Reliance Smart UP | Near Reliance jwells, Shokat ali road, | Rampur | 244901 | Uttar Pradesh | India FS ED&I CSP North Team Total Solution Services Delhi | Rahul Kumar Total Solution Services Delhi | Total Solution Services(500054203) | We Have Visit the Site and Replace the 1 NOS ATS and Fitment the ATS and ATS Working Ok Auto and Manual Mode And Defective ATS Received | Repair |  | 9- Service Validated | 2023-09-01 10:29 |  |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11288796 |  | 2023-09-27 15:29 | 2023-09-02 |  | 2023-09-21 05:23 | APC Symmetra LX 16kVA Scalable to 16kVA N+1 Rack-mount, 220/230/240V or 380/400/ | SYA16K16RMI | SYA16K16RMI | QD0824160104 | Preventive Maintenance/Regular Preventive Maintenance | 2023-09-21 | 2023-09-27 15:45 | No | Contract | Central Board of Excise & Customs-CBEC | Plot No. 155, Sector P-34, NH Jaishta & Vishakha, CIDCO, Nashik null | Nashik | 400013 | Maharashtra | India FS West1 HBN CSP_RACCA INFOTECH PVT LTD Nasik | Nitin Aher RACCA INFOTECH PVT LTD Nasik | Racca Infotech Pvt Ltd | UPS Preventive Maintenance Done. UPS Working Ok | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-27 16:02 |  |  | 10 | INR | 10 | ENM SECURE POWER
WO-11288807 |  | 2023-09-29 11:24 | 2023-09-02 |  | 2023-09-21 05:26 | APC Symmetra LX 16kVA N+1 Ext. Run Tower Frame, 220/230/240V or 380/400/415V | SYAF16KXR9I | SYAF16KXR9I | QD0826360024 | Preventive Maintenance/Regular Preventive Maintenance | 2023-09-21 | 2023-09-29 15:34 | No | Contract | Central Board of Excise & Customs-CBEC | Custom office, 12th Floor, Sector-H, Kendriya Bhawan, Aliganj 5th & 11th Floor | Lucknow | 226024 | Uttar Pradesh | India FS North2 HBN CSP BK Technologies Kanpur | Kuldeep Gutam B.K. Technologies Lucknow | BK TECHNOLOGIES | UPS PM done and working ok on both mode. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-29 15:41 |  |  | 22 | INR | 22 | ENM SECURE POWER
WO-11290684 | 104184686 | 2023-09-21 19:57 | 2023-09-22 |  | 2023-09-21 16:19 | Leonardo EV,DX,R22,EC Fan,TDAV0511A,Downflow Without Heater & Humidifier | TDAV0511AN001 | TDAV0511AN001 | ZK1331020276 | Under AMC P:zk1331020276---Compressor fault S:AMC | 2023-09-21 | 2023-09-23 17:09 | No | Contract | Reliance Jio Infocomm Ltd. | Plot No : AG2 sathya moorthy nagar, Tiruvottiyur | Chennai | 600019 | Tamil Nadu | India FS South4 Cooling CSP Unity Air conditioning Engineers Chennai | V Ramkumar_ Unity Air conditioning Engineers Chennai | UNITY AIRCONDITIONING ENGINEERS | Compressor contactor failure : Now we checked and found compressor contactor failure in the unit. now we changed the new contactor and observe unit working normal. | Repair |  | 10- Closed | 2023-09-25 17:18 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 31 | INR | 31 | ENM SECURE POWER
WO-11288808 |  | 2023-09-29 16:53 | 2023-09-02 |  | 2023-09-21 05:26 | APC SYMMETRA LX 16kVA N+1 Rack-mount Frame, 220/230/240V OR 380/400/415V | SYAF16KRMI | SYAF16KRMI | QD0827260108 | Preventive Maintenance/Regular Preventive Maintenance | 2023-09-21 | 2023-09-29 17:22 | No | Contract | Central Board of Excise & Customs-CBEC | CGST Central excise M/s Ircon International Ltd Ploat number c-232a/2 to c-232a/3 sector 48 null | Noida | 201301 | Uttar Pradesh | India FS North1 HBN CSP Martech Systems & Services Noida | Uttam Yadav_Martech Systems & Services Noida | Martech Systems & Services-Noida | UPS is lying at site in dismantled condition and not is use so call closed | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-29 21:23 |  |  | 22 | INR | 22 | ENM SECURE POWER
WO-11290686 | 104184700 | 2023-09-21 16:44 | 2023-09-21 |  | 2023-09-21 16:20 | WDF0181BN002 | WDF0181BN002 | WDF0181BN002 | ZK1537008181 | Damper Motor Broken P:Damper Motor Broken S:AMC | 2023-09-21 | 2023-09-22 12:35 | No | Contract | Reliance Jio Infocomm Ltd | Jayanta Khanikar, Vill:-Manukhuwa Gaon | Tinsukia | 786153 | Assam | India FS East Cooling CSP SYSCOMP POWERSOL Guwahati | SHUBHAM PATHAK SYSCOMP POWERSOL Guwahati | SYSCOMP POWERSOL - GUWAHATI | REPLACED THE DAMPUR MOTOR. CHECKEDALL PERAMETERS AND CLEAN ALL UNIT | Repair |  | 10- Closed | 2023-09-25 22:40 |  |  | 450 | INR | 450 | ENM SECURE POWER
WO-11290866 | 104187055 | 2023-09-21 17:53 | 2023-09-21 |  | 2023-09-21 17:48 | EFC 1.3TR, Downflow, Bottom Discharge | WDF0181BN001 | WDF0181BN001 | JK1331000204 | P:jk1331000204---Compressor fault Under AMC P:jk1331000204---Compressor fault S:AMC | 2023-09-21 | 2023-09-22 15:32 | No | Contract | Relainec Jio infocom | surajpol Ag2 | Udaipur | 313701 | Rajasthan | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Alok Sharma Freezeotech Airconditioning & Refrigeration GZB | Freezeotech Airconditioning & Refrigeration Corporation | We visited the site and found Compressor faulty it was internally burnt we and replaced the compressor we do the N2 testing and vacuumed the unit and gas charging R-22---2.4 kg now unit is working ok | Repair |  | 10- Closed | 2023-09-22 15:37 |  |  | 520 | INR | 520 | ENM SECURE POWER
WO-11290880 | 104186938 | 2023-09-22 10:55 | 2023-09-21 |  | 2023-09-21 17:54 | SRC3KUXIQ | SRC3KUXIQ | SRC3KUXI | bq1713000817 | FW: Reg-UPS POWER ISSUE S:UPS | 2023-09-21 | 2023-09-23 15:56 | No | Contract | ITC Ltd | M/s. Truckers India. Plot No, 10& 13, Analapatna Industrial Estate, Chandaka, Khurda, | Khurda | 754005 | Odisha | India FS East HBN CSP Disha Computers Bhubneshwar | SUJIT SENAPATI Disha Computers Bhubneshwar | Disha Computers-Bhubaneshwar | PM SERVICE DONE NOW UPS OK | Repair |  | 10- Closed | 2023-09-23 16:02 |  |  | 18 | INR | 18 | ENM SECURE POWER
WO-11290104 | 104176574 | 2023-09-21 12:29 | 2023-09-21 |  | 2023-09-21 12:18 | Amico 6 TrR407cDXDownflow with Heater & Hum. | SDA0601AN002 | SDA0601AN002 | JK2210000008 | DOP:AMC P:PAC -Humidifier Loss of water alarm S:AMC | 2023-09-21 | 2023-09-21 17:42 | No | Contract | Doordarshan Bhawan | Copernicus Marg, Mahatma Jyoti Rao Phule Marg Area | New delhi | 110001 | Delhi | India FS North1 Cooling CSP Smart Engineering Services Delhi | Taranjeet Singh_Smart Engineering Services Delhi | Smart Engineering Services | VISIT AND FOUND LOSS OF WATER ISSUE IN HUMIDIFIER BOTTLE FROM CUSTOMER SIDE, INLET WATER SUPPLE CLOSED, CHECEKD ALL PARAMETERS. NOW UNIT IS WORKING OK. | Repair |  | 10- Closed | 2023-09-21 17:47 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two persons is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 25 | INR | 25 | ENM SECURE POWER
WO-11291483 | 104189196 | 2023-09-22 11:34 | 2023-09-21 |  | 2023-09-21 18:47 | SURT6000XLI-CC | SURT6000XLI-CC | SURT6000XLI-CC | B21905001951 | FW: RR : IM15483372 ¦ Store Code : TU61 ¦ SCHNEIDER ¦KARNATAKA -TRENDS Under AMC P: UPS BACKUP Issue S:AMC | 2023-09-21 | 2023-09-22 16:25 | No | Contract | Reliance Trends | Reliance Trends MEN-First Floor , Bharath Mall, Bejai Road | Mangalore | 575004 | Karnataka | India FS South1 HBN CSP MeghaAssociates Mangalore | Prashanth Anchan MeghaAssociates Mangalore | Megha Associates-Mangalore-BLR008 | Set ok, no fault found. ups working fine now. | Repair |  | 10- Closed | 2023-09-22 16:31 |  |  | 10 | INR | 10 | ENM SECURE POWER
WO-11290747 | 104185613 | 2023-09-21 21:36 | 2023-09-21 |  | 2023-09-21 16:55 | TDAV1321AN009 | TDAV1321AN009 | TDAV1321AN009 | C21844009361 | AMC P: MCB Tripping S: AMC | 2023-09-21 | 2023-09-24 12:00 | No | Contract | MindTree Limited | Plot No 150, EPIP Second Phase | Bangalore | 560066 | Karnataka | India FS South3 Cooling CSP ERIC HVAC SYSTEM Bengaluru | Freddy Dass ERIC HVAC SYSTEM Bengaluru | ERIC HVAC SYSTEM | Cooling unit rectification done. | Repair |  | 8- Service Completed | 2023-09-25 07:23 |  |  | 0 | INR | 0 | ENM SECURE POWER
WO-11291748 | 104189513 | 2023-09-21 19:23 | 2023-09-22 |  | 2023-09-21 18:55 | Std Exch APC Smart-UPS RT 10000VA 230V No Batteries | SURT10000XLINBQ | SURT10000XLINBQ | YQ0439211022 | FW: RR : IM15458562 ¦ Store Code : 8037 ¦ SCHNEIDER ¦ HARYANA -TRENDS Under AMC P: UPS BACKUP Issue S:AMC | 2023-09-21 | 2023-09-22 11:36 | No | Contract | Reliance Retail Limited | RRL Store Code U692, ward 8, Railway road, Thanesar | Kurukshetra | 136118 | Haryana | India FS North2 HBN CSP Green IT Solutions Chandigarh | Deepak Green IT Solutions Chandigarh | Green IT Solutions | Checked and found that ups working fine no available earthing | Repair |  | 10- Closed | 2023-09-22 11:40 |  |  | 130 | INR | 130 | ENM SECURE POWER
WO-11295232 | 104196596 | 2023-09-23 01:12 | 2023-09-22 |  | 2023-09-22 11:43 | PRODUCT UNIFLAIR AMICO DX SDAC0601A DFLOW R407C WITH HTR AND HUM WITH SNMP CARD | SDAQ | SDAQ | JK2308003559 | Water leakage | 2023-09-22 | 2023-09-23 01:12 | No | Warranty | TELEPERFORMANCE GLOBAL SERVICES PRIVATE LIMITED | Raheja Mindspace IT Park, Unit No.3 8Th Floor Mindspace Madhapur Rd, Opposite The Westin Hyderabad Mindspace, HITEC City, null | Hyderabad | 500081 | Telangana | India FS South3 Cooling CSP ERIC HVAC SYSTEM Hyderabad | Samir Prasad ERIC HVAC SYSTEM Hyderabad | ERIC HVAC SYSTEM | Checked and found out the problem iswater leakage issue so we have rectified the issue now the unit is working in normal condition. | Repair |  | 8- Service Completed | 2023-09-23 01:16 |  |  | 30 | INR | 30 | ENM SECURE POWER
WO-11163394 | 103550582 | 2023-08-28 23:24 | 2023-08-25 | NA | 2023-08-25 18:05 | GV2ME32 | GV2ME32 | GV2ME32 | inv | COMPLAINT FOR MPCB Dear Sir / Mam, We have purchased MPCB (GV2ME32) 24-32AMP a few months back. which has gone to the site of the panel. MPCB output is not coming on the site .so please solve this problem asap. Invoice details have been attached. and The site address is given below:- ADDRESS:- D DECORE EXPORT PVT. LTD. G7/1 TARAPUR BOISER, TARAPUR, MAHARASHTRA,401506 CONTACT PERSON:- ATUL KUMAR TIWARY MOBILE NO:- 9135869827 Thanks & Regard"s Bhupendra singh 9873235570 | 2023-08-25 | 2023-08-31 17:02 | No | Warranty | Dicitex Decor Pvt Ltd | Plot No G 15/1 Midc Industrial Area Boisar null | Thane | 401506 | Maharashtra | India FS ED&I CSP West Team Kanekar Consulting Engineers Pvt Ltd Thane | Nitin Arote_Kanekar Consulting Mumbai | Kanekar Consulting Engineers Pvt. Ltd. | Check & found pole open problem need to be replaced MPCB | Repair |  | 9- Service Validated | 2023-09-01 15:23 | =S= Consig Fill up 226005524 |  | 72 | INR | 72 | ENM POWER PRODUCTS
WO-11167339 | 103570526 | 2023-08-28 17:38 | 2023-08-30 |  | 2023-08-26 15:23 | LC1G265KUEN | LC1G265KUEN | LC1G265KUEN | LJ22222700100073 | 185A & 250A, 3P POWER CONTACTORS ARE NOT WORKING AT SITE | 2023-08-26 | 2023-09-06 17:00 | No | Warranty | PCBL (TN) Limited (Chennai _ EPC) | No A-7, SIPCOT Industrial Park, Thervoy Kandigai, Gummidipoondi Taluk, | Tiruvallur | 601202 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Site Visit Done | Repair |  | 9- Service Validated | 2023-09-06 18:35 |  |  | 67 | INR | 67 | ENM POWER PRODUCTS
WO-11125646 |  | 2023-09-30 20:55 | 2023-09-30 |  | 2023-08-16 12:06 | EFC MONOBLOCK 1.3TR R410A START KIT RS485 SEQ CONTROL | WDF0181BN040-1 | WDF0181BN040-1 | JK2046002176 | PM | 2023-08-16 | 2023-09-30 18:00 | No | Commercial Action - Sales | Reliance Jio Infocomm Limited, | 4th Floor, Pavan City, Meghraj Road, Modasa ? District ? Arvalli null | Aravalli | 383315 | Gujarat | India FS West2 Cooling CSP Comfort HVAC Solutions Ahd | Rajesh Pramanik_Comfort HVAC Solutions Ahd | Comfort HVAC Solutions | Preventive Maintenance done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-30 20:58 |  |  | 125 | INR | 125 | ENM SECURE POWER
WO-11302107 | 104230846 | 2023-09-25 10:34 | 2023-09-23 |  | 2023-09-23 20:36 | Easy UPS 3S 15 kVA 400 V 3:3 UPS for external batteries | E3SUPS15KH | E3SUPS15KH | 9E2136T11047 | Dust Filter Check Required,he alarm is beeping continuously | 2023-09-23 | 2023-09-26 18:58 | No | Contract | Oil India Limited | Electrical Department, | Duliajan | 786602 | Assam | India FS East HBN CSP SYSCOMP POWERSOL Guwahati | Gurudas Mukherjee SYSCOMP POWERSOL Guwahati | SYSCOMP POWERSOL - GUWAHATI | found dust filter alarm, dust filter alarm is not in scope of APC. UPS is working properly. | Repair |  | 10- Closed | 2023-09-26 19:00 |  |  | 470 | INR | 470 | ENM SECURE POWER
WO-11172778 | 103577234 | 2023-08-31 15:03 | 2023-08-28 |  | 2023-08-28 12:46 | GCR_LC1E | GCR_EASYPACT | GCR_EASYPACT | LAEN11 8C2229 | Contactor Problem Dear sir Please find the details and solve the problem immediately.I am very sad . Please I request you immediately solve my problem. Thanks & Regards Mohan Yadav Add.- Super market Paota, Near National Highway No.08, Paota, Jaipur Rajasthan 303106 | 2023-08-28 | 2023-09-07 16:23 | No | Warranty | Super Market Grocery Supplies Pvt Ltd | 20, Near National Highway No.08 Paota SP 2033 Seethapur Ext | Jaipur | 303106 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Amarjeet Singh Sharma Electric Jaipur | Sharma Electric Works | Checked the contactor found coil not working, Hence faulty replaced. LAEX12M7 - 2 nos Email : id not provided by customer . | Repair |  | 9- Service Validated | 2023-09-09 16:27 |  |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11302119 | 104230858 | 2023-09-25 10:30 | 2023-09-23 |  | 2023-09-23 20:41 | Easy UPS 3S 15 kVA 400 V 3:3 UPS for external batteries | E3SUPS15KH | E3SUPS15KH | 9E2144T11078 | Dust Filter Check Required " ,, the alarm is beeping continuously | 2023-09-23 | 2023-09-26 18:54 | No | Contract | Oil India Limited | Electrical Department, | Duliajan | 786602 | Assam | India FS East HBN CSP SYSCOMP POWERSOL Guwahati | Gurudas Mukherjee SYSCOMP POWERSOL Guwahati | SYSCOMP POWERSOL - GUWAHATI | found dust filter alarm, dust filter alarm is not in scope of APC. UPS is working properly. | Repair |  | 10- Closed | 2023-09-26 18:56 |  |  | 470 | INR | 470 | ENM SECURE POWER
WO-11177330 | 103593483 | 2023-08-29 15:03 | 2023-08-29 |  | 2023-08-29 10:38 | LC1E80004M5WBIN | LC1E80004M5WBIN | LC1E80004M5WBIN | 8C22421 | Complaint of contactor As Per The serial number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Wunder Controls & Switchgear (P) Ltd. Plot No.17, Saroorpur Industrial Area , Sohna Road, Faridabad, Haryana 121001 India Faridabad 121001 Haryana India Contact Person Details:- Contact Person ? Ankit Jindal 9212780752 Product and Issue:- LC1E80004M5WBIN CONTACTOR 110A FOUR POLE B phase screw Issue, Not opening. | 2023-08-29 | 2023-09-12 15:56 | No | Warranty | Wunder Controls & Switchgear (P) Ltd. | Plot No.17, Saroorpur Industrial Area , Sohna Road, Faridabad, Haryana 121001 India | Faridabad | 121001 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the contactor found terminal screw free, Hence faulty replaced. LC1E8004M5WB - 1 nos Email : id not provided by customer . | Repair |  | 9- Service Validated | 2023-09-13 16:01 |  |  | 45 | INR | 45 | ENM POWER PRODUCTS
WO-11302254 | 104231458 | 2023-09-25 17:37 | 2023-09-24 |  | 2023-09-24 11:41 | TDCVQ | TDCVQ | TDCVQ | C21943002400 | PAC Valve Actuator issue | 2023-09-24 | 2023-09-28 18:00 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | Actuator replacement. | Repair |  | 8- Service Completed | 2023-09-28 18:04 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11178231 | 103596626 | 2023-08-29 15:29 | 2023-08-29 |  | 2023-08-29 11:20 | LV510305 | LV510305 | LV510305 | 10-2023-W22-1-7085L3 | LV510305_MCCB getting tripped when fixed into panel -- Reg LV510305 - 10-2023-W22-1 operating mechanism issue Site Address: Amara Raja Power Systems Limited, Besides Renigunta Cuddapah High Way, Karakambadi Village & Post, Renigunta Mandal, TIRUPATI. PIN: 517520 Contact Person (At site) : Mr.VVH Bhushan Contact No: 0- 99639 68910 | 2023-08-29 | 2023-09-01 15:00 | No | Warranty | Amara Raja Power Systems Ltd | TPT1102,Renigunta-Cudapa Road Karakambadi Village & Post Renigunata Mandal,Chittor District | Tirupati | 517425 | Andhra Pradesh | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Site Visit Done | Repair |  | 9- Service Validated | 2023-09-01 15:26 |  |  | 140 | INR | 140 | ENM POWER PRODUCTS
WO-11302256 | 104231467 | 2023-09-24 13:53 | 2023-09-24 |  | 2023-09-24 11:53 | Leonardo EVDXR407cEC FanTDAV0921ADownflow With Heater & Hum | TDAV0921AN002 | TDAV0921AN002 | C21744000011 | TDAV: Breakdown | 2023-09-24 | 2023-09-24 23:20 | No | Contract | Garden Reach Shipbuilders & Engineers Ltd. | 43/46 Park, Garden Reach Road | Kolkata | 700024 | West Bengal | India FS East Cooling CSP Snow Point Kolkata | Laxmikant Dhang_Snow Point Kolkata | Snow Point | POWER AFTER FAILUAR UNIT ONE MANUALLY OFF.DISPLAY SETTING CHECKED.DISPLAY SETTING PROBLEM SOLVED.ALL PARAMETER CHECKED.MACHINE OK RUNNING. | Repair |  | 10- Closed | 2023-09-24 23:25 |  |  | 30 | INR | 30 | ENM SECURE POWER
WO-11302269 | 104230299 | 2023-09-24 14:12 | 2023-09-24 |  | 2023-09-24 12:32 | UnisplitR40725UCA0341 Indoor (IR33 Controller) | UCA0341CWCAN2 | UCA0341CWCAN2 | C21936001370 | Re: WBPDCL Sagaridghi - E04 Alarm | 2023-09-24 | 2023-09-26 13:29 | No | Warranty | WBPDCL | Sagardighi Thermal Power Plant | Murshidabad | 742237 | West Bengal | India FS East Cooling CSP Snow Point Kolkata | Chandan Nandi_Snow Point Kolkata | Snow Point | LP AND HP ALARM SHOWN.DUSTY CONDENSER.CONDENSER CLEAN.ALL PARAMETER CHECKED.HP ALARM RESET.MACHINE OK RUNNING. | Repair |  | 10- Closed | 2023-09-27 13:31 |  |  | 23 | INR | 23 | ENM SECURE POWER
WO-11178602 | 103619403 | 2023-09-01 11:30 | 2023-08-29 |  | 2023-08-29 13:28 | LC1D12M7 | LC1D12M7 | LC1D12M7 | 1023051L101838 | RE: COMPLAINT FOR NOT WORKING ISSUE, Case: 103527451, [ thread::__MQJBXDceezOj8-HfVSdT4:: ] LC1D12M7 - 1023051L101838 LC1D32N7 LC1DT80AM7 operation issue Site Address: DURGA BHAI & CO KHASRA NO.474,LALDORA OF VILLAGE, 25 FOOTA ROAD, AJIT VIHAR, BURARI,Delhi-110084 MO -9555858879 | 2023-08-29 | 2023-09-01 13:17 | No | Warranty | Durga Bhai & Co. | Khasra No 474, 25 Foota Road,LALDORA OF VILLAGE,AJIT VIHAR,BURARI | Delhi | 110006 | Delhi | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the contactor found no/nc point not working and mcb found phase missing, Hence faulty replaced. LC1D12N7- 1 nos A9N3P10C - 1 nos | Repair |  | 9- Service Validated | 2023-09-01 14:46 |  |  | 28 | INR | 28 | ENM POWER PRODUCTS
WO-11302257 | 104231468 | 2023-09-24 13:55 | 2023-09-24 |  | 2023-09-24 11:54 | Leonardo EVDXR407cEC FanTDAV0921ADownflow With Heater & Hum | TDAV0921AN002 | TDAV0921AN002 | C21745000183 | TDAV: Breakdown | 2023-09-24 | 2023-09-24 23:30 | No | Contract | Garden Reach Shipbuilders & Engineers Ltd. | 43/46 Park, Garden Reach Road | Kolkata | 700024 | West Bengal | India FS East Cooling CSP Snow Point Kolkata | Laxmikant Dhang_Snow Point Kolkata | Snow Point | LOSS OF AIR DISPLAY ALARM AND POWER AFTER FALIURE.RESIT THE DISPLAY CONTROLER AND PIPE BLOKAGE CLEAN.PIPE LOSE OF AIR FLOW ALARM PROBLEM SOLVED.ALL PARAMETER CHECKED. MACHINE OK RUNNING. | Repair |  | 10- Closed | 2023-09-24 23:38 |  |  | 30 | INR | 30 | ENM SECURE POWER
WO-11302297 | 104231592 | 2023-09-24 14:13 | 2023-09-25 |  | 2023-09-24 13:44 | XRAF6422A | XRAF6422A | XRAF6422A | SRF032579 | PAC - Chiller Compressor Not Working | 2023-09-24 | 2023-09-26 02:30 | No | Contract | Yotta Infrastructure | PLOT NO 7, SECTOR KNOWLEDGE PARK V Tusiana Village, Gautam Buddha Nagar | Greater Noida | 201301 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Mohd. Shadab Freezeotech Airconditioning & Refrigeration GZB | Freezeotech Airconditioning & Refrigeration Corporation | site visit unit is working ok | Repair |  | 10- Closed | 2023-09-25 20:31 |  |  | 28 | INR | 28 | ENM SECURE POWER
WO-11302298 | 104231626 | 2023-09-24 13:56 | 2023-09-24 |  | 2023-09-24 13:52 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | C21716000532 | PAC: Blower Fan faulty | 2023-09-24 | 2023-09-27 14:31 | No | Contract | Reliance jio infocomm Ltd | Renuka Colony, Ganesh Nagar, | Kalwan | 423501 | Maharashtra | India FS West2 Cooling CSP Gale HVAC Pune | Vishal Paul Gale HVAC Pune | GALE HVAC | We have repalced the blower fan of the unit then unit working normally | Repair |  | 8- Service Completed | 2023-09-27 14:35 |  |  | 280 | INR | 280 | ENM SECURE POWER
WO-11295497 |  | 2023-09-25 16:09 | 2023-09-22 |  | 2023-09-22 13:26 | Easy UPS 3S 40kVA 400V 3:3 UPS Low Tower | E3SUPS40KH | E3SUPS40KH | 9E1831T11111 | PM | 2023-09-22 | 2023-09-23 19:35 | No | Contract | Polaris ( Virtusa) Technologies | Polaris Consulting & Services LTD Prestige Shantiniketan, Tower B, Level 15, Whitefiled Main road, Whitefield null | Bangalore | 560048 | Karnataka | India FS South1 HBN CSP UBM Autopower Pvt. Ltd Bangalore | Arun UBM Autopower Pvt. Ltd Bangalore | Autopower systems and solutions | Annual Shutdown activity done morning switch off again evening switch on the ups & PM done, UPS working normal. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-25 16:11 |  |  | 0 | INR | 0 | ENM SECURE POWER
WO-11302303 | 104231670 | 2023-09-24 14:24 | 2023-09-25 |  | 2023-09-24 14:20 | HXCVQ | HXCVQ | HXCVQ | JK2243003719 | PAC - Water flood Alarm | 2023-09-24 | 2023-09-26 02:30 | No | Warranty | Yotta Infrastructure | PLOT NO 7, SECTOR KNOWLEDGE PARK V Tusiana Village, Gautam Buddha Nagar | Greater Noida | 201301 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Mohd. Shadab Freezeotech Airconditioning & Refrigeration GZB | Freezeotech Airconditioning & Refrigeration Corporation | unit is showing flood alarm we have check all connection and check unit by running now unit is working ok | Repair |  | 10- Closed | 2023-09-25 20:03 |  |  | 28 | INR | 28 | ENM SECURE POWER
WO-11295499 |  | 2023-09-25 16:01 | 2023-09-22 |  | 2023-09-22 13:28 | Easy UPS 3S 40kVA 400V 3:3 UPS Low Tower | E3SUPS40KH | E3SUPS40KH | 9E1831T11115 | PM | 2023-09-22 | 2023-09-23 19:25 | No | Contract | Polaris ( Virtusa) Technologies | Polaris Consulting & Services LTD Prestige Shantiniketan, Tower B, Level 15, Whitefiled Main road, Whitefield null | Bangalore | 560048 | Karnataka | India FS South1 HBN CSP UBM Autopower Pvt. Ltd Bangalore | Arun UBM Autopower Pvt. Ltd Bangalore | Autopower systems and solutions | Annual Shutdown activity done morning switch off again evening switch on the ups & PM done, UPS working normal. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-25 16:07 |  |  | 0 | INR | 0 | ENM SECURE POWER
WO-11295569 | 104211395 | 2023-09-23 01:10 | 2023-09-22 |  | 2023-09-22 13:56 | InRow RC, 300mm, Chilled Water, 208-230V, 50/60Hz - HT w/o bottom piping kit | ACRC301HX738 | ACRC301HX738 | JK1517003979 | DOP: AMC P: BMS offline Issue S: AMC | 2023-09-22 | 2023-09-23 02:07 | No | Contract | Juniper Networks India Pvt Ltd | Prestige Tech Park Elnath-Exora Business Park Survey No.111/1 to 115/4 Wing A & B Amane Bellandur Khane Village Marathahalli | Bangalore | 560103 | Karnataka | India FS South3 Cooling CSP ERIC HVAC SYSTEM Bengaluru | Freddy Dass ERIC HVAC SYSTEM Bengaluru | ERIC HVAC SYSTEM | Controller board is faulty so we have replace a new one . | Repair |  | 8- Service Completed | 2023-09-27 00:11 |  |  | 30 | INR | 30 | ENM SECURE POWER
WO-11179169 | 103624938 | 2023-08-31 09:15 | 2023-08-29 |  | 2023-08-29 17:39 | METSEEM6433HCL10RS | METSEEM6433HCL10RS | METSEEM6433HCL10RS |  | DOP: 19.10.2022 Schneider Invoice: 9008293019 METSEEM6433HCL10RS Qty:1 P: Meter EM6433 supplied with Panel, display is not working M/S AAR BEE INDUSTRIES 2 Site Address SRI KANDAN SPINNING MILLS NOCHIVALASU PIRIVU, MONGANALLAMPALAYAM ROAD KANNIVADI, DHARAPURAM TK Muthukumar 9710033342 | 2023-08-29 | 2023-09-03 18:54 | No | Warranty | SRI KANDAN SPINNING MILLS | NOCHIVALASU PIRIVU MONGANALLAMPALAYAM ROAD KANNIVADI, DHARAPURAM TK null | Erode | 639202 | Tamil Nadu | India FS ED&I CSP South Team Power Pro Engineering Services Coimbatore | KV ARUNKUMAR_POWER PRO ENGINEERIG SERVICES COIMBATORE | Powerpro Engineering Services | WE HAV EVISITED THE SITE AND INPECTED WE FOUND METER DISPLAY NOT WORKING DUE TO METER CO TOL VOLATGE ISSUE WE HAV INFORMED TO CUSTOMER THIS OW THIS NOT COVRED IN WARRANTY | Repair |  | 9- Service Validated | 2023-09-03 18:55 |  |  | 155 | INR | 155 | ENM POWER PRODUCTS
WO-11295751 | 104213447 | 2023-09-22 15:16 | 2023-09-22 |  | 2023-09-22 14:49 | Leonardo Ev,DX,R22,TUAR0721A,Upflow with Heater & Humidifier (Front Suction) | TUAR0721AN001 | TUAR0721AN001 | NUCU3272 | DOP: Contract P: PAC - Heater Not Working S: AMC Calling number: 7906236874 | 2023-09-22 | 2023-09-30 17:00 | No | Contract | International Tobacco Co. Ltd. | Meerut Road, Guldhar, | Ghaziabad | 201003 | Uttar Pradesh | India FS North2 Cooling CSP D K AIRCON Delhi | Ajay Kumar_D K AIRCON Delhi | DK AIRCON | We have check & found PAC was MCB triping due to Heater faulty (Burnt) Issue. We have New Heater Strip 3KW replacement work done and testing done. All paramenter check and found ok. Now PAC unit is working OK | Repair |  | 8- Service Completed | 2023-09-30 23:01 |  |  | 34 | INR | 34 | ENM SECURE POWER
WO-11295950 | 104216095 | 2023-09-22 18:26 | 2023-09-22 |  | 2023-09-22 16:16 | Leonardo EV,DX,R407c,EC Fan,TDAV1622A(double Skin)Downflow With Heater & Humidif | TDAV1622AN004 | TDAV1622AN004 | ZK1548008425 | AMC P: High condensing pressure OR Compr Contactor Failed. S: AMC | 2023-09-22 | 2023-09-23 13:00 | No | Contract | VODAFONE GLOBAL SERVICES PRIVATE LIMITED | *Unit 1 A&B, Creator Building | BANGALORE | 560066 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Akash MP_UCS Projects and services Bangalore | UCS Projects & Services | High condensing pressure of copresser contactor failed. visit site & observed that refregent presure was low so we have checked the leakage &top up the gas. Now unit working normally. | Repair |  | 8- Service Completed | 2023-09-25 18:20 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11183420 | 103658640 | 2023-09-01 16:26 | 2023-08-30 |  | 2023-08-30 14:23 | LC1D25B7 | LC1D25B7 | LC1D25B7 | 1023134 | Complaint LC1D25B7 humming sound 10231346332L1 Vijayshree Industries, Plot No-9&10, Phase-5, Aditipuri, Industrial Area, Ghamaria, Jamshedpur 832108 Jharkhand Mr. Prakahar 7004675742 | 2023-08-30 | 2023-09-01 17:30 | No | Warranty | Vijayshree Industries Private Limited | Plot No-9&10, Phase-5, Aditipuri, Industrial Area, Ghamaria, null | Jamshedpur | 832108 | Jharkhand | India FS ED&I CSP East Team UNIVERSAL ELECTRIC POWER SOLUTION BHUBANESWAR | Banty Kumar_UNIVERSAL ELECTRIC POWER SOLUTION BHUBANESWAR | Universal Electric Power Solution(500012032) | product have no issue and customer rectify the problem | Repair |  | 9- Service Validated | 2023-09-01 17:32 |  |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11295959 | 104216019 | 2023-09-22 18:28 | 2023-09-22 |  | 2023-09-22 16:18 | Leonardo EV,DX,R410a,EC Fan,TDAV1321A,Downflow With Heater & Humidifier | TDAV1321AN003 | TDAV1321AN003 | ZK1506003746 | AMC P: High condensing pressure OR Compr Contactor Failed. S: AMC | 2023-09-22 | 2023-09-23 13:00 | No | Contract | VODAFONE GLOBAL SERVICES PRIVATE LIMITED | *Unit 1 A&B, Creator Building | BANGALORE | 560066 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Akash MP_UCS Projects and services Bangalore | UCS Projects & Services | High condensing pressure of copresser contactor failed. visit site & observed that refregent presure was low so we have checked the leakage &top up the gas. Now unit working normally. | Repair |  | 8- Service Completed | 2023-09-25 18:15 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11183758 | 103658917 | 2023-08-30 17:58 | 2023-08-30 | NA | 2023-08-30 17:31 | C63F46E630 | C63F46E630 | C63F46E630 |  | Fw: Lock complaint GF-UIPP-1A Panel MCCB As Per The serial number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Triston Digital Group Building 10, Plot No. IT-5, Arioli Knowledge Park, T.T.C Industrial Area Thane 400708 Maharashtra India Contact Person Details:- Dipesh Ji--- Contact No: 9029611982 Product and Issue:- Type No : C63F46E630 Qty : 01 Nos Invoice No.9008118928 Motorized MCCB is not closing Breaker in Auto mode as well as in manual mode | 2023-08-30 | 2023-08-31 17:57 | No | Warranty | Triston Digital Group | Building 10, Plot No. IT-5, Arioli Knowledge Park, T.T.C Industrial Area null | Thane | 400708 | Maharashtra | India FS ED&I CSP West Team East India Power Engineers Mumbai | Sandeep Ingavale East India Power engineers Mumbai | East India Power Engineers (5043) | Visited the site & checked the Motor Mechanism with MCCB electrically auto mod and found the motor not getting spring charging. Checked the Motor mechanism taken a manual mode found the manual getting spring charging & checked the ON / OFF operation and found it okay. The motor mechanism opened the front cover & checked the gear and found a damaged condition. The motor mechanism was found faulty. | Repair |  | 8- Service Completed | 2023-09-07 10:10 | 226018461 |  | 8 | INR | 8 | ENM POWER PRODUCTS
WO-11295994 |  | 2023-09-22 20:31 | 2023-09-22 |  | 2023-09-22 16:34 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | JK1930002442 | Configuration | 2023-09-22 | 2023-09-22 20:33 | No | Contract | Reliance JIO | Village Sakras Post-Sakras Tehsil Firozpur Zhirka Dist ? NUH Rujdar S/o Navab, VPO Sakras, Tehsil-Ferozpur Zirka | Mewat | 122108 | Haryana | India FS North1 Cooling CSP Smart Engineering Services Delhi | Taranjeet Singh_Smart Engineering Services Delhi | Smart Engineering Services | VISIT AND FOUND CUSTOMER HAND VOLTAGE ISSUE, REQUIRED STABLIZER IN AC, CHECKED ALL PARAMETERS, NOW UNIT IS WORKING OK | Configuration & Programming | Basic | 10- Closed | 2023-09-22 20:39 |  |  | 84 | INR | 84 | ENM SECURE POWER
WO-11295995 |  | 2023-09-22 20:41 | 2023-09-22 |  | 2023-09-22 16:34 | WDF0181BN002 | WDF0181BN002 | WDF0181BN002 | C21707000600 | Configuration | 2023-09-22 | 2023-09-22 20:41 | No | Contract | Reliance JIO | Chungi no-1 ,ward no-01, Bhim nagar null | Shona | 122103 | Haryana | India FS North1 Cooling CSP Smart Engineering Services Delhi | Taranjeet Singh_Smart Engineering Services Delhi | Smart Engineering Services | VISIT AND FOUND WIRING ISSUE, WE HAVE TIGHT ALL WIRE CONNECTIONS, CHECKED ALL PARAMETERS, NOW UNIT IS WORKING OK | Configuration & Programming | Basic | 10- Closed | 2023-09-22 20:46 |  |  | 74 | INR | 74 | ENM SECURE POWER
WO-11185956 | 103660529 | 2023-08-31 10:26 | 2023-08-31 | NA | 2023-08-31 10:10 | GCR_NSX100_630 | GCR_NSX100_630 | GCR_NSX100_630 |  | Fw: Item Damage Details for Damage. No: 5322 Dear Team, Please find trail mail Rejection from Mumbai plant. SAP no: 225759752 Invoice No.9008620519 Type No : 33682 SR NO-1231630011 Problem : Not getting output voltage Kindly arrange replacement & Service engineer below mention address: Site Address- M/s. Marine Electricals (I) Ltd. Plot no. D390, T.T.C Industrial Area MIDC Nerul , Navi Mumbai- 400706. Contact no. Hitesh Wankhede Best Regards, Prachi Parab Purchase Executive Industry Division - Low Voltage | 2023-08-31 | 2023-09-06 10:26 | No | Warranty | MARINE ELECTRICALS (I) LTD | D-390 Nerul MIDC Industrial Area TTC Navi Mumbai | THANE | 400701 | Maharashtra | India FS ED&I CSP West Team East India Power Engineers Mumbai | Sandeep Ingavale East India Power engineers Mumbai | East India Power Engineers (5043) | Visited the site & checked the UVR Unit by giving supply to the input & checked the output so not found the output side voltage. Hence UVR unit found faulty needs to be replace with a new one. | Repair |  | 8- Service Completed | 2023-09-06 16:31 | =S= Consig Fill up 226031516 |  | 12 | INR | 12 | ENM POWER PRODUCTS
WO-11296554 |  | 2023-09-24 12:17 | 2023-09-16 |  | 2023-09-22 18:43 | SRCE6KUXI | SRCE6KUXI | SRCE6KUXI | B21629002040 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-25 17:43 | No | Contract | PNB Housing Finance Ltd | 202 Second Floor Riddhi Arcade 100ft. Narangi Bypass Road Virar West Vasai Near Big Bazar | Thane | 401303 | Maharashtra | India FS West1 HBN CSP_Anum Technosolutions Sakinaka | Anil Gupta_Anum Technosolutions Sakinaka | Anum Technosolutions (Pvt) Ltd-Sakinaka- Mumbai | PREVENTIVE MAINTENANCE DONE, UPS WORKING OK | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-25 17:44 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11187800 | 103662106 | 2023-08-31 19:09 | 2023-08-31 |  | 2023-08-31 13:02 | EM7230 | EM7230 | EM7230 | 45068 | Fwd: Service Request EM7230 DOM 22May2023 display issue Site Address: ACE ELECTROTREND PANELS PVT. LTD., 1-B, Electrical & Electronics Industrial Estate, HOSUR -635109 Mr. V.Radhakrishnan 9994306854 | 2023-08-31 | 2023-09-01 13:00 | No | Warranty | Ace Electrotrend Panels Pvt Ltd | 1B, Electricals & Electronics Estate, By-Pass Road, | Hosur | 635109 | Tamil Nadu | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore |  | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported em7230 meter, the problem found was internal display got dislocated. So we re-fixed the same and checked found working ok. The same shown to the customer. | Repair |  | 8- Service Completed | 2023-09-01 22:32 |  |  | 51 | INR | 51 | ENM POWER PRODUCTS
WO-11296581 |  | 2023-09-23 11:53 | 2023-09-16 |  | 2023-09-22 18:46 | APC Smart-UPS RC 6000VA 230V for India - No Batteries | SRC6KUXI | SRC6KUXI | B21509000687 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-26 11:50 | No | Contract | PNB Housing Finance Co Ltd | B-46 B, 2nd Floor Sadul Ganj null | Bikaner | 334002 | Rajasthan | India FS North1 HBN CSP Legacy Systems Jaipur | Rajendra Kumar Legacy Systems Jaipur | Legacy Systems | PM done unit working fien both mode check on load 30 mint | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-26 11:54 |  |  | 350 | INR | 350 | ENM SECURE POWER
WO-11187912 | 103654929 | 2023-08-31 14:59 | 2023-08-31 |  | 2023-08-31 13:44 | LV525303 | LV525303 | LV525303 |  | Material replacement required | 2023-08-31 | 2023-09-05 15:47 | No | Warranty | Delton Control & Switchgears LLP_HO | 43-43A,1st main road, New Timberyard Layout, off Mysore road | Bangalore | 560026 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Santhosh DP_P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | Inspected and found below mentioned, 1)Ref:LC1D12BFD S/N:8B23093 = 1 No, contactor screw threading issue. Hence we will give same new contactor warranty replacement ASAP. | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-05 15:48 |  |  | 8 | INR | 8 | ENM POWER PRODUCTS
WO-11296765 |  | 2023-09-27 18:51 | 2023-12-16 |  | 2023-09-22 19:11 | SRCE6KUXI | SRCE6KUXI | SRCE6KUXI | B21543001568 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-28 17:34 | No | Contract | PNB Housing Finance Limited | 221, 2nd Floor, Mangalam Arcade, Opp. Odhav Lake, Odhav BRTS Road, Odhav null | Ahmedabad | 395009 | Gujarat | India FS West2 HBN CSP_Safal Solutions Mehsana | Almas Saiyad Safal Solutions Mehsana | Safal Solutions | UPS & Battery PM Done. UPS Is properly working fine. | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-28 17:38 |  |  | 8 | INR | 8 | ENM SECURE POWER
WO-11296601 |  | 2023-09-23 15:50 | 2023-09-16 |  | 2023-09-22 18:50 | SRV3KUXI-IN | SRV3KUXI-IN | SRV3KUXI-IN | 9S2224A01699 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-25 12:02 | No | Contract | PNB Housing Finance Ltd | Old Survey No. 97/4,New Survey No. 97/6 B1, 5 Roads null | SALEM | 636007 | Tamil Nadu | India FS South2 HBN CSP GRControlSystems Salem | Mohamed falulullah GRControlSystems Salem | GR Control Systems-Salem | Unit Model & Serial number missmatch. Physical Model:SRV3KUXI-IN Physical Serial Number:9S2224A01699 PM Service done Unit & Battery working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-25 17:47 |  |  | 18 | INR | 18 | ENM SECURE POWER
WO-11188003 | 103658210 | 2023-08-31 14:33 | 2023-08-31 | NA | 2023-08-31 14:28 | LV432894 | LV432894 | LV432894 | AA2720132135 | Person Assistance Required Fw: NCF for POR: AEB23240011(NTT DC09) As Per The Invoice number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Arrow Electricals India Pvt. Ltd. Arrow House (11A/11B), K.T. Industrial Park, Goraipada,, Vasai E, Dist. Palghar Vasai 401208 Maharashtra India Contact Person Details:- MR. AJAY YADA 8296588418 Product and Issue:- LV432894 NSX630N 630 A FP MCCB Invoice No.: AA2720132135 Invoice Dt.: 26.Dec.2022 Discussed with Mr. Ajay, MCCB operation Issue, Tripping rapidly when trying to make it on. UV and shunt coil not installed. | 2023-08-31 | 2023-09-01 19:35 | No | Warranty | Arrow Electricals India Pvt. Ltd. | Arrow House (11A/11B), K.T. Industrial Park, Goraipada,, Vasai E, Dist. Palghar | Vasai | 401208 | Maharashtra | India FS ED&I CSP West Team Kanekar Consulting Engineers Pvt Ltd Thane | Nitin Arote_Kanekar Consulting Mumbai | Kanekar Consulting Engineers Pvt. Ltd. | Check mccb check SDE adaptor properly fit in MCCB, then check on off ok | Repair |  | 9- Service Validated | 2023-09-01 19:35 |  |  | 27 | INR | 27 | ENM POWER PRODUCTS
WO-11296970 |  | 2023-09-28 14:53 | 2023-09-16 |  | 2023-09-22 19:38 | SRCE6KUXI | SRCE6KUXI | SRCE6KUXI | B21635000118 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-28 17:26 | No | Contract | PNB Housing Finance Ltd | F1, KEK Tower,First Floor, Opp. To Trivandrum Development Authority, Vazhuthacaud null | THIRUVANANTHAPURAM | 695010 | Kerala | India FS South2 HBN CSP YEMYEMEnterprises Trivandrum | SAMBHU P YEMYEMEnterprises Trivandrum | Yemyem Enterprises | Preventive Maintenance Completed- UPS Working fine. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-28 17:35 |  |  | 6 | INR | 6 | ENM SECURE POWER
WO-11188156 | 103685079 | 2023-09-02 14:38 | 2023-08-31 |  | 2023-08-31 15:20 | LV525021 | LV525021 | LV525021 | 10230630330 | Failure MCCB 250A/TP LV525021 - 10230630330 pole continuity issue Site Address: AMBA AGRO INDIA PVT LTD # SUBHASH MANDI GATE, NEAR GEETA KANYA SCHOOL,AMIN ROAD, KURUKSHETRA 136118 Contact No.: 9996220001 | 2023-08-31 | 2023-09-02 14:40 | No | Warranty | AMBA AGRO INDIA PRIVATE LIMITED | SUBHASH MANDI GATE | KURUKSHETRA | 136118 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the MCCB found phase missing and defective product not available at site. Hence complaint is closed. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-02 14:53 |  |  | 105 | INR | 105 | ENM POWER PRODUCTS
WO-11296619 |  | 2023-09-27 17:58 | 2023-12-16 |  | 2023-09-22 18:52 | SRCE6KUXI | SRCE6KUXI | SRCE6KUXI | B21836002755 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-30 11:39 | No | Contract | PNB Housing Finance Ltd | Plot No. 46, 1st Floor, Ahuja Tower, Napier Town null | Jabalpur | 482001 | Madhya Pradesh | India FS West2 HBN CSP_Powertech Jabalpur | Iftekhar khan_Powertech Jabalpur | Powertech | I checked UPS input and output, visited PM, UPS is working fine. | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-30 11:39 |  |  | 0 | INR | 0 | ENM SECURE POWER
WO-11296640 |  | 2023-09-29 16:22 | 2023-09-16 |  | 2023-09-22 18:55 | APC SMART-UPS RC 6000VA 230V FOR INDIA - NO BATTERIES | SRCE6KUXI | SRCE6KUXI | B21551000474 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-30 14:49 | No | Contract | PNB Housing Finance Ltd | SCO No-136 1st Floor HUDA market Above Allahabad Bank Sector- 21 C null | Faridabad | 121003 | Haryana | India FS North1 HBN CSP Prokon Hi Tech Systems Gurgaon | Subodh Pasupat Prokon Hi-Tech Systems Faridabad | Prokon Hi-Tech Systems-Faridabad-Haryana | UPS properly checked but no problem found in ups, working is okay. | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-30 14:53 |  |  | 10 | INR | 10 | ENM SECURE POWER
WO-11188256 | 103687906 | 2023-08-31 18:24 | 2023-08-31 | NA | 2023-08-31 16:21 | LV435001 | LV435001 | LV435001 | TC-2023-W12-1 | Motor Mechanism Issue LV435001 TC-2023-W12-1 operation issue Site Address: POWERCON SWITCHGEAR LLP, W- 379, MIDC INDUSTRIAL AREA, THANE - BELAPUR ROAD, RABALE, NAVI MUMBAI - 400701 SITE CONTACT NAME: KHALID SITE CONTACT NUMBER: 8291917100 | 2023-08-31 | 2023-09-01 18:17 | No | Warranty | Powercon Switchgear_SD | W-379, TTC MIDC, Rabale, | Navimumbai | 400701 | Maharashtra | India FS ED&I CSP West Team East India Power Engineers Mumbai | Sandeep Ingavale East India Power engineers Mumbai | East India Power Engineers (5043) | Visited the site and checked the motor mechanism with MCCB manually On/Off working ok. Checked the motor mechanism by giving supply not getting On/Off condition. Also checked manually on and giving supply to off working found working ok. So not getting to on command to electrically | Repair |  | 8- Service Completed | 2023-09-26 16:19 | =S= Consig Fill up 226022691 |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11296650 |  | 2023-09-28 19:13 | 2023-12-16 |  | 2023-09-22 18:57 | SRCE6KUXI | SRCE6KUXI | SRCE6KUXI | B21720000667 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-30 17:40 | No | Contract | PNB Housing Finance Limited | C2/21, First Floor, C-block, Mata Chanan Devi Road, Janakpuri null | New Delhi | 110001 | Delhi | India FS North1 HBN CSP HITEK BUSINESS SYSTEMS PVT LTD Delhi | Brajesh B_Hitek Business Systems New Delhi | Hitek Business Systems Pvt Ltd | Engineer this site UPS Preventive Maintenance done UPS working ok | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-30 18:14 |  |  | 15 | INR | 15 | ENM SECURE POWER
WO-11188403 | 103693321 | 2023-09-01 10:52 | 2023-08-31 |  | 2023-08-31 17:09 | GCR_NW_CB | GCR_NW_CB | GCR_NW_CB |  | ACB received in Damage Condition | 2023-08-31 | 2023-09-01 18:39 | No | Warranty | Dynam Electro Controls | Site No,3/3 Yerrappa Industrial Area, Magadi Main Road,Chennenahalli Village, Tavarekere Hobli | Bangalore | 562130 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Nagaraja G_P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | Inspected and found below mentioned 1)Ref:MTZ220H120X3PMD S/N:10232310007 = 1 No ACB breaker ON/OFF working found ok. But breaker CDP cover was damaged and cracked and also we took the photos and details of the ACB. CDP cover Ref No:LV848603SP S/N:PL2022_W11-2 = 1 No Hence we will inform to Schneider FCE and will give the feedback ASAP. Invoice No:AA3630024031 Date: 25/07/2023 Docket no: 387889246 We sended all the transit damage details to Schneider customer care and get the reference No: 103729949 | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-01 18:40 |  |  | 15 | INR | 15 | ENM POWER PRODUCTS
WO-11296707 |  | 2023-09-28 09:45 | 2023-09-28 |  | 2023-09-22 19:04 | SRCE6KUXI | SRCE6KUXI | SRCE6KUXI | B21808001478 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-29 02:30 | No | Contract | PNB Housing Finance Limited | 2nd & 4th Floor Megha House ,opp Kotak Bank, Mithakhali Law Garden Road, Ellisbridge, null | Ahmedabad | 380006 | Gujarat | India FS West2 HBN CSP_Safal Solutions Ahmedabad | Ranjit Thakor Safal Solutions Ahmedabad | Safal Solutions | UPS PM has been done and find both ups and batteries are working fine. | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-28 17:16 |  |  | 3 | INR | 3 | ENM SECURE POWER
WO-11188949 | 103697685 | 2023-08-31 19:42 | 2023-08-31 |  | 2023-08-31 18:46 | GCR_MTZ2_CB | GCR_MTZ2_CB | GCR_MTZ2_CB | GCR_MTZ2_CB | mtz breaker tripping issue at wipro sarjapur road bengaluru Complaint Registration 1 Name of Customer M/s. Wipro Limited 2 Site Address Sarjapura ( Civil ) Dodda Kannenahalli Sarjapura Road Bengaluru - 560029 3 Name of contact person at site Mr. Harish 4 Contact Phone / Mob. No: 8147805256 5 Defective product details MTZ Breaker 6 Nature of Defect Tripping issue in load condition. ( RCA required ) 7 Warranty status Under warranty 8 Commissioned / Installed date Under commissioning 9 Name & phone No: of person registering the complaint Sanjeev: 7676875776 Complaint Date: 31-08-23 | 2023-08-31 | 2023-09-01 12:09 | No | Warranty | Wipro Limited | D Block SJP1 Tower S-3 Dodda Kannelli, Sarjapur Road, Ramagondanahalli Village | Bangalore | 560035 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | C Gunasekaran_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | We had visited the site and checked the customer reported MTZ ACB. FOUND sensor plug not sensing. Due to sensor plug not connected with micrologic. So we reconnect and checked sensing ok , there is no issues with our product. | Repair |  | 9- Service Validated | 2023-09-02 00:16 |  |  | 22 | INR | 22 | ENM POWER PRODUCTS
WO-11296734 |  | 2023-09-29 11:42 | 2023-09-29 |  | 2023-09-22 19:07 | APC Smart-UPS RC 6000VA 230V for India - No Batteries | SRC6KUXI | SRC6KUXI | B21420000824 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-29 16:18 | No | Contract | PNB Housing Finance Ltd | SCO 323-324, 1st Floor, Sector 35B null | Chandigarh | 160035 | Chandigarh | India FS North2 HBN CSP Green IT Solutions Chandigarh | Raju R_Green IT Solutions Chandigarh | Green IT Solutions | Pm done now ups working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-29 16:21 |  |  | 8 | INR | 8 | ENM SECURE POWER
WO-11192167 | 103698700 | 2023-09-03 18:57 | 2023-09-01 |  | 2023-09-01 11:08 | METSEEM6436HCL10NC | METSEEM6436HCL10NC | METSEEM6436HCL10NC | 540410014121 | Complaint Registration For METSEEM6436HCL10NC METSEEM6436HCL10NC 540410014121 as per customer statement - display issue Site Address: RK Engineering and Infrastructure D.No.176, Mettukadu, Chinnamedu, Thindal, Perundurai 638 012 Tamil Nadu Mr. GUNASEELAN 9626033328 | 2023-09-01 | 2023-09-04 18:34 | No | Warranty | RK Engineering and Infrastructure | D.No.176, Mettukadu, Chinnamedu, Thindal, | Perundurai | 638 012 | Tamil Nadu | India FS ED&I CSP South Team Power Pro Engineering Services Coimbatore | KV ARUNKUMAR_POWER PRO ENGINEERIG SERVICES COIMBATORE | Powerpro Engineering Services | WE HAVE VISITED THE SITE AND INSPECTED WE FOUND TER POWER ON ISSUE DUE TO METER INTERNAL COMPONANTS FOUND MALL FUNCTIOING WE HAVE COLLECTED THE DETAILS FOR FURTHER ACION AND ARRAGING FOR FREE REPLACEMENT FOR THIS AND COLLECTED THE DETAILS FOR FURTHER ACTION | Repair |  | 8- Service Completed | 2023-09-04 18:36 |  |  | 110 | INR | 110 | ENM POWER PRODUCTS
WO-11296738 |  | 2023-09-29 11:31 | 2023-09-29 |  | 2023-09-22 19:07 | SRCE6KUXI | SRC10000UXI | SRC10000UXI | B21934000084 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-29 16:27 | No | Contract | PNB Housing Finance Ltd | SCO 323-324, 1st Floor, Sector 35B null | Chandigarh | 160035 | Chandigarh | India FS North2 HBN CSP Green IT Solutions Chandigarh | Raju R_Green IT Solutions Chandigarh | Green IT Solutions | Pm done now ups working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-29 16:32 |  |  | 8 | INR | 8 | ENM SECURE POWER
WO-11193511 | 103719697 | 2023-09-05 14:59 | 2023-09-01 |  | 2023-09-01 12:19 | LV516313 | LV516313 | LV516313 | 10-2023-W19-2-0521L1 | LV516313 - 10-2023-W19-2-0521L1 tripping issue Site Address: THE ATTIRE Plot No 187, The Attire, Udyog Vihar Phase-iv, Gurugram Gurugram 122016 Haryana Mr. Subhash Chandra 9899131851 | 2023-09-01 | 2023-09-05 15:01 | No | Warranty | THE ATTIRE | Plot No 187, The Attire, Udyog Vihar Phase-iv, Gurugram | Gurugram | 122016 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the Mccb found tripping issue Due to cable heating. Our product working ok. Email : id not provided by customer. | Repair |  | 9- Service Validated | 2023-09-05 15:04 |  |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11296749 |  | 2023-09-29 11:28 | 2023-09-29 |  | 2023-09-22 19:08 | SRCE6KUXI | SRCE6KUXI | SRCE6KUXI | B21819003560 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-29 16:52 | No | Contract | PNB Housing Finance Ltd | SCO 218-219, 1st Floor, Sector 12, Part 1 City Centre karnal | Karnal | 132001 | Haryana | India FS North2 HBN CSP Green IT Solutions Chandigarh | Deepak Green IT Solutions Chandigarh | Green IT Solutions | Pm done now ups working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-29 16:54 |  |  | 140 | INR | 140 | ENM SECURE POWER
WO-11194039 | 103590863 | 2023-09-12 16:31 | 2023-09-01 |  | 2023-09-01 13:04 | INA_ENSET_PANEL | INA_ENSET_PANEL | INA_ENSET_PANEL | LTX2248 | RE: ADVANCE VENTILATION _ TATA CDU VDU ( BARMER SITE - RAJASTHAN) PANEL DAMAGE - LTX 2248 Dear CCC Team, As per trail mail, Please register complaint (damage panel). Panels SO No. 224751018 Siter Peron : Mr. Amir, Mobile- 8295375529 , 9627373060 & Shiv Raj Verma (9711095828 / 7290083152 ) E-mail ID: shivraj.verma@advanceventilation.com Site address: TATA PROJECTS LTD Project : EPCC 01 Package ? CDU_VDU C/O HPCL Rajasthan Refinery Limited (HRRL), Rajasthan Refinery Project of HRRL Village; Sajiyali Roopji kanthwada & Sambhra, Tehsil- Pachpadra, Distt: Barmer, Rajasthan, 344 032 | 2023-09-01 | 2023-09-12 16:33 | No | Warranty | HPCL Rajasthan Refinery Limited | HPCL Rajasthan Refinery, Pachpadra ,District Barmar | Barmer | 344032 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | Inv. No. AA2430001207 dt 31.5.23 OA no. 224751016 As per Customer Panal received at site 3 month back. Docket / GR details are not available with end customer As per Customer, After getting Panal from store , they opened and found damages | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-12 16:36 |  |  | 550 | INR | 550 | ENM POWER PRODUCTS
WO-11296756 |  | 2023-09-29 15:52 | 2023-09-16 |  | 2023-09-22 19:09 | SRCE6KUXI | SRCE6KUXI | SRCE6KUXI | B21820009790 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-30 15:02 | No | Contract | PNB Housing Finance Ltd | PNB Housing Finance Ltd 2nd Floor 286 Shopping center null | Kota | 324006 | Rajasthan | India FS North1 HBN CSP EL-TRONICS Kota | Taufiq Raza EL-TRONICS Kota | EL-TRONICS | PM activity done.UPS is working ok. | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-30 15:05 |  |  | 15 | INR | 15 | ENM SECURE POWER
WO-11194070 | 103717237 | 2023-09-02 16:51 | 2023-09-01 |  | 2023-09-01 13:07 | LC1E12M7 | LC1E12M7 | LC1E12M7 |  | Replacement of contractor As Per The Serial number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Ashmita Associates Plot number:- 148/1 benada road, bassi Jaipur 303301 Rajasthan India Contact Person Details:- Bharat Aggarwal:---9928357575 Product and Issue:- LC1E12M7 Contactor Powering up issue and not operating | 2023-09-01 | 2023-09-02 16:53 | No | Warranty | Ashmita Associates | Plot number:- 148/1 benada road, bassi null | Jaipur | 303301 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | Checked the add on block found working ok. Email : id not provided by customer . | Repair |  | 9- Service Validated | 2023-09-02 17:01 |  |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11296771 |  | 2023-09-29 08:34 | 2023-09-16 |  | 2023-09-22 19:12 | SRCE6KUXI | SRCE6KUXI | SRCE6KUXI | B21837009051 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-30 08:46 | No | Contract | PNB Housing Finance Ltd | b29, 1st floor, baby electronics 262/1 dr sham sing road shirosha road opposite to firoz gandi road null | Ludhiana | 141001 | Punjab | India FS North2 HBN CSP Essar Engineers Chandigarh | Karan Singh Essar Engineers Chandigarh | Essar Engineers | Preventive Maintenance of the UPS is done UPS tested on load its working normal | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-30 08:52 |  |  | 110 | INR | 110 | ENM SECURE POWER
WO-11194659 | 103723633 | 2023-09-02 16:03 | 2023-09-01 |  | 2023-09-01 14:28 | GCR_MVS | GCR_MVS | GCR_MVS | WX23106 | Shunt coil not operating by giving 24V--33659 As Per The serial number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- PSG electrical S 22/23, Sikandarabad indistrial area, near sharma hotel BULANDSHAHR 203205 Uttar Pradesh India Contact Person Details:- Pavan Sharma 9718439725 Product and Issue:- 33659 WX23106 Shunt coil not operating by giving 24V--33659 | 2023-09-01 | 2023-09-04 16:25 | No | Warranty | PSG electrical | S 22/23, Sikandarabad indistrial area, near sharma hotel | BULANDSHAHR | 203205 | Uttar Pradesh | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the shunt coil found not working and meter found display not showing, Hence faulty replaced. 33659 - 3 nos METSEEM6436HCL10RS - 3 nos Email : id not provided by customer . | Repair |  | 9- Service Validated | 2023-09-05 16:28 |  |  | 92 | INR | 92 | ENM POWER PRODUCTS
WO-11296775 |  | 2023-09-29 09:38 | 2023-09-16 |  | 2023-09-22 19:13 | SRCE6KUXI | SRCE6KUXI | SRCE6KUXI | B21839023183 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-29 10:45 | No | Contract | PNB Housing Finance Ltd | Office No. 23, 24, 25 , 1st Floor, City Square Mall, Civil Lines, Old G. T. Road BMP Chowk | Jalandhar | 144001 | Punjab | India FS North2 HBN CSP Crest & Company Chandigarh | HARPREET SINGH Crest & Company Jalandhar | Crest & Company - Jalandhar - Chandigarh | preventive maintenance done, check all the parameter and contacts are ok, check battery backup 5 minutes, ups working fine on main and battery mode. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-29 10:56 |  |  | 5 | INR | 5 | ENM SECURE POWER
WO-11195150 | 103722881 | 2023-09-01 17:34 | 2023-09-01 |  | 2023-09-01 16:36 | C2ADTLB30250KD00 | C2ADTLB30250KD00 | C2ADTLB30250KD00 |  | DOP: In warranty C2ADTLB30250KD00 Qty:2 P: Not Working Ramakrishna Reddy pala 8464977755 Center for sight eye hospital 4TH LN Mogalrajpuram sidhartha nagar labbipet vijayawada Andhra Pradesh 520010 | 2023-09-01 | 2023-09-12 12:00 | No | Warranty | Center for sight eye hospital | 4TH LN Mogalrajpuram sidhartha nagar labbipe null | Vijayawada | 520010 | Andhra Pradesh | India FS ED&I CSP South Team Sumanth Electrical Services Hyderabad | Pramoud Kumar_SUMANTH ELECTRICAL SERVICES HYDERABAD | Sumanth Electrical Services | Self Visited Site and Inspected Schneider Electric C2ADTLB30250KD ATS and in our observation we found that the ATS is not transferring from Normal to Emergency Source we are suspecting Problem with EB side Normal Side PCB has been damaged due to External Voltages Surge Voltages and we have requested to End User and Panel Builder to Proved SPD with SCPD with Proper Earthing But We are replacing with New ATS as per instructions of Mr.Nagabushnam sir we are closing this work order | Repair |  | 9- Service Validated | 2023-09-12 16:48 |  |  | 290 | INR | 290 | ENM POWER PRODUCTS
WO-11296841 |  | 2023-09-23 12:27 | 2023-09-16 |  | 2023-09-22 19:21 | APC Smart-UPS RC 6000VA 230V for India - No Batteries | SRC6KUXI | SRC6KUXI | B21406000062 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-25 17:01 | No | Contract | PNB Housing Finance Limited | Plot No-17, 3rd Floor, K.P. Tower, Upper Chopasani Road, Near Bombay Motor Circle, Baldev Nagar null | Jodhpur | 342003 | Rajasthan | India FS North1 HBN CSP EL-TRONICS Jodhpur | Sukhdev Bhati EL-TRONICS Jodhpur | EL-TRONIC | UPS not install at site. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-25 17:04 |  |  | 20 | INR | 20 | ENM SECURE POWER
WO-11296855 |  | 2023-09-28 16:02 | 2023-12-16 |  | 2023-09-22 19:24 | SRCE6KUXI | SRCE6KUXI | SRCE6KUXI | B22125007438 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-30 17:25 | No | Contract | TNP Housing Finance Ltd | 1st Floor Nobel Center Lakshmi Mills null | Coimbatore | 641037 | Tamil Nadu | India FS South2 HBN CSP GRControlSystems Coimbatore | Mani kandan GRControlSystems Coimbatore | GR Control Systems-Coimbatore | PM done. Unit & Battery working fine call closed | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-30 17:32 |  |  | 18 | INR | 18 | ENM SECURE POWER
WO-11199085 | 103727019 | 2023-09-02 11:31 | 2023-09-04 | Engineer observed the meters display not coming. Input voltage within the range. Replaced new Meters. | 2023-09-02 10:23 | METSEEM6436HCL10RS | METSEEM6436HCL10RS | METSEEM6436HCL10RS |  | RE: COMPLAINT OF ATS CHANGE OVER AND MULTI FUNCTION METERS [ thread::sME3pKxeelm2QKOumET0Cj4:: ] GOOD MORNING TEAM HAVE A NICE DAY NAME OF THE CUSTOMER;- Ramakrishna Reddy pala CUSTOMER NUMBER;- 8464977755 ADDRESS;- Center for sight eye hospital ,520010,4TH LN Mogalrajpuram,sidhartha nagar,labbipet,vijayawada,Andhra Pradesh NATURE OF COMPLAINT;- 1.ASCO AUTO TRANSFER SWITCH CONTROLLERS IS NOT WORKING WHY BECAUSE THE TWO PANELS CHANGE OVER NOT CHANGES TO AUTOMATICALLY E.B POWER TO D.G POWER AND NOT CHANGE DG POWER TO EB POWER 2.AND SECOND COMPLAINT TWO MULTI FUNCTION METERS NOT SHOWS DISPLAYS 1).AUTO TRANSFER SWITCH MODEL NO;-C2ADTLB30250KD00-4P-250A-ATS -2NOS 2) MULTI FUNCTION METER MODEL NO ;-EM6436H-RS485-METSEEM6436HCL10RS -2NOS SUPPLIER OF PANELS AT SRINIVASA ELECTRICALS KAKINADA SERVICE PERSON NAME RAJESH NUMBER 9030162810 TWO PANELS INVOICE ATTACHED Following attachments are linked to this email: 1.658.pdf 2.659.pdf | 2023-09-02 | 2023-09-15 10:30 | No | Warranty | Center for sight eye hospital | 4TH LN Mogalrajpuram sidhartha nagar labbipe | Vijayawada | 520010 | Andhra Pradesh | India FS ED&I CSP South Team ENERPRO ENGINEERING SOLUTIONS Vijayawada | SK SIRAJUDDIN_ENERPRO ENGINEERING SOLUTIONS VIJAYAWADA | Enerpro Engineering Solutions - 500012682 | METERS NOT WORKING | Repair |  | 9- Service Validated | 2023-09-14 10:31 |  |  | 28 | INR | 28 | ENM POWER PRODUCTS
WO-11296868 |  | 2023-09-28 16:12 | 2023-12-16 |  | 2023-09-22 19:26 | SRCE6KUXI | SRCE6KUXI | SRCE6KUXI | b21817005904 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-30 17:12 | No | Contract | PNB Housing Finance Limited | Noble Centre, 1st floor, laxmi mills signal, pappanayakan palayam null | Coimbatore | 641037 | Tamil Nadu | India FS South2 HBN CSP GRControlSystems Coimbatore | Edison V GRControlSystems Coimbatore | GR Control Systems-Coimbatore | PM Service done. Unit & Battery working fine call closed | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-30 17:22 |  |  | 0 | INR | 0 | ENM SECURE POWER
WO-11199088 | 103723933 | 2023-09-02 20:27 | 2023-09-02 | MCCB operation issue after installing coil | 2023-09-02 10:26 | LV563505 | LV563505 | LV563505 | TC-2022-W09-5 | LV563505E complaint operation issue after installing coil Site Address: NAVASASYAM DANDEKAR PVT LTD 624, ARENJA CORNER SECTOR 17, VASHI 6TH FLOOR PLOT NO. 71 NAVI MUMBAI-400703 Mr.Atul Shinde Sir 9673540064 | 2023-09-02 | 2023-09-04 16:57 | No | Warranty | Navasasyam Processing Equipments Pvt Ltd | 624, Arenja Corner,6th Floor,Plot No. 71,Sector 17, Vashi | Navi Mumbai | 400703 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Swamesh S_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the MCCB operation issue after installing coil. UV coil right side mechanism dis mental due to improper fitting. so we fitted properly. also observed red stopper of MCCB was damaged.so we fitted it and then taken on/off operation found ok. | Repair |  | 9- Service Validated | 2023-09-04 17:03 |  |  | 65 | INR | 65 | ENM POWER PRODUCTS
WO-11296890 |  | 2023-09-28 16:05 | 2023-12-16 |  | 2023-09-22 19:29 | SRCE6KUXI | SRCE6KUXI | SRCE6KUXI | B21811017868 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-30 11:14 | No | Contract | PNB Housing | UTR Tower 139 1st Floor Perundorai Road null | Erode | 638011 | Tamil Nadu | India FS South2 HBN CSP GRControlSystems Coimbatore | Mani kandan GRControlSystems Coimbatore | GR Control Systems-Coimbatore | PM done. Unit & Battery working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-30 11:23 |  |  | 0 | INR | 0 | ENM SECURE POWER
WO-11200583 | 103741224 | 2023-09-03 19:13 | 2023-09-02 |  | 2023-09-02 12:33 | LC1E160M5 | LC1E160M5 | LC1E160M5 |  | Inv. No : 9008677223 DOP: 12/8/2023 LC1E160M5 Qty:1 P: Screw issue M/s. SRI RAGAVENDRA CONTROLS SYSTEMS S.F.NO:786/7A,NARSAN THOTTAM, VELLANAI PATTI VI LLAGE, COIMBATORE - 641 048. Mr.Kalidas 9786613024 purchase@ragavendracontrol.com | 2023-09-02 | 2023-09-04 18:29 | No | Warranty | SRI RAGAVENDRA CONTROL SYSTEM | 786/7A,Narsan Thottam,Pinchikuttai Road Vellanaipatti (Po) | Coimbatore | 641048 | Tamil Nadu | India FS ED&I CSP South Team Power Pro Engineering Services Coimbatore | KV ARUNKUMAR_POWER PRO ENGINEERIG SERVICES COIMBATORE | Powerpro Engineering Services | WE HAVE VISITED THE SITE AND INSPECTED WE FOUND CONTACTOR FRONT COVER SCREW JAMMGED & NIOT TIGHT DUE TO WRONG THREAD BU CUSTOMER WE HACE RECTIFIED THE SAME TESTED AND FOUND OK TESTED AND ELECTRICALLY FOUND OK | Repair |  | 9- Service Validated | 2023-09-04 18:30 |  |  | 31 | INR | 31 | ENM POWER PRODUCTS
WO-11296901 |  | 2023-09-23 11:08 | 2023-09-16 |  | 2023-09-22 19:30 | APC Smart-UPS RC 6000VA 230V for India - No Batteries | SRC6KUXI | SRC6KUXI | B21418000501 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-26 17:38 | No | Contract | PNB Housing Finance Limited | 2nd Floor, Tulsi Complex, C-19/134, M-B, Shastri Nagar, Sigra null | Varanasi | 221010 | Uttar Pradesh | India FS North2 HBN CSP Sun Power Systems Varanasi | Deepak Shukla Sun Power Systems Varanasi | Sun Power Systems | PM has been done, UPS working fine. Correct Sr. No.- BQ1635000074(SRCE6KUXI) | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-26 17:40 |  |  | 15 | INR | 15 | ENM SECURE POWER
WO-11200594 | 103741437 | 2023-09-02 12:45 | 2023-09-02 | Part order request validated by Mr. Pradeep Patil Sir | 2023-09-02 12:39 | LV510347 | LV510347 | LV510347 | 10-2022-W34-6 | COMPLAIN FOR MCCB As Per The serial number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Jain batteries Global Pvt Ltd Plot number:- 310 A, Sector E, sanwer road indore 452015 Madhya Pradesh India Contact Person Details:- SITE CONTACT PERSON-MR ANISH JAIN JI CONTACT NO.-8349120000 Product and Issue:- 100A FP MCCB LV510347 10-2022-W34-6 mccb 1 pole not working | 2023-09-02 | 2023-09-04 16:09 | No | Warranty | Jain batteries Global Pvt Ltd | Plot number:- 310 A, Sector E, sanwer road null | indore | 452015 | Madhya Pradesh | India FS ED&I CSP West Team ABR Technical Service Indore | Chirag Jain_ABR Tecneical Services Indore | ABR Technical Services (9574) | Reached at site and checked MCCB and found its ON/OFF operation OK.Then we checked I/P voltage R4-415V YB-416B ,NR-251, NR-250V,NB-251V.Then we check o/p side voltage -NR-215V,,N4-250V, NB-28V RY-415V, YB-251V BR-250V. MCCB installed in panel not remove because plant is running condition. so we unable to checked MCCB internally. so only for customer satisfaction we recommended please replace 1No. MCCB | Repair |  | 9- Service Validated | 2023-09-04 16:11 | =S= Consig Fill up 226020706 |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11296932 |  | 2023-09-23 13:15 | 2023-09-16 |  | 2023-09-22 19:35 | SRC6KUXI | SRC6KUXI | SRC6KUXI | B21450000888 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-25 17:42 | No | Contract | PNB Housing Finance Limited | Plot No.TC/G 2/2, and TC/G 5/5, office number307 & 308, 3rd Floor, Commercial Complex, CYBER HEIGHTS, Vibhuti Khand, Gomti Nagar null | Lucknow | 226010 | Uttar Pradesh | India FS North2 HBN CSP Shriddha Power Solutions Pvt Ltd Lucknow | Anand Tiwari_Shriddha Power Solutions Pvt Ltd Lucknow | Shriddha Power Solutions Pvt. Ltd | FSE visited the site and done the PM. Now UPS is working fine. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-25 18:28 |  |  | 18 | INR | 18 | ENM SECURE POWER
WO-11200665 | 103728700 | 2023-09-02 15:29 | 2023-09-05 |  | 2023-09-02 14:25 | LV525313 | LV525313 | LV525313 |  | Complaint Register- Camex MCCB As Per The Invoice number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Camex Technologies Plot 82, Part & 83 Part, KINFRA Industrial Park, Tiruvalla 689581 Kerala India Contact Person Details:- Sreejith Ji 9446674479 Product and Issue:- LV525313 250A 4P MCCB , manual tripping is not working | 2023-09-02 | 2023-09-05 15:23 | No | Warranty | Camex Technologies | Plot 82, Part & 83 Part, KINFRA Industrial Park, | Tiruvalla | 689581 | Kerala | India FS ED&I CSP South Team Geartech Electric Cochin | Vineesh M_Geartech Electric Cochin | Geartech Electric ASC for Schneider Electric | Inspected the MCCB with HOM and found the problem with not tripping on the trip button. Now rectified the problem. (Sill under observation ) | Repair |  | 9- Service Validated | 2023-09-05 15:23 |  |  | 95 | INR | 95 | ENM POWER PRODUCTS
WO-11296961 |  | 2023-09-27 12:28 | 2023-09-27 | PM CALL | 2023-09-22 19:37 | SRCE6KUXI | SRCE6KUXI | SRCE6KUXI | B21635000105 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-27 19:27 | No | Contract | PNB Housing Finance Ltd | Door No. 1A, Chidambaranagar First Street null | Tuticorin | 628008 | Tamil Nadu | India FS South2 HBN CSP TechQPowerControls Madurai | N.M.Ananthan TechQPowerControls Madurai | Tech Q Power Controls-Madhurai | PM DONE, UPS GOOD WORKING | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-27 19:42 |  |  | 173 | INR | 173 | ENM SECURE POWER
WO-11200690 | 103741503 | 2023-09-02 16:11 | 2023-09-02 | NA | 2023-09-02 15:23 | GCR_MVS | GCR_MVS | GCR_MVS |  | ACB found faulty_SO 225593666 Dear Sir, The below mentioned ACB found faulty, there is a problem in connection of UV coil and closing coil. Please rectify the same immediately. Matter very urgent. ACB is in our factory. Factory contact person Mr. Rafique Molla (Mob: 9147089517) Factory Address: Ground Floor, Mouza - 58, Dag - 351, 348, Dakshin Ramchandrapur, Kolkata, South 24 Parganas, West Bengal - 700103 PS & PO - Narendrapur SO 225593666, ACB Part No: MVS20N4EW6L Invoice No: 9008604221 Invoice Date: 16.06.2023 Thanks & Regards Madhurima Basu VISSION AUTOMATION PVT LTD. (Authorized System Integrator of Schneider Electric) Dakshin Ramchandrapur, P.S & P. O - Narendrapur, South 24 Parganas, Kolkata - 700103 West Bengal. | 2023-09-02 | 2023-09-12 16:30 | No | Warranty | Vission Automation Pvt Ltd. | Dakshin Ramchandrapur Ps & Po Narendrapur South 24 Parganas | Kolkata | 700103 | West Bengal | India FS ED&I CSP East Team B.D Electroservices Kolkata | RAHUL RAY_B.D Electroservices Kolkata | B.D Electroservices(500017330) | We close this complain because panel builder already send defective material customer address. | Repair |  | 9- Service Validated | 2023-09-12 16:30 |  |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11296963 |  | 2023-09-29 19:00 | 2023-09-28 | P.M./ CALL | 2023-09-22 19:37 | SRCE6KUXI | SRCE6KUXI | SRCE6KUXI | B21635000105 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-29 19:25 | No | Contract | PNB Housing Finance Ltd | Door No. 1A, Chidambaranagar First Street null | Tuticorin | 628008 | Tamil Nadu | India FS South2 HBN CSP TechQPowerControls Madurai | P.Sankar TechQPowerControls Madurai | Tech Q Power Controls-Madhurai | P.M DONE, U[PS GOOD WORKLING | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-29 19:31 |  |  | 165 | INR | 165 | ENM SECURE POWER
WO-11200719 | 103742392 | 2023-09-02 17:42 | 2023-09-02 |  | 2023-09-02 15:59 | LC1D1506M7 | LC1D1506M7 | LC1D1506M7 |  | DOP: 13/12/2022 LC1D1506M7 Qty- 01 No's P: Coil issue Bharat Fritz Werner Ltd. No. 371 & 372, 10 Cross road, Peenya Indl. Area, Bangalore- 560058 Mr.Arun Mob No. : 8884559336 | 2023-09-02 | 2023-09-09 16:45 | No | Warranty | Bharat Fritz Werner Ltd. | No. 371 & 372, 10 Cross road, Peenya Indl. Area null | Bangalore | 560058 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Santhosh DP_P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | Inspected and found below mentioned 1)Ref: LC1D1506M7 S/N:PK21464 = 1 No contactor. Contactor not getting on because of coil was burnt out inside. Hence we will give new good warranty replacement after confirmation from FSE (Schneider) | Repair |  | 9- Service Validated | 2023-09-09 16:49 |  |  | 12 | INR | 12 | ENM POWER PRODUCTS
WO-11296985 |  | 2023-09-23 10:38 | 2023-09-16 |  | 2023-09-22 19:41 | SRCE6KUXI | SRCE6KUXI | SRCE6KUXI | b21812013658 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-23 18:05 | No | Contract | PNB Housing Finance Ltd | Ranjan plaza Kiliyallor kolachenkotta road Kollam null | Kollam | 691004 | Kerala | India FS South2 HBN CSP YEMYEMEnterprises Trivandrum | Akhil Nath.R YEMYEMEnterprises Trivandrum | Yemyem Enterprises | Preventive Maintenance Completed-UPS Working fine. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-23 18:13 |  |  | 77 | INR | 77 | ENM SECURE POWER
WO-11200720 | 103741772 | 2023-09-04 11:43 | 2023-09-02 |  | 2023-09-02 16:03 | LC1G185KUEN | LC1G185KUEN | LC1G185KUEN |  | CONTACTOR LC1G185KUEN not working As Per The Invoice The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- C&S AUTOMATION Shop no-11, Kanchanpur Tower, Mohddipur Gorakhpur 273008 Uttar Pradesh India Contact Person Details:- Pradeep Kumar Mob. 8467959702 Product and Issue:- LC1G185KUEN Coil power up issue in 1 quantity. | 2023-09-02 | 2023-09-11 16:31 | No | Warranty | C&S AUTOMATION | Shop no-11, Kanchanpur Tower, Mohddipur null | Gorakhpur | 273008 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Abhishek Patel Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found contactor having holding issue so we replaced. | Repair |  | 9- Service Validated | 2023-09-11 16:36 |  |  | 280 | INR | 280 | ENM POWER PRODUCTS
WO-11297657 |  | 2023-09-23 15:24 | 2023-09-16 |  | 2023-09-22 19:55 | SRCE6KUXI | SRCE6KUXI | SRCE6KUXI | B21540000278 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-30 13:31 | No | Contract | PNB Housing Finance Limited | MCH No- 15-24-173, Road No-1, KPHB Colony, 2nd Floor, Kukatpally null | Hyderabad | 500072 | Tamil Nadu | India FS South3 HBN CSP CENTRALDATASYSTEMS HYDERABAD | Nagesh CENTRALDATASYSTEMS HYDERABAD | Central Data Systems Pvt Ltd | visited site and checked ups on both battery and mains for 5 mins some batteries are weak condition informed to customer to replace batteries | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-30 13:37 |  |  | 16 | INR | 16 | ENM SECURE POWER
WO-11297659 |  | 2023-09-30 14:53 | 2023-12-16 |  | 2023-09-22 19:55 | SRCE6KUXI | SRCE6KUXI | SRCE6KUXI | B21540000278 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-30 14:59 | No | Contract | PNB Housing Finance Limited | MCH No- 15-24-173, Road No-1, KPHB Colony, 2nd Floor, Kukatpally null | Hyderabad | 500072 | Tamil Nadu | India FS South3 HBN CSP CENTRALDATASYSTEMS HYDERABAD | B Ramakrishna CENTRALDATASYSTEMS HYDERABAD | Central Data Systems Pvt Ltd | pm activity done ups working fine | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-30 15:01 |  |  | 16 | INR | 16 | ENM SECURE POWER
WO-11200769 | 103742653 | 2023-09-02 18:26 | 2023-09-04 | Validated By Prashant | 2023-09-02 17:09 | INH8451(BZ)-A | INH8451(BZ)-A | INH8451(BZ)-A | 8100009017 | COMPLAINT INH8451(BZ) :- 16 NOS NOT WORKING INH8452(BZ) :- 16 NOS NOT WORKING INH8454(BZ) :- 16 NOS NOT WORKING INH8455(BZ) :- 16 NOS NOT WORKING Dear All, ITC LTD. UNIT: ITC GRAND CENTRAL, 287, DR. BABASAHEB AMBEDKAR ROAD, PAREL,MUMBAI 400 012 Contact # 99875 67606 BILL # 1453 DT :- 18.07.2023 Regards Dhaval Jariwala / Nirav Jariwala Handheld:- 9987767377 / 9867363285 : order@sunilelectricco.com Invoice attached over same case. | 2023-09-02 | 2023-09-26 14:19 | No | Warranty | ITC Limited | ITC Grand Central 287, Dr. B. Ambedkar Road, Parel | Mumbai | 400012 | Maharashtra | India FS ED&I CSP West Team S K SERVICES Mumbai | Ganesh Tati_S K SERVICES Mumbai | S.K. Services (10237) | We Visited Site 6A 2 Way Switch is Properly Not Operating So Stuck issue 6A MMR Switch is Operating Ok But Indicator Not Operating Ok So Indicator Problem MMR Indicator Side Lock Broken Iusse We Check All Rooms Flat 1801 To 1817 All Operating Ok Raise The ZVO Next Visit | Repair |  | 9- Service Validated | 2023-09-26 17:33 | VIP FSR= No 3. FSR Request: Unavailability of the preferred FSR, need to depute Non VIP FSR(prashant kotian). =S= Consig Fill up 226019119 |  | 18 | INR | 18 | ENM POWER PRODUCTS
WO-11297705 |  | 2023-09-29 10:00 | 2023-09-16 |  | 2023-09-22 20:02 | APC SMART-UPS RC 6000VA 230V FOR INDIA - NO BATTERIES | SRCE6KUXI | SRCE6KUXI | B21607000068 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-29 15:58 | No | Contract | PNB Housing Finance Ltd | 4th Floor Mathrushree Plaza Vinus Corner Station Road Kolapur null | Kolapur | 416001 | Maharashtra | India FS West1 HBN CSP_Modular Electronics Pvt Ltd Kolhapur | Santosh Kambale_Modular Electronics Pvt Ltd Kolhapur | Modular Electronics Pvt Ltd-Kolhapur | On site checked UPS & Battery, UPS working ok. battery voltage ok PM done | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-29 16:05 |  |  | 30 | INR | 30 | ENM SECURE POWER
WO-11297732 |  | 2023-09-28 17:14 | 2023-12-16 |  | 2023-09-22 20:06 | APC Smart-UPS RC 6000VA 230V for India - No Batteries | SRC6KUXI | SRC6KUXI | B21431010140 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-29 15:30 | No | Contract | PNB Housing Finance Limited | 207 & 209 2nd Floor, Antriksh Bhawan, 22 KG Marg null | New Delhi | 110001 | Delhi | India FS North1 HBN CSP HITEK BUSINESS SYSTEMS PVT LTD Delhi | Mangal M_Hitek Business Systems New Delhi | Hitek Business Systems Pvt Ltd | Engineer this site UPS Preventive Maintenance done UPS working ok but address and UPS & UPS serial number mismatch Kindly update - UPS Model - SRCE6KUXIQ Serial No - BQ1837009059 | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-29 19:25 |  |  | 15 | INR | 15 | ENM SECURE POWER
WO-11297733 |  | 2023-09-28 17:08 | 2023-12-16 |  | 2023-09-22 20:06 | SRCE6KUXI | SRCE6KUXI | SRCE6KUXI | B21614001063 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-29 16:00 | No | Contract | PNB Housing Finance Limited | 207 & 209 2nd Floor, Antriksh Bhawan, 22 KG Marg null | New Delhi | 110001 | Delhi | India FS North1 HBN CSP HITEK BUSINESS SYSTEMS PVT LTD Delhi | Brajesh B_Hitek Business Systems New Delhi | Hitek Business Systems Pvt Ltd | Engineer this site UPS Preventive Maintenance done UPS working ok | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-29 19:21 |  |  | 15 | INR | 15 | ENM SECURE POWER
WO-11209210 | 103755481 | 2023-09-04 13:28 | 2023-09-04 |  | 2023-09-04 10:34 | LC1D18BD | LC1D18BD | LC1D18BD | 1021355 | Contactor Power Up issue by giving Coil supply As Per The serial number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Saini Enterprises Plot number:- 1510, Deep complex, Hala Majra Chandigarh 160002 Chandigarh India Contact Person Details:- Mr. Anand Ji 6284754844 Product and Issue:- LC1D18BD 1021355 Contactor Power Up issue by giving Coil supply | 2023-09-04 | 2023-09-04 13:31 | No | Warranty | Saini Enterprises | Plot number:- 1510, Deep complex, Hala Majra null | Chandigarh | 160002 | Chandigarh | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Vinod Kumar_Sharma Electric Chandigarh | Sharma Electric works(1003) | checked the contactor found plunger stuck. Hence faulty, replaced. LC1D18BD - 1 Nos. Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-04 14:55 |  |  | 20 | INR | 20 | ENM POWER PRODUCTS
WO-11297800 |  | 2023-09-23 10:38 | 2023-09-16 |  | 2023-09-22 20:15 | APC SMART-UPS RC 6000VA 230V FOR INDIA - NO BATTERIES | SRCE6KUXI | SRCE6KUXI | B21549000228 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-26 14:55 | No | Contract | PNB Housing Finance Ltd | 3rd Floor 16/104 Sri Siddivinayak Building Civil Line null | Kanpur Nagar | 208001 | Uttar Pradesh | India FS North2 HBN CSP BK Technologies Kanpur | Shakti kumar_B.K. Technologies Kanpur | BK Technologies | UPS PM done and working ok on both mode. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-26 14:59 |  |  | 16 | INR | 16 | ENM SECURE POWER
WO-11210602 | 103756504 | 2023-09-06 13:52 | 2023-09-04 |  | 2023-09-04 11:37 | GFP12CT23P | GFP12CT23P | GFP12CT23P |  | Schneider Electric India Pvt Ltd. No. 12 (A), Attibele Industrial Area, Neralur, Bangalore - 562 107 Sardar Pasha 9972552400 sardar.pasha@schneider-electric.com GFP12CT23P 10-2023-W28 damaged inside the packaging 04-09-2023 under warranty Not applicable Sardar Pasha 9972552400 04-09-2023 | 2023-09-04 | 2023-09-06 14:23 | No | Warranty | Schneider Electric India Pvt Ltd | 12( A), Attibele Industrial Area, Hosur Main Road, neralur | Bangalore | 562107 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | C Gunasekaran_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | We had visited the site and inspected,customer purchased GFP relay.Found CBCT get cracked mark in received condition. invoice no AA2730112929= 21 nos. We collected details and escalate to schneider. | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-07 07:30 |  |  | 40 | INR | 40 | ENM POWER PRODUCTS
WO-11297806 |  | 2023-09-23 11:54 | 2023-09-25 |  | 2023-09-22 20:16 | APC SYMMETRA LX 16kVA N+1 Rack-mount Frame, 220/230/240V OR 380/400/415V | SYAF16KRMI | SYAF16KRMI | QD1422260639 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-25 16:34 | No | Contract | Linked In Technology Information Pvt Ltd | Maker Maxity, 3 North Avenue, 4th Floor,Bandra Kurla Bandra-Kula Complex, Bandra (East) | Mumbai | 400051 | Maharashtra | India FS West1 HBN CSP_United Solutions Mumbai | Rohan Kamble United Solutions Mumbai | UNITED SOLUTIONS - MUMBAI | Online Preventive Maintenance has been done. Checked all parameter are ok. Checked UPS logs. Checked input and output cable. Check power module and battery module found very thing are ok. UPS is working good condition. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-25 16:40 |  |  | 10 | INR | 10 | ENM SECURE POWER
WO-11210771 | 103758585 | 2023-09-05 11:32 | 2023-09-04 |  | 2023-09-04 12:33 | MVS25N4NW6L | MVS25N4NW6L | MVS25N4NW6L | 10231260193 | ACB Rack In Rack-Out Issue As Per The serial number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Powertech Switchgears India Pvt. Ltd(140168) Plot No. 171, 172, 191 & 192, EHTP, Sector-56, Phase-5, Kundli Industrial Estate, Distt. Sonepat, Haryana, Pin Code- 131028 Sonepat 131028 Haryana India Contact Person Details:- Jitender kumar 7988203408 Product and Issue:- MVS25N4EW6L SERIAL NUMBER:- 10231260193 ACB Rack In Rack-Out Issue | 2023-09-04 | 2023-09-04 17:35 | No | Warranty | Powertech Switchgears India Pvt. Ltd(140168) | Plot No. 171, 172, 191 & 192, EHTP, Sector-56, Phase-5, Kundli Industrial Estate, Distt. Sonepat, Haryana, Pin Code- 131028 | Sonepat | 131028 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the ACB found rack in rack out issue after repairing now ACB found working ok. Email : id not provided by customer . | Repair |  | 9- Service Validated | 2023-09-05 12:00 |  |  | 65 | INR | 65 | ENM POWER PRODUCTS
WO-11297812 |  | 2023-09-26 11:35 | 2023-09-16 |  | 2023-09-22 20:17 | SRCE6KUXI | SRCE6KUXI | SRCE6KUXI | B21720000662 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-27 16:34 | No | Contract | PNB Housing Finance Ltd | 2nd Floor Cabin 7 & 8 Kushe Sadan K R Road Kodialvidal | Mangalore | 575003 | Karnataka | India FS South1 HBN CSP MeghaAssociates Mangalore | Prashanth Anchan MeghaAssociates Mangalore | Megha Associates-Mangalore-BLR008 | PM Done, ups working fine. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-27 16:45 |  |  | 8 | INR | 8 | ENM SECURE POWER
WO-11210993 | 103760747 | 2023-09-04 17:42 | 2023-09-04 |  | 2023-09-04 13:34 | LV563316 | LV563316 | LV563316 | 1023094 | LV563316 - 1023094 MCCB operation issue Site Address: GAJANAN POLYPLAST PRIVATE LIMITED Survey No. 793, Near Railway Crossing, Village Karua Morena 476001 Madhya Pradesh Mr. Deepak Agarwal 8949132152 | 2023-09-04 | 2023-09-05 15:17 | No | Warranty | GAJANAN POLYPLAST PRIVATE LIMITED | Survey No. 793, Near Railway Crossing, Village Karua null | Morena | 476001 | Madhya Pradesh | India FS ED&I CSP West Team ABR Technical Service Indore | Mayank Patidar_ABR Technical Services Indore | ABR Technical Services (9574) | reached at site as per customer MCCB given output on, off condition. then we check on/off operation and found ok. then we checked continuity of all three pole and found ok. then we checked i/p voltage and found RY-415V, YB-419, BR-416V AC. checked output voltage and found zero when MCCB on, off position and found satisfactory results. then we checked on load and found working properly also check with test button MCCB tripping ok no issue observed. so as per our primary observation its not a product issue so we are going to close this case. | Repair |  | 9- Service Validated | 2023-09-05 15:20 |  |  | 650 | INR | 650 | ENM POWER PRODUCTS
WO-11297830 |  | 2023-09-29 15:08 | 2023-09-29 |  | 2023-09-22 20:20 | SRCE6KUXI | SRCE6KUXI | SRCE6KUXI | B21806012890 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-29 16:03 | No | Contract | PNB Housing Finance Ltd | 1st Floor F 236 Balmev Plaza Modern Town Delhi Road null | Rohtak | 124001 | Haryana | India FS North2 HBN CSP Microvolt Communication Pvt Ltd Rohtak | Naveen N_Microvolt Communication Pvt Ltd Rohtak | Microvolt Communication Pvt. Ltd. - Rohtak - Chandigarh | PM visit Done ( UPS dead Due to LPS PCB missing in the UPS) | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-29 16:07 |  |  | 3 | INR | 3 | ENM SECURE POWER
WO-11211167 | 103762882 | 2023-09-04 20:36 | 2023-09-04 |  | 2023-09-04 14:29 | GCR_NW_CB | GCR_NW_CB | GCR_NW_CB |  | NW10H14PMD02.0A 10220350109 Qty:1 P: 1000A Spring Charge Issue M/S. Boeing India Pvt.Ltd, B2 Plot No.55-B, 56, 57, 59, Hitech ? Defence and Aerospace Park, Aerospace Sector Bangalore Urban - 562149 Kumar 9980448841 | 2023-09-04 | 2023-09-05 17:42 | No | Warranty | M/S. Boeing India PVT LTD | BIETCampus-PH-1A-B1 & Security Plaza Interior GCPlOT NO:-55-B56,57&59, HI- Tech, Defense aerospace Park ( Aerospace Sector) Devanhalli Village, Jala Hobli, Yelahanka Taluk | Bangalore | 562110 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Mohammad Riyaz_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | We had visited the site and checked the customer reported MTZ ACB.Fiund not getting ON in auto mode.Due to control neutral not getting proper.so we rectified the wiring issue and checked AUTO AND MANUAL MODE WORKING OK.There is no issues with our ACB. | Repair |  | 9- Service Validated | 2023-09-05 17:45 |  |  | 45 | INR | 45 | ENM POWER PRODUCTS
WO-11297832 |  | 2023-09-29 10:31 | 2023-12-29 |  | 2023-09-22 20:20 | SRCE6KUXI | SRCE6KUXI | SRCE6KUXI | B21806012890 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-29 15:58 | No | Contract | PNB Housing Finance Ltd | 1st Floor F 236 Balmev Plaza Modern Town Delhi Road null | Rohtak | 124001 | Haryana | India FS North2 HBN CSP Microvolt Communication Pvt Ltd Rohtak | Naveen N_Microvolt Communication Pvt Ltd Rohtak | Microvolt Communication Pvt. Ltd. - Rohtak - Chandigarh | PM visit Done ( UPS dead Due to LPS PCB missing in the UPS, serial# sticker not available on UPS) | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-29 16:03 |  |  | 3 | INR | 3 | ENM SECURE POWER
WO-11211179 | 103762963 | 2023-09-05 15:56 | 2023-09-04 |  | 2023-09-04 14:33 | LC1D95M7 | LC1D95M7 | LC1D95M7 | PK23094 | Contactor 1 pole open Issue As Per The SL no. The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Trela Footwear Exports D 38, Site C, Industrial Area, Sikandra Agra 282007 Uttar Pradesh India Contact Person Details:- Mr. Rajesh Ji 8630029787 Product and Issue:- LC1D95M7 PK23094 Contactor 1 pole open Issue | 2023-09-04 | 2023-09-07 11:00 | No | Warranty | Trela Footwear Exports | D 38, Site C, Industrial Area, Sikandra | Agra | 282007 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Monu Pandey_Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found contactor having humming sound issue , so we replaced. | Repair |  | 9- Service Validated | 2023-09-07 11:06 |  |  | 360 | INR | 360 | ENM POWER PRODUCTS
WO-11297847 |  | 2023-09-28 09:49 | 2023-09-28 |  | 2023-09-22 20:22 | SRC6000UXI | SRC6000UXI | SRC6000UXI | B21541004433 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-29 02:30 | No | Contract | PNB Housing Finance Limited | 2nd & 4th Floor Megha House ,opp Kotak Bank, Mithakhali Law Garden Road, Ellisbridge, null | Ahmedabad | 380006 | Gujarat | India FS West2 HBN CSP_Safal Solutions Ahmedabad | Ranjit Thakor Safal Solutions Ahmedabad | Safal Solutions | UPS PM HAS BEEN DONE AND UPS AND BATTERIES ARE WORKIG FINE. | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-28 17:21 |  |  | 3 | INR | 3 | ENM SECURE POWER
WO-11211265 | 103757063 | 2023-09-04 15:32 | 2023-09-04 | MPCB Handle issue | 2023-09-04 15:14 | TeSys GV2-LV equipment - Low voltage circuit breaker | TeSys GV2-LV equipment - Low voltage circuit breaker |  | GV2APN01 | Complaint : Cat No. GV2APN01 11 Qty - Faulty. As Per The Invoice copy The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Accusonic Controls Pvt. Ltd. Gate No-79 & 102, Savrgaon Mulshi, Pune 412106 Maharashtra India Contact Person Details:- Dharmendra Ghadage 7722093756 Product and Issue:- Cat No. GV2APN01 Schneider MPCB MPCB handle problem with 11 Nos supplied Fitment Issue As per the last visit done allignment has been done | 2023-09-04 | 2023-09-05 15:28 | No | Warranty | Accusonic Controls Pvt. Ltd. | Gate No-79 & 102, Savrgaon Mulshi, | Pune | 412106 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Samadhan S_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the MPCB Handle issue. panel door not opened. checked internal defect metallic part on that part excessive material found . finishing is not found . then we fitting that part and reassemble the part and checked operation of panel door found ok. | Repair |  | 9- Service Validated | 2023-09-05 15:36 |  |  | 52 | INR | 52 | ENM POWER PRODUCTS
WO-11297848 |  | 2023-09-28 09:54 | 2023-09-28 |  | 2023-09-22 20:22 | SRC6000UXI | SRC6000UXI | SRC6000UXI | B21528000432 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-22 | 2023-09-29 02:30 | No | Contract | PNB Housing Finance Limited | 2nd & 4th Floor Megha House ,opp Kotak Bank, Mithakhali Law Garden Road, Ellisbridge, null | Ahmedabad | 380006 | Gujarat | India FS West2 HBN CSP_Safal Solutions Ahmedabad | Ranjit Thakor Safal Solutions Ahmedabad | Safal Solutions | UPS PM HAS BEEN DONE AND UPS AND BATTERIES ARE WORKIG FINE. | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-28 17:32 |  |  | 3 | INR | 3 | ENM SECURE POWER
WO-11211269 | 103755640 | 2023-09-04 16:28 | 2023-09-04 | Relay not getting reset | 2023-09-04 15:16 | LRD16 | LRD16 | LRD16 |  | RE: Schneider Electric confirmation on closing Case 103658775 LRD16 operation issue Site Address: Virtuoso Projects & Engineers Pvt.Ltd Gat No.112, At Pimpalgaon,Post. Solu, Tal.Khed Pune 412105 Maharashtra Mr. Venkat Shinde 9373287100 | 2023-09-04 | 2023-09-05 10:42 | No | Warranty | Virtuoso Projects & Engineers Pvt.Ltd | Gat No.112, At Pimpalgaon,Post. Solu, Tal.Khed | Pune | 412105 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Samadhan S_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the Relay not getting reset.relay is on reset condition. we push reset button but it's not getting reset. also we checked add on block take continuity and observed this block NO contact not working. it's not getting NO to NC. so this product needs to be replaced. Required Material : LRD16 - 01 nos , LADN22 - 01 nos | Repair |  | 9- Service Validated | 2023-09-06 11:43 | =S= Consig Fill up 226018464 |  | 40 | INR | 40 | ENM POWER PRODUCTS
WO-11211334 | 103756525 | 2023-09-05 14:08 | 2023-09-04 |  | 2023-09-04 15:39 | LV540306 | LV540306 | LV540306 | 1022445 | SV POWER CONTROL- ISSUE IN 400A MCCB 3P. LV540306 - 1022445 MCCB is not getting OFF Site Address: Tata Croma CHADHA MALL, GT Road, KARTAR NAGAR MOGA 142001 Punjab Mr. Ashish Ji 7814751992 7738648701 | 2023-09-04 | 2023-09-05 14:09 | No | Warranty | Tata Croma | CHADHA MALL, GT Road, KARTAR NAGAR Near ITI | MOGA | 142001 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the mccb found not getting on due to Lever bend. It may be due to customer mishandling. Hence no replacement given to customer. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-05 14:52 |  |  | 75 | INR | 75 | ENM POWER PRODUCTS
WO-11211568 | 103740694 | 2023-09-06 10:37 | 2023-09-06 |  | 2023-09-04 16:38 | GCR_CVS_T1_06 | GCR_CVS_T1_06 | GCR_CVS_T1_06 | TC 2022 W23 6 | MCCB ISSUE @ EVEY TRANS TIRUPATI Dear Team, We have been reported 1 nos 250 Amp MCCB malfunctioning issue from one of our Evey site - rating plate picture attached for your reference Please look into and arrange replacement of the same on an urgent basis Site and contact person details given below for your needful action Site Address:- EVEY TRANS (JAB) PRIVATE LIMITED C/o APSRTC BUS DEPOT, HARE KRISHANA ROAD, SRINIVASA NAGAR, DWARAKA NAGAR,,,,TIRUPATI, ANDHRA PRADESH, 517507, IN Contact Person Mr Mouli - 9398890034 Best Regards, Ankit Kumar ? Service Advisor Sudhir Power Ltd. Plot No.1 ¦E.H.T.P.¦Sector 34 ¦Gurgaon-122001 ¦Haryana¦ India Mob.: +91-9319981890 ¦Office: +91-124-4275851 ¦ Fax: +91-124-4168010/ 20 Email: servicesupport@sudhirpower.com ¦ Web: www.sudhirpower.com signature | 2023-09-04 | 2023-09-06 20:30 | No | Warranty | EVEY TRANS (JAB) PRIVATE LIMITED | C/o APSRTC, ALIPIRI BUS DEPOT,,,,TIRUPATI, ANDHRA PRADESH, | Chittoor | 517501 | Andhra Pradesh | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | MCCB not Working | Repair |  | 9- Service Validated | 2023-09-08 17:54 |  |  | 145 | INR | 145 | ENM POWER PRODUCTS
WO-11211575 | 103762820 | 2023-09-05 12:51 | 2023-09-04 |  | 2023-09-04 16:40 | MVS12N4MW6L | MVS12N4MW6L | MVS12N4MW6L |  | As Per The Invoice copy The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- L.S. POWER CONTROL PVT. LTD Plot No - C 440 - C 443, Ansal Pioneer Industrial Park, Village - Pathreri, Bilaspur Gurgaon 122413 Haryana India Contact Person Details:- Chandan Kushwaha. Mo, No- +91 8707386430 WhatsApp- 9651834450 Product and Issue:- Item Description- ACB 1250A FP MDO 50KA ET6G MVS Cat no-MVS12N4MW6L Qty-01 Nos RACKIN- RACKOUT ISSUE | 2023-09-04 | 2023-09-05 12:53 | No | Warranty | L.S. POWER CONTROL PVT. LTD | Plot No - C 440 - C 443, Ansal Pioneer Industrial Park, Village - Pathreri, Bilaspur | Gurgaon | 122413 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the ACB found not working after repair now ACB found working ok/. Email : id not provided by customer . | Repair |  | 9- Service Validated | 2023-09-05 14:43 |  |  | 56 | INR | 56 | ENM POWER PRODUCTS
WO-11211850 | 103757026 | 2023-09-06 14:43 | 2023-09-04 |  | 2023-09-04 19:08 | GV2ME10 | GV2ME10 | GV2ME10 |  | Please register complaint of PART NO.- GV2ME10 , QTY ? 1 nos GV2ME10 operation issue Site Address: JOY D-ZIGN ENGINEERS PRIVATE LIMITED PLOT NO-13, ROAD NO-1 A, MUNDKA UDYOG NAGAR WEST DELHI-110041 Contact No. :- Mr. Sunil :8826014411 | 2023-09-04 | 2023-09-06 14:46 | No | Warranty | Joy Design Engineers Pvt Ltd | Plot No-13, Road No-1A, Mundka Udyog Nagar, | New Delhi | 110009 | Delhi | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mpcb found push button broken . MPCB packing box found broken .Hence no replacement given to customer. Email : id not provided by customer . | Repair |  | 9- Service Validated | 2023-09-06 14:57 |  |  | 25 | INR | 25 | ENM POWER PRODUCTS
WO-11213590 | 103755955 | 2023-09-05 20:37 | 2023-09-05 |  | 2023-09-05 09:29 | LC1G150KUEN | LC1G150KUEN | LC1G150KUEN |  | LTMR & 150A POWER CONTACTOR defective at site (PHOTOGRAPH ATTACHED) | 2023-09-05 | 2023-09-12 17:00 | No | Warranty | PCBL (TN) Limited (Chennai _ EPC) | No A-7, SIPCOT Industrial Park, Thervoy Kandigai, Gummidipoondi Taluk, | Tiruvallur | 601202 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Site Visit Done | Repair |  | 9- Service Validated | 2023-09-12 20:57 |  |  | 70 | INR | 70 | ENM POWER PRODUCTS
WO-11213597 | 103765618 | 2023-09-05 19:58 | 2023-09-05 |  | 2023-09-05 09:33 | GCR_NSX | GCR_NSX | GCR_NSX | AA3330052568 | RE: WO Re-assign Request : WO-11163247, Feather lite Developers | 2023-09-05 | 2023-09-05 18:00 | No | Warranty | Feather lite Developers | Sy. no 203/10B, Pallavaram-Thoraipakkam Road, (1200 Ft Radial Road) Pallavaram | Chennai | 600043 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Site Visit Done | Repair |  | 9- Service Validated | 2023-09-05 20:18 |  |  | 48 | INR | 48 | ENM POWER PRODUCTS
WO-11213671 | 103766557 | 2023-09-05 11:11 | 2023-09-05 |  | 2023-09-05 10:27 | LRD14 | LRD14 | LRD14 | inv | Name of Customer:-GAYATRI ELECTRICALS Site Address:-1810/1, PADA POLE GANDHI ROAD Ahmedabad, 380001 Name of contact person at site:-Bhavin bhai Contact Phone / Mob. No:-9898331268.00 Defective product details:-LRD14(1QTY), Invoice no.:-PSI/22002240(16/03 | 2023-09-05 | 2023-09-11 11:25 | No | Warranty | Gayatri Electricals | 4, Milancomplex, Cross Road, Chattral | Ahmedabad | 380025 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Mistri Anik Engineering Ahmedabad | Anik Engineering (554) | LRD14 - NC contact not working - FR LRD10 - stop button not working - FR A9KF71206 - dolly free A9KF71232 - dolly free A9KF71463 - dolly free A9KF71432 - Dolly free A9KF71416 - dolly free A9KF71440 - dolly free A9KF7146 - 3 nos - dolly free - FR | Repair |  | 9- Service Validated | 2023-09-11 11:25 | =S= Consig Fill up 226035395 |  | 15 | INR | 15 | ENM POWER PRODUCTS
WO-11214296 | 103769108 | 2023-09-07 15:22 | 2023-09-05 |  | 2023-09-05 10:44 | MEHVCHDY150A44 | MEHVCHDY150A44 | MEHVCHDY150A44 |  | DOP: 14/1/2023 MEHVCHDY150A44 ME-F4720663 Qty:1 P: No output ACB India Ltd Dipka Washery Behind Dipka Police Station P.O Gevra Project, Korba, Chhattisgarh 495452 Contact Person Name - Rajesh S Nair Mob- 9425534138 | 2023-09-05 | 2023-09-08 12:00 | No | Warranty | ACB India Ltd | Dipka Washery Behind Dipka Police Station P.O Gevra Project, null | Korba | 495452 | chhattisgarh | India FS ED&I CSP East Team SOMDEV & COMPANY RAIPUR | SOUMYA BEHERA_SOMDEV & COMPANY RAIPUR | Somdev & Company | after checking the capacitor through capacitance meter the value is not showing so we replace the material. | Repair |  | 9- Service Validated | 2023-09-08 17:16 |  |  | 250 | INR | 250 | ENM POWER PRODUCTS
WO-11214882 | 103768836 | 2023-09-06 11:03 | 2023-09-05 |  | 2023-09-05 10:52 | MEHVCHDY050A44 | MEHVCHDY050A44 | MEHVCHDY050A44 |  | DOP: 1/10/2022 MEHVCHDY050A44 L5263394 Qty:1 P: Not Working CHEMENGI GUMS AND INDUSTRIES E1 278 Agro Food Park Boranada Jodhpur -342012 India NAVNEET SHARMA 9982177222 navneet.chemengi2@gmail.com | 2023-09-05 | 2023-09-11 18:16 | No | Warranty | CHEMENGI GUMS AND INDUSTRIES | E1 278 Agro Food Park Boranada null | Jodhpur | 342012 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Amarjeet Singh Sharma Electric Jaipur | Sharma Electric Works | checked the capacitor found derated. hence faulty, replaced. MEHVCHDY050A44 - 1 Nos. Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-12 11:19 |  |  | 350 | INR | 350 | ENM POWER PRODUCTS
WO-11215297 | 103767513 | 2023-09-05 15:07 | 2023-09-05 |  | 2023-09-05 10:58 | GCR_MTZ1_CB | GCR_MTZ1_CB | GCR_MTZ1_CB | 10232160014 | FW: Schneider Service Engineer Required for Shakthi Electricals----MTZ212H16.0x3PEDO ACB Rack in / Out problem As Per The serial number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Power Control Equipments No. 40A, 3rd Road Jigani Industrial Area Bengaluru - 560105 Contact Person Details:- Mr. Vijay kumar Joshi 9900981131 Product and Issue:- SCHNEIDER MAKE MTZ ACB, 1250A, 3P, 65kA, MDO, MTZ212H16.0x3PEDO RACK IN & RACK OUT PROBLEM Sl No:10232160014. As per the discussion with mr. Vijay, Breaker is having Rack In rack Out issue, Indication is not properly giving. | 2023-09-05 | 2023-09-05 16:01 | No | Warranty | Power Control Equipments Unit - 2 | No. 57, 3rd Road, Jigani Industrial Area | bangalore | 562106 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Mohammad Riyaz_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | i had visited the site and checked the customer reported acb chassis, the problem found was acb rack-in/ rackout issue. we dismantled and assembled again then checked the rack-in, rack-out operation found working ok. the same shown to the customer. | Repair |  | 9- Service Validated | 2023-09-05 21:07 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11215412 | 103766398 | 2023-09-06 16:51 | 2023-09-05 |  | 2023-09-05 11:35 | LC1D25M7 | LC1D25M7 | LC1D25M7 |  | One pole out put in not showing of contractor LC1D25M7 qty.-01no. Dear sir, One pole out put in not showing of contractor LC1D25M7 Coil voltage 230vac from Schneider Electric. Bill no. aa2730118362 DT. 09-Aug-2023 So please to be replaced its. With Regards Vinay Shukla 09599039110 Add.-Vidhyut control (India) Pvt. Ltd. D-12 & 13, Sec-17, Kavi Nagar Indl. Area, Ghaziabad:- 201002. Email:-qc@vcipl.net | 2023-09-05 | 2023-09-12 15:33 | No | Warranty | Vidhyut Control India Pvt. Ltd. | D-12, Sector-17, Kavi Nagar Industrial Area, | Ghaziabad | 201002 | Uttar Pradesh | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the contactor found phase missing, Hence faulty replaced. LC1D25M7 - 1 nos GFP12CT24P - 1 nos Email : id not provided by customer | Repair |  | 9- Service Validated | 2023-09-12 15:38 |  |  | 52 | INR | 52 | ENM POWER PRODUCTS
WO-11215591 | 103785984 | 2023-09-06 15:16 | 2023-09-05 |  | 2023-09-05 12:57 | MEHVCSDY250A44PB | MEHVCSDY250A44PB | MEHVCSDY250A44PB |  | MEHVCSDY250A44PB ME-M3233387 ME-M3233383 ME-M3173217 ME- L0873429 Qty: 4 P: Not taking load Nirmal Balaji Majra road Brahman Naultha Village Panipat 132145 Ankit +917459904638 8299255764 ankitchaudhry7459@gmail.com | 2023-09-05 | 2023-09-09 16:21 | No | Warranty | Nirmal Balaji | Majra road Brahman Naultha Village null | Panipat | 132145 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the capacitor found derated and mcb found dolly free. Hence faulty replaced. MEHVCSDY250A44 - 2 Nos. A9N3P63C - 1 Nos. email : ankitchaudhry7459@gmail.com | Repair |  | 9- Service Validated | 2023-09-09 16:24 |  |  | 165 | INR | 165 | ENM POWER PRODUCTS
WO-11215665 | 103766364 | 2023-09-06 11:03 | 2023-09-05 |  | 2023-09-05 13:22 | EZC250N4250 | EZC250N4250 | EZC250N4250 | 8ADL-2022-W45-3 | Mccb pole open EZC250N4250 Serial no- 8ADL -2022-W-45-3 Problem - pole open y phase Site Address: Leprosy mission trust hospital Address - national highway Lucknow faizabad Barabanki UP Pin code - 225001 Contact person - md.Amir khan Contact No.- 7524891341 | 2023-09-05 | 2023-09-06 17:14 | No | Warranty | THE LEPROSY MISSION HOSPITAL | Barabanki, Faizabad main road null | Barabanki | 225204 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Aman Khare_Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found MCCB having pole open issue so we replaced. | Repair |  | 9- Service Validated | 2023-09-06 17:16 |  |  | 33 | INR | 33 | ENM POWER PRODUCTS
WO-11215848 | 103769768 | 2023-09-05 18:06 | 2023-09-07 |  | 2023-09-05 14:19 | LC1D506M7 | LC1D506M7 | LC1D506M7 |  | Complaint - BFW LC1D1506M7- 02 No's Craftsman automation Sriperumbud, Kancheepuram H6600 sl no 201 As Per The Invoice copy The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Craftsman Automation Limited Plot No. L-3, Sipcot Industrial Park, Phase II, Sriperumbudur, Mambakkam Post KANCHIPURAM 602106 Tamil Nadu India Contact Person Details:- Mr. Hariharan Mob No. : 7824805325 Product and Issue:- LC1D1506M7 - 02 Nos. Coil issue | 2023-09-05 | 2023-09-11 17:00 | No | Warranty | Craftsman Automation Limited-Sriperumbudur (BFW) | Plot No. L-3, Sipcot Industrial Park, Phase II, Sriperumbudur, Mambakkam Post | KANCHIPURAM | 602106 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | During our site visit We give External 230V AC Supply to the Contactor is not Working. | Repair |  | 9- Service Validated | 2023-09-12 20:25 | Hi Team, Same material LC1D1506M7 3 nos Zfre booked in this work order WO-11215848 Zvo : 226053253 |  | 40 | INR | 40 | ENM POWER PRODUCTS
WO-11216065 | 103791797 | 2023-09-05 15:57 | 2023-09-05 |  | 2023-09-05 15:29 | NA04004V | NA04004V | NA04004V |  | SERVICE FORM NO 6 | 2023-09-05 | 2023-09-05 10:51 | No | Warranty | Second Inning Enterprises | PLOT NO. PAP-R-108, TTC IND. AREA, NEAR ARUNA INDUSTRY, OPP. THANE BELAPUR ROAD, MIDC RABALE, NAVI MUMBAI | Navi Mumbai | 400701 | Maharashtra | India FS ED&I CSP West Team R P Electrical Mumbai | Samrat Pawaskar R P Electrical Mumbai | R P Electrical | ATS is not working in auto mode found that ATS showing alarm. Reset the ATS fault was reset. Took operation working Ok in auto mode. | Repair |  | 9- Service Validated | 2023-09-06 10:55 |  |  | 23 | INR | 23 | ENM POWER PRODUCTS
WO-11216080 | 103792098 | 2023-09-06 17:06 | 2023-09-05 |  | 2023-09-05 15:37 | LC1D40AF7 | LC1D40AF7 | LC1D40AF7 | 8B23131 | Contactor Plunger not moving- LC1D40AF7 As Per The serial number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- chopra electrical BE 303 hari nagar delhi 110064 Delhi India Contact Person Details:- Mr. Akash Chopra 9999808544 Product and Issue:- LC1D40AF7 Serial number:- 8B23131 Plunger not moving | 2023-09-05 | 2023-09-07 17:06 | No | Warranty | chopra electrical | BE 303 hari nagar | delhi | 110064 | Delhi | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the contactor found coil not working, Hence faulty replaced. LXD3F7 - 1 nos Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-07 17:15 |  |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11216109 | 103768889 | 2023-09-07 14:21 | 2023-09-05 |  | 2023-09-05 15:57 | MVS16N4NW6L | MVS16N4NW6L | MVS16N4NW6L | 1023272 | RE: Defective breaker & Bezel recived, Case: 103684442, [ thread::RR5bsF0UclaRZBQzCgcRbz4:: ] As Per The serial number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- AR ENGINEERS Plot No 34A 35B 35C Sector 11 IIE SIDCUL Haridwar HARIDWAR 249403 Uttarakhand India Contact Person Details:- Ujjwal Singh- +91-7055702819 Product and Issue:- MVS16N4NW6L 1023272 RACK IN RACK OUT ISSUE | 2023-09-05 | 2023-09-07 14:25 | No | Warranty | AR ENGINEERS | Plot No 34A 35B 35C Sector 11 IIE SIDCUL Haridwar | HARIDWAR | 249403 | Uttarakhand | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the ACB found not getting rack out / stuck in b/w cradle in test mode. Set right the same and now working ok. Also checked by ACB door facia found broken it might be broken in transist. Hence suggest to customer kindly inform to customer care team. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-07 14:35 |  |  | 215 | INR | 215 | ENM POWER PRODUCTS
WO-11216343 | 103796134 | 2023-09-06 12:57 | 2023-09-05 |  | 2023-09-05 17:51 | LC1D32M7 | LC1D32M7 | LC1D32M7 | 1022084 | LC1D32M7---Phase missing Issue As Per The serial number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Jassal Electrical Dehra Mandi, Jalandhar Bypass, Bahadur k Road, Opposite Mini King Factory Ludhiana 141008 Punjab India Contact Person Details:- Mr. Jitendra Kumar 6356000056 Product and Issue:- MODEL NUMBER:- LC1D32M7 SERIAL NUMBER:- 1022085 Phase missing Issue | 2023-09-05 | 2023-09-07 11:38 | No | Warranty | Jassal Electrical | Dehra Mandi, Jalandhar Bypass, Bahadur k Road, Opposite Mini King Factory | Ludhiana | 141008 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the contactor found not giving output i. Hence faulty , but when we try to scan , nothing shown, Hence we will discuss this matter with company. (Product might be duplicate ). email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-07 11:54 |  |  | 25 | INR | 25 | ENM POWER PRODUCTS
WO-11219275 | 103786626 | 2023-09-06 17:06 | 2023-09-06 |  | 2023-09-06 09:46 | LV563305 | LV563305 | LV563305 | 1022363 | FW: complaint Faulty MCCB need replacement. As Per The SL number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Shri Bajrang Chemical Distillery LLP Kh. No. 1151/2 , Tehsil- Arang, Arang national Highway Road Raipur 493221 Chhattisgarh India Contact Person Details:- Contact Person Name- Vibhuti Bhushan jha Mob No. -9337045010 Product and Issue:- Part Code- LV563305 Serial number:- 1022363 So No. - 225491868 - 28/02/2023 - SPA R phase missing Issue | 2023-09-06 | 2023-09-15 12:00 | No | Warranty | Shri Bajrang Chemical Distillery LLP | Kh. No. 1151/2 , Tehsil- Arang, Arang national Highway Road null | Raipur | 493221 | chhattisgarh | India FS ED&I CSP East Team SOMDEV & COMPANY RAIPUR | SOUMYA BEHERA_SOMDEV & COMPANY RAIPUR | Somdev & Company | the mccb R-point is not getting power after switching it on so we replace the same. | Repair |  | 9- Service Validated | 2023-09-15 10:36 |  |  | 34 | INR | 34 | ENM POWER PRODUCTS
WO-11219339 | 103767047 | 2023-09-06 12:32 | 2023-09-06 |  | 2023-09-06 10:33 | LC1D50AF7 | LC1D50AF7 | LC1D50AF7 | 8B21274 | Fwd: LC1D50AF7 8B21274 dist invoice shared operation issue Site Address: Sahjanand Electric, Shop # F4, R16 Arcade Walia Road Akhleshwar Dist:- Bharuch Bharuch 393002 Gujarat Mr. Kirit 9033177910 | 2023-09-06 | 2023-09-07 11:59 | No | Warranty | Kamdhenu Mineral | Sahjanand Electric, Shop # F4, R16 Arcade Walia Road Akhleshwar Dist:- Bharuch null | Bharuch | 393002 | Gujarat | India FS ED&I CSP West Team Jay Services Vadodara | Ghanshyam Kachiya_Jay Services Vadodara | Jay Services | We visited at site & checked contactor found physically ok. We test contactor ON-OFF operation found ok. But it is Y phase pole continuity open. R & B phase found ok. All I/C & O/g terminals are ok. Now we replace contactor from our distributor stock. | Repair |  | 9- Service Validated | 2023-09-07 11:59 | =S= Consig Fill up 226030546 |  | 103 | INR | 103 | ENM POWER PRODUCTS
WO-11221109 | 103814934 | 2023-09-06 11:47 | 2023-09-06 |  | 2023-09-06 11:34 | LC1D09N7 | LC1D09N7 | LC1D09N7 | 102235 | LC1D09N7 - 102235 operation issue Site Address: Sai Samarth Industries S No. 173 , Nagamallithota junction, kakinada, Kakinada 533005 Andhra Pradesh Mr. Avinash Kumar 8328307504 | 2023-09-06 | 2023-09-11 17:18 | No | Warranty | Sai Samarth Industries | S No. 173 , Nagamallithota junction, kakinada, | Kakinada | 533005 | Andhra Pradesh | India FS ED&I CSP South Team Voltamp Electrical Works Visakhapatnam | Chinni SaiKumar_VOLT AMP ELECTRICAL WORKS Visakhapatnam | Voltamp Electrical Works | Visited the site and found above the Tesys Power Contractor is not working so today we have observed the problem power contactor and we give the input voltage 230 V but contactor inside coil issue and we check the on site voltage 230 V perfect is ok so zvo material replaced | Repair |  | 9- Service Validated | 2023-09-11 17:19 | Hi Team, Material booked zfre Zvo : 226040566 |  | 180 | INR | 180 | ENM POWER PRODUCTS
WO-11221117 | 103815143 | 2023-09-06 16:42 | 2023-09-06 |  | 2023-09-06 11:37 | LC1D32M7 | LC1D32M7 | LC1D32M7 | 1022034 | LC1D32M7--Phase missing Issue As Per The serial number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Krishna Electrical J Block 2818, GIDC Narela Industrial Area, Bhorgarh Delhi 110040 Delhi India Contact Person Details:- Pankaj Goyel 9212027264 Product and Issue:- LC1D32M7 SERIAL NUMBER:- 1022034 Phase missing Issue | 2023-09-06 | 2023-09-06 16:44 | No | Warranty | Krishna Electrical | J Block 2818, GIDC Narela Industrial Area, Bhorgarh | Delhi | 110040 | Delhi | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the contactor found E- core lock damaged , Hence no replacement given to customer. Email : id not provided by customer . | Repair |  | 9- Service Validated | 2023-09-06 16:48 |  |  | 65 | INR | 65 | ENM POWER PRODUCTS
WO-11304378 | 104236698 | 2023-09-25 11:33 | 2023-09-25 |  | 2023-09-25 11:20 | Leonardo EV,DX,R407C,EC Fan,TUAV0721A,Upflow With Heater & Humidifier | TUAV0721AN003 | TUAV0721AN003 | ZK1542009172 | AMC P: BMS Offline S: AMC | 2023-09-25 | 2023-09-22 18:05 | No | Contract | Godfrey Phillips India Limited | Plot 19 , TTC Industrial area , Opp Rabale Station , Rabale , | Thane | 400701 | Maharashtra | India FS West1 Cooling CSP Shree Krishma Services Mumbai | Mahendra Suryabali Sharma_Shree Krishma Services Mumbai | Shree Krishna Services | AMC site visit done for PAC unit 2 no link alarm. PAC unit not working. As per check PAC unit bisplat no link check controller board nut proper working. Need to Replace Required. | Repair |  | 10- Closed | 2023-09-25 15:37 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11221188 | 103815530 | 2023-09-06 16:59 | 2023-09-06 |  | 2023-09-06 11:50 | Masterpact NW | GCR_NW_CB | GCR_NW_CB | 10232440037 | NW40 ACB Chassis Shutter Damage | 2023-09-06 | 2023-09-14 22:37 | No | Warranty | Switchgear and Control Technics Pvt.Ltd. | 152, Bommasandra Ind Area, Hosur Road, Anekal Taluk, | Bangalore | 560099 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Mohammad Riyaz_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | As per previous inspection WO-11102187, now approval taken from SE and ZVO directly booked to SCTPL.customer received new chasis,so we closed thos WO. | Repair |  | 9- Service Validated | 2023-09-17 22:43 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11221262 | 103815938 | 2023-09-06 13:59 | 2023-09-06 |  | 2023-09-06 12:05 | GCR_MVS | GCR_MVS | GCR_MVS |  | 9008599014 DOP: 13/6/2023 10232230238 MVS20N4NW6L Qty:1 P: Damage M/s. STAR Switchgears NO.15, 3rd MAIN RD, BEGUR ROAD CROSS BOMMANAHALLI, BANGALORE - 560068 Hari (7760411568) | 2023-09-06 | 2023-09-07 15:49 | No | Warranty | M/s. STAR Switchgears | NO.15, 3rd MAIN RD, BEGUR ROAD CROSS BOMMANAHALLI, null | Bnagalore | 560068 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | C Gunasekaran_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | We had visited the site and checked the customer reported ACB.Founded 3wire TB get broken condiition.For customer urgency we replaced 3nos TB from our stock and checked working ok.There is no issues after fixing.so we close this WO. | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-08 07:53 |  |  | 25 | INR | 25 | ENM POWER PRODUCTS
WO-11304572 |  | 2023-09-25 17:31 | 2023-09-26 |  | 2023-09-25 12:13 | Easy UPS 3S 20 kVA 400 V 3:3 UPS for external batteries | E3SUPS20KH | E3SUPS20KH | 9E2153T10047 | PM | 2023-09-25 | 2023-09-26 17:01 | No | Commercial Action - Sales | Meritor CVS India Pvt Ltd. | Plot No. 36, Hootagalli Industrial Area null | Mysore | 570018 | Karnataka | India FS South1 HBN CSP Aspire Infra Solutions Bangalore | Nithin Kumar Aspire Infra Solutions Bangalore | Aspire Infra Solutions | Preventive Maintenance Completed | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-26 17:31 |  |  | 146 | INR | 146 | ENM SECURE POWER
WO-11221321 | 103814765 | 2023-09-06 13:05 | 2023-09-06 | Escalated the case to SEI | 2023-09-06 12:33 | LC1D65AM7 | LC1D65AM7 | LC1D65AM7 |  | KNACK PACKAGING PVT LTD (DEV ELE) Checklist for Complaint Registration Doc. Ref :- SE/CCC/22-23/351 1 Company Name & Complete Address with pin code - Where product is installed KNACK PACKAGING PVT LTD (DEV ELECTRIC CORPORATION VITHALAPUR) 2 SIDE ADRESS Block No. 493,497 B/H Shankar Parvati Cotton Mill,Kadi, Kadi thol Road, Village Borisana, Dist Mehsana, Gujarat 3 Contact Person at Site: Name & Mobile No. Bakulbhai - M :- 9925199633 4 Altemate Mobile No. : Bhavin Shroff -Cell No. : +91 63522 21342 5 Contact Person at Site - Email Address**. 6 Defective Product Model/Part No (Pls refer FAQ sheet ) LC1D65AM7 6-a Defective Product Model/Part No (Pls refer FAQ sheet ) 6-b Defective Product Model/Part No (Pls refer FAQ sheet ) 6-c Defective Product Model/Part No (Pls refer FAQ sheet ) 6-d Defective Product Model/Part No (Pls refer FAQ sheet ) 6-e Defective Product Model/Part No (Pls refer FAQ sheet ) 6-f Defective Product Model/Part No (Pls refer FAQ sheet ) 7 Nature of Defect* - Defects Video and Photographs HEATING PROBLEM 8 Shutdown availability if applicable 9 POP - SE Authorised Partner Invoice soft copy Invoice No - 106218 , Date - 22/07/2023 10 Photograph of product where Serial No/Batch Code or Date of Manufacturing printed - Please refer FAQ sheet 11 Name & phone No: of person registering the complaint SHAILESH MAKWANA - 9924227896 Points 1,2,3,4,5 & (7or8) are mandatory. * Kindly share defect symptoms instead of "Not working", Please share the link of large files(product photoes or videoes) | 2023-09-06 | 2023-09-12 12:06 | No | Warranty | Knack Packaging Pvt Ltd | Block No. 493,497 B/H Shankar Parvati Cotton Mill,Kadi, Kadi thol Road, Village Borisana, null | Mehsana | 382715 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Nijesh Patel_Anik Engineering Ahmedabad | Anik Engineering (554) | visited site and checked the product, Observed physically ok, No burnt termnal or physical damage observed, Customer using product in heating application, Having Input coltgae - 407-407-408 vac, and 32 - 33 - 33 Amps of load, as per customer the contactor got stuck, for primary observation we opened the contact and observed the power tips of the contact is stuck, we have requested the data from customer like load, no of opeartion, SLD and excalaed the case | Repair |  | 9- Service Validated | 2023-09-12 12:07 | =S= Consig Fill up 226047062 |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11221387 | 103791041 | 2023-09-07 10:36 | 2023-09-06 | LRE Reset Button Not operating | 2023-09-06 13:00 | LRE14 | LRE14 | LRE14 |  | Complaint As Per The Invoice copy The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- PROEXCEL SYSTEMS PROEXCEL SYSTEMS "Mahasainik Industrial Estate ,Shop No -60 , Plot : T-153/1 pimpri Industrial Area , Bhosari , Pune - 411 026 Contact Person Details:- SUNIL DESAI 9766480790 Product and Issue:- LRE14 & LADS2 SCHNEIDER Not working NO/nc points Issue as per customer | 2023-09-06 | 2023-09-07 11:02 | No | Warranty | PROEXCEL SYSTEMS | Mahasainik Industrial Estate, Shop No -60 , Plot : T-153/1, Pimpri Industrial Area , Bhosari null | Pune | 411026 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Sachin Jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the LRE Reset Button Not operating. relay is in trip condition. also checked timer we checked continuity by multi meter, we observed this timer NO , NC contact not change over. problem observed in product. So Product needs to be replaced. Required Material : LRE14- 01 nos , LADS52- 01 nos | Repair |  | 9- Service Validated | 2023-09-08 11:15 | =S= Consig Fill up 226035512 |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11305151 | 104244120 | 2023-09-25 15:13 | 2023-09-25 |  | 2023-09-25 15:06 | Leonardo EV,DX,R407c,EC Fan,TDAV1021A,Downflow With Heater & Humidifier | TDAV1021AN002 | TDAV1021AN002 | ZK1413007834 | AMC P: LP Alarm S: AMC | 2023-09-25 | 2023-09-27 18:30 | No | Contract | Balmer Lawrie And Co. Limited | Address: 21,Netaji Subhas Road Kolkata - West Bengal INDIA, 700001 | Kolkata | 700001 | West Bengal | India FS East Cooling CSP Snow Point Kolkata | Laxmikant Dhang_Snow Point Kolkata | Snow Point | LP ALARM. SITE ATTEND AND CHECKED THE MACHINE CONDITION.CONDENSER COIL LEAKAGE.CONDENSER COIL LEAKAGE REPAIRING AND N2 HOLD DONE BY THIRD PARTY.VACUUM AND 27.6KG R407 GAS CHARGE.LP TRANDUSER CHANGE.ALL PARAMETER CHECKED.MACHINE OK RUNNING. | Repair |  | 10- Closed | 2023-09-27 18:46 |  |  | 35 | INR | 35 | ENM SECURE POWER
WO-11221393 | 103796645 | 2023-09-06 15:46 | 2023-09-06 |  | 2023-09-06 13:03 | GCR_CVS_T1_06 | GCR_CVS_T1_06 | GCR_CVS_T1_06 | 1023 | MCCB complaint Dear Sir, We are using Schneider MCCB and this MCCB not getting ON. And it's leaver comes to trip position. MCCB reset but not getting ON. MCCB detail below. Referance. LV563319 Serial number. 1023031 Qty. 01 nos Problem . Not getting ON. Photo attached. Kindly depute the engineer at below address to resolve the issue. Add. Laxmi Engineering Works Behind Adrash Nagar Poolish Station Parbatpura Bai Pass Ajmer -305002 mob _ +918239607777 Gst 08BDAPM6344K1ZC | 2023-09-06 | 2023-09-14 17:13 | No | Warranty | laxmi engineering works | Behind Adrash Nagar Poolish Station Parbatpura Bai Pass null | Ajmer | 305002 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | Checked the mccb found not getting on, Hence faulty replaced LV563319 - 1 nos Email : id not provided by customer. | Repair |  | 9- Service Validated | 2023-09-15 17:13 |  |  | 140 | INR | 140 | ENM POWER PRODUCTS
WO-11221563 | 103816370 | 2023-09-06 14:46 | 2023-09-06 |  | 2023-09-06 13:53 | GCR_MVS | GCR_MVS | GCR_MVS |  | SO : 225471647 ACB Serial no 10230830020 ACB Model: MVS16N4EW6A Qty: 1No Issue : ON & OFF Push button Operation is not Working BHEL Near Mindi, Vishikapatanam Pin 530012 Andhra Pradesh Contact Person : Nagaraj : 9620532212 | 2023-09-06 | 2023-09-07 10:11 | No | Warranty | BHEL | Near Mindi, null | Vishikapatanam | 530012 | Andhra Pradesh | India FS ED&I CSP South Team Voltamp Electrical Works Visakhapatnam | Vydha Venkatesh_VOLT AMP ELECTRICAL WORKS Visakhapatnam | Voltamp Electrical Works | Visited the site and found above the ACB Easy pact 1600 A 4 pole Is not working so today we have observed the problem of ACB On /off push Button operation issue so ratified the problem so closed the issue | Repair |  | 9- Service Validated | 2023-09-07 10:18 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11306758 | 104247100 | 2023-09-26 23:53 | 2023-09-25 |  | 2023-09-25 19:45 | IRC JK1520000213 | ACRC301HX738 | ACRC301HX738 | JK1520000213 | AMC P: Internal Communication Error S: AMC | 2023-09-25 | 2023-09-25 23:53 | No | Contract | Juniper Networks India Pvt Ltd | Prestige Tech Park Elnath-Exora Business Park Survey No.111/1 to 115/4 Wing A & B Amane Bellandur Khane Village Marathahalli | Bangalore | 560103 | Karnataka | India FS South3 Cooling CSP ERIC HVAC SYSTEM Bengaluru | Vijai VelanKannan ERIC HVAC SYSTEM Bengaluru | ERIC HVAC SYSTEM | Controller board is faulty so we have replace a new one . | Repair |  | 8- Service Completed | 2023-09-26 23:56 |  |  | 30 | INR | 30 | ENM SECURE POWER
WO-11221828 | 103814330 | 2023-09-07 15:05 | 2023-09-07 |  | 2023-09-06 15:18 | GCR_NSX100_630 | GCR_NSX100_630 | GCR_NSX100_630 | in | FW: COMPLIANT REGISTRATION - MALNAD CONTROLS Dear CC team, Kindly find trailing mail from customer please note LV432641 - 1no not working. Complaint Form attached, please request to depute your Service Engineer to resolve the case immediately. Soft copy of the invoice materials supplied attached for your reference. Kindly need your immediate action on the case. Warm regards, Uma G ________________________________________________________________ Purchase & Logistics NOVATEK ELECTRO ENGINEERS PRIVATE | 2023-09-06 | 2023-09-16 10:11 | No | Warranty | IBS Software Pvt Ltd | IT/ITES Special Economic Zone, Carnival Info park-1, Infopark campus, Ernakulam null | ERNAKULAM | 682042 | Kerala | India FS ED&I CSP South Team Geartech Electric Cochin | Vineesh M_Geartech Electric Cochin | Geartech Electric ASC for Schneider Electric | Inspected the equipment and found the problem with the motor mechanism and EFR, need to replace the MCH and EFR units. | Repair |  | 9- Service Validated | 2023-09-16 11:56 |  |  | 15 | INR | 15 | ENM POWER PRODUCTS
WO-11221960 | 103816286 | 2023-09-08 14:38 | 2023-09-06 |  | 2023-09-06 16:33 | GCR_NSX100_630 | GCR_NSX100_630 | GCR_NSX100_630 | 1022 inv | MCCB Shunt complaint Dear team, Customer is facing problem in MCCB Under voltage LV429407 Bill & Customer details attached Kindly resolve the proble. Panel builder MK Enterprises Mr. Mukesh kapoor- 9355223960 | 2023-09-06 | 2023-09-08 14:54 | No | Warranty | TRIUPATI PLYWOOD | Dadurpur, Kharwan, Jagadhari null | Yamunanagar | 135001 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the mccb found uvr not work, mccb getting trip when try to ON, even when UVR is energised as reported by customer. Checked it is happening due to MCCB tripping Lever bent. It might be happend due to improper fitment of UVR. Set the lever both MCCB and checked after fix UVR and energised UVR 220VAC. ON/OFF tripp reset observation effectively. Now working ok. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-08 15:04 |  |  | 105 | INR | 105 | ENM POWER PRODUCTS
WO-11223365 | 103829940 | 2023-09-07 10:42 | 2023-09-07 |  | 2023-09-07 09:20 | LV432809X63E630 | LV432809X63E630 | LV432809X63E630 | 1022272 | Reg : AWS HYD111 - ROMP03 - MCCB Communication issue Warranty Part code : LV432809X63E630 Serial no : 1022272 Issue:MCCB TU not communicating with IFE module "Amazon Data Services India Pvt Ltd (HYD-111), Survey No 190, Chandanvelly Village, Hytabad, Shabad Mandal, Rangareddy District, Telangana - 509217" Christo Thomas - 9074737395 8547733458 christo.thomas1@se.com | 2023-09-07 | 2023-09-12 12:00 | No | Warranty | Amazon Data Services India Private Limited | Survey Number 190(P) of Chandanvelly Village / 195(P) of Hythabad Village, Shabad Mandal, Ranga Reddy District, | Shabad Mandal | 501503 | Telangana | India FS ED&I CSP South Team Sumanth Electrical Services Hyderabad | Basanth Reddy_SUMANTH ELECTRICAL SERVICES HYDERABAD | Sumanth Electrical Services | Self Visited AWS Amazon 111 Site and inspected Schneider Compact NSX MCCB and in our observation we found that Micrologic is not Communicating and we are suspecting problem with MCCB and we have replaced with New MCCB | Repair |  | 9- Service Validated | 2023-09-12 19:34 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 60 | INR | 60 | ENM POWER PRODUCTS
WO-11223373 | 103830288 | 2023-09-07 10:47 | 2023-09-07 |  | 2023-09-07 09:27 | METSEPM5320 | METSEPM5320 | METSEPM5320 | 540110069913 | Reg : AWS HYD111 - ROMP04 - PM5320 Meter function keys not working. Warranty Part code : METSEPM5320 Serial no : 540110069913 Issue:Meter funtion keys are not working properly. "Amazon Data Services India Pvt Ltd (HYD-111), Survey No 190, Chandanvelly Village, Hytabad, Shabad Mandal, Rangareddy District, Telangana - 509217" Christo Thomas - 9074737395 8547733458 christo.thomas1@se.com | 2023-09-07 | 2023-09-12 12:00 | No | Warranty | Amazon Data Services India Private Limited | Survey Number 190(P) of Chandanvelly Village / 195(P) of Hythabad Village, Shabad Mandal, Ranga Reddy District, | Shabad Mandal | 501503 | Telangana | India FS ED&I CSP South Team Sumanth Electrical Services Hyderabad | Venkata Prasad_SUMANTH ELECTRICAL SERVICES HYDERABAD | Sumanth Electrical Services | Self Visited Site AWS Amazon 111 Site and Inspected Schneider Electric METSEPM5320 and 300003005D Power Meter Found Scrolling Buttons are not working properly we found problem with Power Meter and we have replaced with new Power Meter and Complaint is closed | Repair |  | 9- Service Validated | 2023-09-12 19:26 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 60 | INR | 60 | ENM POWER PRODUCTS
WO-11223914 | 103816392 | 2023-09-07 16:17 | 2023-09-07 |  | 2023-09-07 10:55 | LC1E3810M7 | LC1E3810M7 | LC1E3810M7 |  | LC1E3810M7 1022285 Qty:1 P: T1 Terminal Screw Thread out found during assembly works. Ragavendra Controls (P) ltd S.F.No.685/1-A Molapalayam Road Vellanaipatti Post Coimbatore - 641048 Tamilnadu Karthikraja 7397797109 | 2023-09-07 | 2023-09-13 12:16 | No | Warranty | RAGAVENDRA CONTROLS PRIVATE LIMITED | Site Address 6855\1A MOLAPALAYAM ROAD VELLANAIPATTI POST | COIMBATORE | 641048 | Tamil Nadu | India FS ED&I CSP South Team Power Pro Engineering Services Coimbatore | KV ARUNKUMAR_POWER PRO ENGINEERIG SERVICES COIMBATORE | Powerpro Engineering Services | we have visited the site and isnpected we found contactor screw thread spoiled unble to tight. we have collected the details for further action and arranging for free replacement and this | Repair |  | 9- Service Validated | 2023-09-13 12:18 | Hi Team, Material booked zfre Zvo : 226038974 |  | 31 | INR | 31 | ENM POWER PRODUCTS
WO-11224418 | 103827752 | 2023-09-07 12:30 | 2023-09-07 |  | 2023-09-07 11:24 | LC1G265KUEN | LC1G265KUEN | LC1G265KUEN |  | DOP: 25/4/2023 LC1G265KUEN Qty:1 P: Diagnosis LED on and start delay BHANDARI FEEDS PVT. LTD. PLOT NO.C-31 BELA INDUSTRIAL AREA PHASE II MUZZAFARPUR - 842005 , BIHAR MR.RAJAN PATEL 9725848765 | 2023-09-07 | 2023-09-09 18:27 | No | Warranty | BHANDARI FEEDS PVT. LTD. | PLOT NO.C-31 BELA INDUSTRIAL AREA PHASE II null | Muzaffarpur | 842005 | Bihar | India FS ED&I CSP East Team Vidya Enterprises Lucknow | Rana Ranjan_Vidya Enterprises Lucknow | Vidya Enterprises | As per customer complaint visited the site check the giga contactor found diagnosis LED blink when contactor get auxiliary supply for 10 sec. after that contactor close total install base is 7 out of there 1 contactor. Check the auxiliary supply 110 V i.e.. ok. We reset the contactor by reset switch instruction found in manual. again we mount the control module by interchange from then problem resolve now at this time all contactor are working fine as per customer satisfaction. now sit is under observation for some times. we check the contactor no of time on/off we did not get fault. | Repair |  | 9- Service Validated | 2023-09-09 18:29 |  |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11224516 | 103848266 | 2023-09-07 13:40 | 2023-09-07 | NA | 2023-09-07 12:23 | LC1DT60AM7 | LC1DT60AM7 | LC1DT60AM7 |  | Company Name : Aditi Power Solution Address: Antara Jewellers, Near SBI Bank, Ponda-Goa Contact Person : Sunil Singh Contact Number : 7021947072 Product reference : LC1DT60AM7 Invoice No.CEE/22-23/1273 Date: 12/11/2022 Product Problem: Not working Warranty: under warranty | 2023-09-07 | 2023-09-08 14:38 | No | Warranty | Antara Jewellers | C/o Aditi Power Solution Near SBI Bank, Ponda-Goa null | Valpoi | 403506 | Goa | India FS ED&I CSP West Team East India Power Engineers Mumbai | Abhishek Parab_East India Power engineers Mumbai | East India Power Engineers (5043) | Visited the site & checked the Contactor and found 13-14 NO contacts not working properly. The Contactor needs to be replace with the new one. | Repair |  | 8- Service Completed | 2023-09-13 10:48 | =S= Consig Fill up 226031792 |  | 14 | INR | 14 | ENM POWER PRODUCTS
WO-11310751 | 104274331 | 2023-09-26 15:55 | 2023-09-26 |  | 2023-09-26 14:26 | TDAVQ | TDAVQ | TDAVQ | C21930001791 | AMC P: PAC - Compressor oil leakage T: Need FSE visit S: AMC | 2023-09-26 | 2023-09-30 20:40 | No | Contract | Army commanding Office | Army commanding Office Signal | DANAPUR | 801503 | Bihar | India FS East Cooling CSP Cool Care Refrigerant Bhubaneshwar | Satyaranjan Rout_Cool Care Refrigerant Bhubaneshwar | Cool Care Refrigerant | we attend the site found gas leakage oil iqiilizer pipe ,replaced oil iqilizer line psi testing vaccuming & gas charging ,now pac running ok . | Repair |  | 8- Service Completed | 2023-09-30 20:42 |  |  | 319 | INR | 319 | ENM SECURE POWER
WO-11228910 | 103879566 | 2023-09-08 11:17 | 2023-09-08 |  | 2023-09-08 10:45 | LC1D40AM7 | LC1D40AM7 | LC1D40AM7 |  | Your request is: Product : :LC1D40A F7 - Quantity : 1no. Sr No. 10-23012 Jan 2023 With In warranty Coil Over heated / Burnt Not Getting ON Reliance Trends Shopping Center Mall Bus Stand Road Chamba Himachal Pradesh. 176310 Email : metagearelectric@gmail.com Contact Person : Mr Gaurav Contact No. 9815673062 | 2023-09-08 | 2023-09-08 11:19 | No | Warranty | Reliance Trends | Shopping Center Mall Bus Stand road | Chamba | 176310 | Himachal Pradesh | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Rakesh Kumar Sharma Electric Chandigarh | Sharma Electric works(1003) | checked the contactor found coil burnt and meter found not power up. Hence faulty, replaced. LXD3F7 - 1 Nos. METSEEM6400NGRSCL2 - 1 Nos. Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-08 15:48 |  |  | 335 | INR | 335 | ENM POWER PRODUCTS
WO-11229144 | 103846756 | 2023-09-08 12:07 | 2023-09-08 |  | 2023-09-08 11:05 | MEHVCSDY075A44 | MEHVCSDY075A44 | MEHVCSDY075A44 | ME-M4133363 | DOM Oct 2022 MEHVCSDY075A44 Sr No. ME-M4133363 P: Not drawing current Sunrise International Village Alawalpur Focal Point Jalandhar Mr Suraj Mittal 9417198561, 7508265466 | 2023-09-08 | 2023-09-08 12:19 | No | Warranty | Sunrise International | Village Alawalpur Focal Point Jalandhar | Jalandhar | 144001 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the capacitor found working ok. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-08 12:25 |  |  | 65 | INR | 65 | ENM POWER PRODUCTS
WO-11296125 | 104215909 | 2023-09-23 10:01 | 2023-09-22 |  | 2023-09-22 17:28 | LC1E50M7 | LC1E50M7 | LC1E50M7 |  | Warning: Email body is too large and was truncated at 32 000 characters. Information may have been lost. Checklist for Complaint Registration Doc. Ref :- SE/CCC/22-23/353 1 Company Name & Complete Address with pin code - Where product is installed IMPULSE POWERTEK 2 SIDE ADRESS Plot No- 1222, Phase-3,Near V-Trans, GIDC Vatva, Ahmedabad, (Guj ) - 382445 3 Contact Person at Site: Name & Mobile No. KETANBHAI - 9067083290 4 Altemate Mobile No. : Tel: 079 - 40085952, M.098250 10468 5 Contact Person at Site - Email Address**. 6 Defective Product Model/Part No (Pls refer FAQ sheet ) A9KF71306BQ = TRIPPING PROBLEM 6-a Defective Product Model/Part No (Pls refer FAQ sheet ) LC1E50M7 = 02 NO. ON PROBLEM 6-b Defective Product Model/Part No (Pls refer FAQ sheet ) 6-c Defective Product Model/Part No (Pls refer FAQ sheet ) 6-d Defective Product Model/Part No (Pls refer FAQ sheet ) 6-e Defective Product Model/Part No (Pls refer FAQ sheet ) 6-f Defective Product Model/Part No (Pls refer FAQ sheet ) 7 Nature of Defect* - Defects Video and Photographs TRIPPING PROBLEM 8 Shutdown availability if applicable 9 POP - SE Authorised Partner Invoice soft copy INV. : 23000 & 108140 10 Photograph of product where Serial No/Batch Code or Date of Manufacturing printed - Please refer FAQ sheet 11 Name & phone No: of person registering the complaint SHAILESH MAKWANA - 9924227896 Points 1,2,3,4,5 & (7or8) are mandatory. * Kindly share defect symptoms instead of "Not working", Please share the link of large files(product photoes or videoes) ** End user will receive a survey asking feedback on service POP - Proof of Purchase Please fill above details and send this sheet to customer care, Customer care contact link is give below https://www.se.com/in/en/work/support/contacts.jsp | 2023-09-22 | 2023-09-25 09:56 | No | Warranty | IMPULSE POWERTEK(500053334) | PLOT NO -1222, PHASE-III, G.I.D.C. VATVA | Ahmedabad | 382445 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Sitpuriya_Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product observed. A9KF71306 SR NO : 2306 dolly free. A9KF71450 SR NO : D2115 dolly free. lc1e50m7 sr no : wh2230 physically ok no burnt or damaged power contact obsrved. no contactor operating nvc get burnt and bulged. nvc burnt due to overvoltage. so free replacemnt for customer satisfaction. | Repair |  | 9- Service Validated | 2023-09-25 09:58 | 226079493 |  | 10 | INR | 10 | ENM POWER PRODUCTS
WO-11229248 | 103848885 | 2023-09-08 14:36 | 2023-09-08 |  | 2023-09-08 11:56 | LC1D80B7 | LC1D80B7 | LC1D80B7 | PK22411 | Re: Fwd: Contactor Issue on Site. 103417443, Case: 103662243,, Case: 103768930, [ thread::xyAYlybOdpW-myVd4aGjkj4:: ] LC1D80B7 PK22411 operation issue Site Address: RAMKY INFRASTRUCTURE LIMITED Ramky One Odyssey, Survey No. 176,177 & 178, Narsingi,Hyderabad - 500075 Telangana. Mr. Prashant Saple 7666350214 | 2023-09-08 | 2023-09-11 12:00 | No | Warranty | RAMKY INFRASTRUCTURE LIMITED | Survey No. 176,177 & 178, Narsingi, | Hyderabad | 500075 | Telangana | India FS ED&I CSP South Team Sumanth Electrical Services Hyderabad | Madhu Mantena_SUMANTH ELECTRICAL SERVICES HYDERABAD | Sumanth Electrical Services | Self Visited Site and Inspected Schneider Electric Power Contactors LC1D80B7 and in our observation we found that Contactors are giving Humming Noise and Chattering Noise so we have replaced with New LC1D80B7 Contactors Qty 03Nos and Faulty Contactors are Collected For RTS to ASC CSP For RTS and Work order has been closed and complaint is closed | Repair |  | 9- Service Validated | 2023-09-12 14:08 |  |  | 20 | INR | 20 | ENM POWER PRODUCTS
WO-11299988 | 104229294 | 2023-09-25 17:17 | 2023-09-23 |  | 2023-09-23 10:22 | C25N3MA220 | C25N3MA220 | C25N3MA220 |  | RE: Failure of Schneider MCCB at E20/Patel agri site [ thread::hEeV4mJVclOxTycSq8c_Dz4:: ] Please treat this as special case and to assign an engineer to the sites mentioned, as we need to get preliminary analysis to see further course of action, to provide alternate suggestion if required etc.., (Todays meeting with customer same was provided), The WO is only for site visit, if the discussion on replacement is required, then we will consider and validate as per warranty before initiating. Regards, Santosh Pitre DGM Business Operations Quality- CS&Q International Operations D +91 80 45541969 M +91 9686576061 E santosh.pitre@se.com During discussion it was observed that this is occurring only in 90KW Starter MCCB -NSXMA 220A Star Contactor ? LC1D80 Mains/ Delta contactor ? LC1G185KUEN Star Delta Timer ? GIC with 10seconds delay | 2023-09-23 | 2023-09-23 17:20 | No | Warranty | M.G.Petrochem Pvt.Ltd. | Village Firozpur, Tehsil Raipur Rani, | Panchkula | 134204 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Vinod Kumar_Sharma Electric Chandigarh | Sharma Electric works(1003) | Site visited and observed that there is no MCCB installed at site. All motors are having SFU as in backup protection. Email id not provided by the customer | Assessment/ Inspection | Data Collection | 8- Service Completed | 2023-09-25 17:24 |  |  | 45 | INR | 45 | ENM POWER PRODUCTS
WO-11229389 | 103823554 | 2023-09-08 16:45 | 2023-09-08 | NA | 2023-09-08 12:55 | GCR_NT | GCR_NT | GCR_NT | 102144 | Fw: Interconnection ACB issue in MSB Y-3035 GRSE Warning: Email body is too large and was truncated at 32 000 characters. Information may have been lost. P {margin-top:0;margin-bottom:0;} Please find trail mail Rejection from GRSE Y-3035 MSB Kolkata SAP no: 225224350 Invoice No. 9008342342 Type No : NT08H13PEDO2.0A Qty : 01 NO Problem :Upon switching on the control supply, the internal charging motor initiates but continues running indefinitely. Unfortunately, the ACB does not seem to charge despite the continuous operation of the charging motor ACB remains in discharged and Off position. Kindly arrange replacement & Service engineer below mention address: Site Address- Garden Reach Ship builders & Engineers Ltd. Main unit , Gate no.1 Garden reach road, Metiabruz Bichalighat Kolkata- 700024 Contact no : Binod Kumar Das Manager Mob- 9007216874 | 2023-09-08 | 2023-09-14 14:00 | No | Warranty | Garden reach ship builders | Main unit , Gate no.1 Garden reach road, Metiabruz Bichalighat Kolkata | Kolkata | 700024 | West Bengal | India FS ED&I CSP East Team B.D Electroservices Kolkata | RAHUL RAY_B.D Electroservices Kolkata | B.D Electroservices(500017330) | We close this complain and we will do the physically work 19.09.2023 | Repair |  | 9- Service Validated | 2023-09-14 17:34 | =S= Consig Fill up 226038994 |  | 20 | INR | 20 | ENM POWER PRODUCTS
WO-11311292 | 104281735 | 2023-09-26 23:31 | 2023-09-26 |  | 2023-09-26 18:30 | Easy UPS 3S 30 kVA 400 V 3:3 UPS for external batteries | E3SUPS30KH | E3SUPS30KH | 9E2149T11005 | AMC P: UPS Not working S: AMC | 2023-09-26 | 2023-09-27 12:30 | No | Contract | HDFC Securities Limited | GKR Sapthagiri Vaishtadhama, No 38, 12 th Cross, Ganganagar, North Bangalore | Bangalore | 560032 | Karnataka | India FS South1 HBN CSP UBM Autopower Pvt. Ltd Bangalore | Arun UBM Autopower Pvt. Ltd Bangalore | Autopower systems and solutions | We received call on Tue - 26th Sep,6:41 PM only, Onsite Date: 27th Sep. Checked the ups Found battery problem informed Customer battery Need to change , Battery is customer scope, UPS working fine. | Repair |  | 10- Closed | 2023-09-28 10:11 |  |  | 7 | INR | 7 | ENM SECURE POWER
WO-11301180 | 104229656 | 2023-09-25 09:03 | 2023-09-25 |  | 2023-09-23 13:19 | METSEPM2230D | METSEPM2230D | METSEPM2230D |  | Godrej Complaint tmalai@godrej.com Mr. Raja Gopal 7995007913 METSEPM2230D during installation and operation the values are not showing in the meter NA YES 9008509298/Dt: 06.04.2023 Ms. Jisha Nair. Tel No- 9594940045 E-mail ID - procurement@elecare.in | 2023-09-23 | 2023-09-25 17:30 | No | Warranty | Godrej Electricals & Electronics | RMZ ONE PARAMOUNT C/O Godrej Electricals & Electronics No.110, Mount Ponamalle Road null | Chennai | 600116 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Meter not showing on values. | Repair |  | 8- Service Completed | 2023-09-26 16:11 |  |  | 52 | INR | 52 | ENM POWER PRODUCTS
WO-11229300 | 103824076 | 2023-09-08 12:51 | 2023-09-08 |  | 2023-09-08 12:20 | LC1E80004M5WBIN | LC1E80004M5WBIN | LC1E80004M5WBIN | 1023 | COMPLAIN ? LC1E80004M5WBIN - QTY - 1 (POWER TECH ENERGY SOLUTIONS.) Checklist for Complaint Registration 1 Name of Customer M/S POWER TECH ENERGY SOLUTIONS 2 Site Address C/O M/S DEPUTY EXE.ENGG.R B -NEAR INAJ PATIA, JILLA SEVA SADAN, AT INAJ - 362269 Contact Phone / Mob. No: 9510733104 3 Name of contact person at site MR. Parth Solex Sir Goldi 5 Defective product details LC1E80004M5WBIN - QTY - 1 6 Product Make SCHNEIDER-CONTACTOR 7 Nature of Defect NOT WORKING 8 Shutdown availability if applicable 9 Warranty status UNDER WARRANTY 10 Commissioned / Installed date 11 Serial No: or DOM of the product BILL NO - : 7757/22-23 DATE - 06-12-2022 12 Name & phone No: of person registering the complaint JOHNSON- 8780431402 13 NOTE | 2023-09-08 | 2023-09-12 14:23 | No | Warranty | Power Tech Energy Solutions | 78/3, GIDC Makarpura, Nr. Krishna Unity Car, | Vadodara | 390010 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | RAHUL PARMAR JKS Rajkot | JKS Engineering Co. | visited site and observed check onside customer himself contector remove and send to panel builder mahesana, then check its wiring but also this wiring remove, not any Evidence available on site, so talk with with supplier when available tour site that time inform us, Now I am leaving the site without any evidence As per cusomer reporting use 16mm wire with pintypes lugs and terminal side burning | Repair |  | 9- Service Validated | 2023-09-13 10:21 |  |  | 210 | INR | 210 | ENM POWER PRODUCTS
WO-11311576 | 104282915 | 2023-09-26 19:14 | 2023-09-26 |  | 2023-09-26 18:41 | AMICO 3 TR R407C (M172) With Heater and Humidifier | SDAC0351AN001 | SDAC0351AN001 | JK2032001215 | DOP : AMC P : Evaporator Fan Run Hours Exceeded S : AMC | 2023-09-26 | 2023-09-27 11:00 | No | Contract | VUENOW INFOTECH PRIVATE LIMITED | National Highway 58, Morta Village | Ghaziabad | 201003 | Uttar Pradesh | India FS North2 Cooling CSP D K AIRCON Delhi | Mubarak Ali_D K AIRCON Delhi | DK AIRCON | We have check & found PAC was Alarm showing due to Evaporator fan run hourly Issue. We have done Evaporator fan run hourly Alarm reset and testing done. All paramenter check and found ok. Now PAC unit is working OK | Repair |  | 8- Service Completed | 2023-09-27 13:23 |  |  | 16 | INR | 16 | ENM SECURE POWER
WO-11301292 | 104230477 | 2023-09-25 10:20 | 2023-09-23 |  | 2023-09-23 17:28 | LV540309 | LV540309 | LV540309 | 1023264 | Complaint No. Reqd a/c Gobind Dear Sir, Please issue Complaint No. Gobind Electrical Corporation PLOT NO-371, INDUSTRIAL AREA PH-2,Chandigarh. Mr.Amarjit Singh 8566932490 Product : LV540309 Srn : 1023264 Issue:loose terminal issue Regards Mukesh Kumar | 2023-09-23 | 2023-09-25 10:23 | No | Warranty | Gobind Electrical Corporation | PLOT NO-371, INDUSTRIAL AREA PH-2 | Chandigarh | 160002 | Chandigarh | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Vinod Kumar_Sharma Electric Chandigarh | Sharma Electric works(1003) | checked the mccb found malfunctioning . hence faulty, replaced. LV540309 - 1 Nos. 32593 - 1 Nos. Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-27 10:05 |  |  | 15 | INR | 15 | ENM POWER PRODUCTS
WO-11229735 | 103862246 | 2023-09-09 10:58 | 2023-09-08 |  | 2023-09-08 14:53 | MEHVCSDY250A44PB | MEHVCSDY250A44PB | MEHVCSDY250A44PB |  | MEHVCSDY250A44PB ME-K19211564 P: Not Working Rishab Singh 9026319452 Address- pani ki tanki maigalganj Shahjahanpur 209622 | 2023-09-08 | 2023-09-09 11:40 | No | Warranty | Rishab Singh | Pani ki Tanki, Maigalganj, | Sitapur | 261505 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Abhishek Patel Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found contactor having pole open issue so we replaced. | Repair |  | 9- Service Validated | 2023-09-09 11:43 |  |  | 150 | INR | 150 | ENM POWER PRODUCTS
WO-11304749 | 104237748 | 2023-09-25 16:14 | 2023-09-25 | Power Analyzer installation | 2023-09-25 13:15 | LC1D1506M7 | LC1D1506M7 | LC1D1506M7 | PK21513HOR00014 | Dear CCC, Pl issue complaint no.1. Name of Customer: CRAFTSMAN AUTOMATION LTD PUNE UNIT 4 2. Site Address: - GAT No. / Hissa No. 137/2, 138/2 & 136/1Sanaswadi Village, Shirur Taluka 412208 PUNE3. Name of contact person at site :-Mr. Naren Magar4. Contact Phone / Mob No. : 83084712175. Defective product details:- LC1D1506M76. Product Make:-Schneider Electric7. Nature of Defect: Contactor Power Analyser Installation 8. Shutdown availability if applicable :nil9. Serial No: or DOM of the product- PK2303510. Dealer Name /OA no. /Invoice Details: - NIL11. Commissioned / Installed date:- new material12. Name & phone No: of person registering the complaint: Amit Patil - 8888192174 =======Thanks&Regards=============================================== For Super Electrical's Engineering Services Executive-Customer Service Support Authorized Service Center(Schneider Electric India Pvt.Ltd) Sachin Gadekar Service of All Types Of HT,PCC,MCC,APFC,ACB,VFD Panel,Specialist in Retrofitting of ACB ,VCB,AC/DC Drive Mob+91 9145512112 , Mob+91 9623057979 E-mail:superelctrical83@gmail.com sales@superelectricals.co.in Please do visit us at www.superelectricals.co.in ADD-SHOP- No-SR NO 13H.NO 1A/1A PLOT NO 11 SHOP NO 2 GEETA GRACIA THITE WASTI KHARADI PUNE 411014 , MAHARASHTRA INDIA | 2023-09-25 | 2023-09-25 16:47 | No | Warranty | Craftsman Automation Pvt. Ltd.-UNIT-2 | GAT No.-137, Hissa No.-2, Sanaswadi Village, Shirur Taluk, | Pune | 412208 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Amit Patil_Super electricals Pune | Super Electricals Engineering Services(500017125) | We installed the power Analyzer across the low speed conatctor LC1D1506M7 - 01 nos of BFW Machine no - 133.we connect phase neutral of contactor to power analyzer . also connect Ct properly. | Repair |  | 9- Service Validated | 2023-09-26 10:09 |  |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11304835 | 104241522 | 2023-09-26 11:26 | 2023-09-25 |  | 2023-09-25 13:53 | METSEEM6436HCL10RS | METSEEM6436HCL10RS | METSEEM6436HCL10RS |  | Meter --No display Model: METSEEM6436HCL10RS Inv dated----------09 sep 2023 No display Add: Ican Automation Solutions plotno 331, udyog kenda 1 Ecotech -3 Gr. Noida 201308 Juggal Ji 9958669146 | 2023-09-25 | 2023-09-27 15:41 | No | Warranty | I CAN AUTOMATION SOLUTIONS | Plot number:- 331, udyog kedra 1, Echotech 3, near new police station | Greater Noida | 201306 | Uttar Pradesh | India FS ED&I CSP North Team Sharma Electric Works Delhi | Pradeep Sharma_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the meter display not showing and due to resit burnt without protection fused, Hence no replacement given to customer. Email : id not provided by customer . | Repair |  | 8- Service Completed | 2023-09-27 15:46 |  |  | 52 | INR | 52 | ENM POWER PRODUCTS
WO-11229805 | 103858202 | 2023-09-08 21:12 | 2023-09-08 |  | 2023-09-08 15:16 | GCR_NSX | GCR_NSX | GCR_NSX |  | DOP: 6/9/2023 LV429410 Qty: 1 P: Power supply connection terminal Not working. "M/s Switchgear & Control Automations No.37, 5th Cross, Doddamma Industrial Layout, Hulimavu, B G Road,Bangalore-560076 Karnataka" Devaraj Cell No:-9844811868 9844811868 design@sca-blr.com | 2023-09-08 | 2023-09-15 16:58 | No | Warranty | Switchgear & Control Automation | No-37, 5th Cross, Dodamma Industrial Layout, Hulimavu null | Bangalore | 560076 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | C Gunasekaran_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | We had visited the site and checked the customer reported coil.Found wire unable to connect wire.Due to internal hardware issue.so we arranged the free replacement. | Repair |  | 9- Service Validated | 2023-09-15 23:04 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11304891 | 104241826 | 2023-09-27 12:43 | 2023-09-25 |  | 2023-09-25 14:02 | METSEEM6436HCL10RS | METSEEM6436HCL10RS | METSEEM6436HCL10RS |  | Meter--Display Issue METSEEM6436HCL10RS Sr: 540410047485-----Inv dated: 09 sep 2023 Fault:- Display issue Himcon Engineers B-115, sector-67 Noida 9910869615----Aman | 2023-09-25 | 2023-09-27 14:52 | No | Warranty | Himcon Engineers India Pvt Ltd | B-115,, Sector 67 | Noida | 201301 | Uttar Pradesh | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the meter found working ok.Product found ok. Email : | Repair |  | 8- Service Completed | 2023-09-27 14:56 |  |  | 50 | INR | 50 | ENM POWER PRODUCTS
WO-11234199 | 103882751 | 2023-09-09 13:44 | 2023-09-09 |  | 2023-09-09 11:27 | GCR_CVS_T1_06 | GCR_CVS_T1_06 | GCR_CVS_T1_06 | 1022141 | Complaint 09-01 Dear CCC, We are facing a problem in MCCB reference No.LV563620 Breaker CVS630F 6.3 630A 3P Serial No. 1022141 at our site. Please arrange the expert at site & diagnose the problem. Problem Type ? Tripping Fault Details as Follows: Customer Address : SSG PAPER MILS (LLP) VILLAGE ?KHUSROPUR, MAIN ROAD, PATIALA (PB) Contact Person : Mr. Narinder Contact Number : 75289-66945 We are requesting you to please solve the problem on URGENT basis. Thank You, Munish Sharma Manager Purchase & Materials ¦ Automation Systems ¦ System Integrator of Schneider Electric ¦ Description: https://cdn2.hubspot.net/hubfs/53/tools/email-signature-generator/icons/phone-icon-2x.png 0161-4613111 ¦ +91 9803018933 Description: https://cdn2.hubspot.net/hubfs/53/tools/email-signature-generator/icons/email-icon-2x.png munish.s@automationsystems.org Description: https://cdn2.hubspot.net/hubfs/53/tools/email-signature-generator/icons/link-icon-2x.png http://www.automationsystems.org Description: https://cdn2.hubspot.net/hubfs/53/tools/email-signature-generator/icons/address-icon-2x.png Address: # 291, Guru Nanak Market, Near Giaspura Railway Crossing, Focal Point, Ludhiana-141010 (PB) | 2023-09-09 | 2023-09-15 10:23 | No | Warranty | SSG PAPER MILS (LLP) | VILLAGE ?KHUSROPUR, MAIN ROAD, | Patiala | 147001 | Punjab | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Karnail Singh Sharma Electric Chandigarh | Sharma Electric works(1003) | checked the mccb found not getting On due to mechanism faulty, replaced. LV563620 - 1 Nos. Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-15 13:00 |  |  | 75 | INR | 75 | ENM POWER PRODUCTS
WO-11305421 | 104238014 | 2023-09-25 16:28 | 2023-09-25 |  | 2023-09-25 15:58 | GV2ME16 | GV2ME16 | GV2ME16 |  | Dear Sir, ''Greetings from APS " Please find enclosed Part NO Reference:-GV2ME16, 9-14A MPCB Qty:-1 NO. and also Supplied customer Invoice Copy Enclosed. Customer Complaint:-This is to bring in your kind attention one MPCB was not working when our engineer was testing the panel.So replace as soon as possible . For the Proof Video is Enclosed. Invoice copy Enclosed. Invoice Details: Invoice number: AA3330043935 Contact Person Name:- Ayodhya , 85009 67383 Customer Address:- ¦ Visiontekniks Engineering & Automation ¦ # Plot No: 208/10 ¦ Phase-II, Sector-III, Lane-IV ¦ IDA Cherlapally, Hyderabad- 51 Phone: + 91 7013383897 ¦ Mobile: +91 9392424883¦ www.visiontekniks.co.in Best Regards P.Durga Prasad ALL-TEC POWER SOLUTIONS SUKRUTHI BUILDING PLOT NO.5, H.NO.34-118/5 MATHRUPURI COLONY SAINIKPURI, SECUNDERABAD - 500 094 apsols@gmail.com Office Phone :040 27719956 & 27119957 purchase@alltec-aps.com GST NO: 36AASFA1621P1Z3 TIN & CST NO: 36720637913 ECC NUMBER: AASFA1621PED001 | 2023-09-25 | 2023-09-28 12:00 | No | Warranty | VISION TEKNIKS | Plot No 208/10, St 4, Sector3, Phase-ii, Ida Cherlapallt | Hyderabad | 500005 | Andhra Pradesh | India FS ED&I CSP South Team Sumanth Electrical Services Hyderabad | Basanth Reddy_SUMANTH ELECTRICAL SERVICES HYDERABAD | Sumanth Electrical Services | Visited Site and inspected schneider electric GV2 ME 16 MPCB and in our observation we found that the MPCB is having toggle free and dolly free problem and we have replaced with new MPCB and Faulty Collected to ASC CSP For RTS and work order is closed | Repair |  | 8- Service Completed | 2023-09-28 20:06 |  |  | 10 | INR | 10 | ENM POWER PRODUCTS
WO-11234210 | 103884291 | 2023-09-09 17:05 | 2023-09-11 |  | 2023-09-09 11:31 | LV540309 | LV540309 | LV540309 |  | DMAK ENERGIA LV540309 tripping issue Site Address: SAHEB POLYPLAST PVT LTD Survey No : 507 , Chandisar- kumbhalmer road , Nr. Railway Crossing , chandisar Ta: PALANPUR ? 385510 GUJARAT Contact Person Mobile No :- +91 9879540019 | 2023-09-09 | 2023-09-11 17:52 | No | Warranty | SAHEB POLYPLAST PVT LTD | Survey No : 507, Chandisar- Kumbhalmer road, chandisar, PALANPUR | BANASKANTHA | 385510 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | Parthiv Patel JKS Ahmedabad | JKS Engineering Co. | We visited to the side and found decodery MCCB in used for dusibaren applycusam... due to mussam coustumer bypass to McCB. Who mesure.. the Ampere at bypass the cable 125 A per fase No Any beting land. budking the MCCB trumimal as well. as inside the MCCB. Pressent coustumer not Decaly to shut down give.. loud didect to MCCB. We are mat cible do Conclude.. as per Coustomer. new. fed buck. Permal bilder Supply to MCCB and it well be insttal dure to cut dowem.. So, we recoused to custormed to insttal the new. MCCB and poovied. the seed back furcen in obser MCCB and this depotea MCCB need to be Servies... Sented for loud testing. we are closing the case and well take mew case... ? mumede was this depoted MCCB well Tech to Lour MCCB. We oubser the not use to cooling... | Repair |  | 9- Service Validated | 2023-09-11 17:52 | =S= Free Order 226048903 |  | 145 | INR | 145 | ENM POWER PRODUCTS
WO-11234284 | 103908750 | 2023-09-09 12:47 | 2023-09-09 |  | 2023-09-09 12:32 | NW16H24PML6A | NW16H24PML6A | NW16H24PML6A |  | RE: Regarding 3 Nos ACB release faulty at Esplanade Metro station, KMRCL Site, Case: 103251888, [ thread::GCbnf2oGfPG_LW2d2GomIj4:: ] | 2023-09-09 | 2023-09-09 16:09 | No | Warranty | Kolkata Metro- Esplanade Station | Esplanade Metro, Jawaharlal Nehru Rd, Esplanade | Kolkata | 700013 | West Bengal | India FS ED&I CSP East Team SREYAM SERVICES BHATPARA | AMIT BHATTACHARYA_SREYAM SERVICES BHATPARA | Sreyam Services(8513) | AFTER SITE VISIT FOUND 4 NOS ACB IS ISD, IG, OP FAULT INDICATION LED ALL TIME GLOWING MICROWLOGIC , BATTERY OPEN INDICATION NOT GLOWING BUT WHEN BATTERY WAS FITTED PROBLEM WAS SAME . THIS IS NOT REPAIRABLE. | Repair |  | 9- Service Validated | 2023-09-11 16:29 |  |  | 14 | INR | 14 | ENM POWER PRODUCTS
WO-11234288 | 103889297 | 2023-09-09 14:43 | 2023-09-09 | Part order request validated by Mr Pradeep Patil sir | 2023-09-09 12:39 | LV516302 | LV516302 | LV516302 | 10-2022-W46-3 | complaint for MCCB 125 A LV516302 10-2022-W46-3 pole continuity issue Site Address: Grasim Ind. Limited Unit: Vikram Woollens GH I to IV, Malanpur, Bhind Madhya Pradesh-INDIA? 477117 Mr. Santosh pandey 8435000468 7773013212 | 2023-09-09 | 2023-09-15 15:01 | No | Warranty | Grasim Industries Limited | GH I to IV, Malanpur Unit: Vikram Woollens | Bhind | 477117 | Madhya Pradesh | India FS ED&I CSP West Team ABR Technical Service Indore | Chirag Jain_ABR Tecneical Services Indore | ABR Technical Services (9574) | Reached at site and as per customer MCCB R pole out then we check on/off operation and found ok also check with test button MCCB tripping ok then we check continuity of all three poles and found R pole not showing continuity . Customer remove MCCB from the panel and installed other MCCB. Then we check other MCCB Voltage and found R = 425VAC , Y=430VAC ,B=431VAC As per our observation MCCB R pole out may be due to internal mechanisms malfunctioning that?s why R pole out . So we recommend to replace 1 Nos. MCCB. Note-New MCCB handover to customer and faulty collect. Now we are closing this case. | Repair |  | 9- Service Validated | 2023-09-15 15:06 | =S= Consig Fill up 226045855 |  | 640 | INR | 640 | ENM POWER PRODUCTS
WO-11234324 | 103889070 | 2023-09-09 14:39 | 2023-09-09 |  | 2023-09-09 13:34 | GCR_CVS_T1_06 | GCR_CVS_T1_06 | GCR_CVS_T1_06 |  | COMPLAIN ? LV563640 - QTY -01 (SUKHARAM ELECTRIC CORPORATION.) Please Provide Complain number has per Attached Deta Checklist for Complaint Registration 1 Name of Customer M/S SUKHARAM ELECTRIC CORPORATION 2 Site Address CLIENT SITE - C/O PVK TECHNOLOGY,PLOT NO.: 77,78, NAVAGAM UDYOG NAGAR VAV, SURAT SUKHARAM SITE - 34, T V COMPOUND, RD. NO. 06, UDHNA SURAT. Contact Phone / Mob. No: 8866320029 3 Name of contact person at site Mr. CHINTAN JARIWALA,Mr. KIRAN PRAJAPATI 5 Defective product details LV563640 - QTY -01 6 Product Make SCHNEIDER - 630A FP MCCB 7 Nature of Defect NOT WORKING (WHEN INSTALLED SHUNT RELEASE MCCB DOES NOT CLOSE.) 8 Shutdown availability if applicable 9 Warranty status UNDER WARRANTY 10 Commissioned / Installed date 11 Serial No: or DOM of the product BILL NO - : 5140/23-24 DATE -24-08-2023 12 Name & phone No: of person registering the complaint HEMAN GANDHI- 8780431402 13 NOTE Note : Point Nos: 1 to 9 are compulsory JOHNSON.. | 2023-09-09 | 2023-09-11 12:02 | No | Warranty | Sukharam Electric Corporation | C/O PVK TECHNOLOGY,PLOT NO.: 77,78, NAVAGAM UDYOG NAGAR VAV, SUKHARAM SITE - 34, T V COMPOUND, RD. NO. 06, UDHNA Udhna Udyog Nagar Road Aanjada Nagar null | Surat | 395002 | Gujarat | India FS ED&I CSP West Team Jay Services Vadodara | Ghanshyam Kachiya_Jay Services Vadodara | Jay Services | We visited at site & checked that MCCB Not ON with MX ( shunt release) due to it is not reser. Now we open ERHOM & observed MX reset lever out of space. Now rectify & refitted MX release & test MCCB ON-OFF operation found working satisfactory. We explain to customer MX release always mount in MCCB trip position & operate MCCB after fitting front facia OR ERHOM . Now MCCB working satisfactory. | Repair |  | 9- Service Validated | 2023-09-11 12:03 |  |  | 141 | INR | 141 | ENM POWER PRODUCTS
WO-11234335 | 103893869 | 2023-09-09 15:56 | 2023-09-09 |  | 2023-09-09 13:57 | METSEEM6400NGRSCL1 | METSEEM6400NGRSCL1 | METSEEM6400NGRSCL1 | 540180121010 | METSEEM6400NGRSCL1 Qty:1 P: Not Working PRAGATHI CONTROLS NO 9/16, 4th MAIN J.C INDUSTRIAL AREA, KANAKAPURA ROAD BANGALORE - 560062 Vidya 9353678519 | 2023-09-09 | 2023-09-13 11:56 | No | Warranty | Pragathi Controls | Unit -2, 9/16, 4th Main,J.C Industrial Layout, Yelachenahalli,Kanakapura Main Road | Bangalore | 560062 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Santhosh DP_P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | INSPECTED AND FOUND BELOW MENTIONED REF:METSEEM6400NGRSCL1 S/N:540180267915=01NO METER DISPLAY NOT GETTING ON . HENCE WE WILL GIVE SAME NEW METER WARRANTY REPLACEMENT ASAP. | Repair |  | 9- Service Validated | 2023-09-13 11:57 |  |  | 15 | INR | 15 | ENM POWER PRODUCTS
WO-11234368 | 103891781 | 2023-09-09 22:04 | 2023-09-11 |  | 2023-09-09 15:07 | METSEEM6436HCL10RS | METSEEM6436HCL10RS | METSEEM6436HCL10RS | 45047 | Re: Energy Meter reading fault, Case: 103847294, [ thread::bpQbmb_qdFOoiwu2t5Nc6j4:: ] Checklist for the Registration of Service Request Sr. No Particulars Doc. Ref :- SE/CCC/001/V0.1 1 Company Name & Complete Address with pin code - Where product is installed PREMIER CARBONIC PVT.LTD, Plot No 9/5, Near EID Parry India Ltd., Udaikula Village, Koothandan Post,Sivaganga Taluk & District, 630561. Installed at Our Plant energy meter 2 Contact Person at Site : Name & Mobile No. S. Boopathi- Ph. 6381423860 Alternate Mobile No : 8220030531 3 Contact Person at Site - Email Address** S. Boopathi boopathi.s@premiercarbonic.com 4 Product Issue Type (Please select from drop down of column C-9) Energy meter reading is not showing properly, old energy meter shows per hr consumption is 220 units, but it showing per hr nt even crossing 100 units, New capacitor also installed but Power factor is 0.923. 5 Are you ready to troubleshoot the issue remotely ? Yes/NO. If Yes, Our technical support engineer will call back to troubleshoot the issue remotely. NO 6 Defective Product Model/Part No (Pls refer FAQ sheet ) METSEEM6436HCL10RS / 540420237493 7 Nature of Defect* - Defects Video and Photographs 8 Shutdown availability if applicable yes 9 Photograph of product where Serial No/Batch Code or Date of Manufacturing printed - Please refer FAQ sheet to find the Batch code details on the products Serial No- 54020237493 10 Proof Of Purchase - Pease attach SE*** Authorised Partner Invoice soft copy along with this check list Attached in mail 11 Name & phone No: of person registering the Service Request S BOOPATHI / Ph-6381423860, 820030531 "All fields are mandatory. Free of cost service visit subjected to warranty policy of the product and contract between Schneider Electric and buying party . Warranty will be check either by serial no/Batch code/DOM printed on the product or date of invoice of our authorised partner /Schneider Electric direct invoice or Contract . Warranty policy may be change product to product or contract with the customer. * Kindly share defect symptoms instead of ""Not working"", Please share the link of large files(product photoes or videoes) ** End user will receive a survey asking feedback on service " | 2023-09-09 | 2023-09-12 07:49 | No | Warranty | Premier Trading Corporation | Plot No 9/5, Near EID Parry India Ltd., Udaikula Village, Koothandan Post,Sivaganga Taluk null | Sivaganga | 630561 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | George KJ_Omicon Engineering Madurai | Omicon Engineering | Inspected the site found meter parameter is wrong after changed and found ok . | Repair |  | 9- Service Validated | 2023-09-12 07:52 |  |  | 60 | INR | 60 | ENM POWER PRODUCTS
WO-11234385 | 103911324 | 2023-09-09 16:14 | 2023-09-09 |  | 2023-09-09 15:51 | LC1D32BL | LC1D32BL | LC1D32BL |  | DOP: 16/3/2023 LC1D32BL Qty:1 P: Over Tighting Vinayaka Controls No-30, 3rd Cross, Behind Ranganatha Milk Diary Near Peenya 2nd Stage Bangalore - 560091 Mr.Dinesh BN 9731299226 | 2023-09-09 | 2023-09-15 10:49 | No | Warranty | VINAYAKA CONTROLS | #30,3rd Cross, Behind Ranganatha Milk Diary Near Peenya 2nd Stage | Bengaluru | 560026 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Nagaraja G_P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | Inspected and found below mentioned 1)Ref:LC1D32BL S/N:102306 = 1 No contactor, contactor, 2 T1 pole was screw threading issue. Hence we will give same new warranty replacement ASAP | Repair |  | 9- Service Validated | 2023-09-15 10:49 |  |  | 11 | INR | 11 | ENM POWER PRODUCTS
WO-11234386 | 103894834 | 2023-09-09 17:16 | 2023-09-09 |  | 2023-09-09 15:54 | GCR_NSX100_630 | GCR_NSX100_630 | GCR_NSX100_630 |  | SERVICE REQUEST FOR MCCB REPLACEMENT Checklist for the Registration of Service Request Sr. No Particulars Doc. Ref :- SE/CCC/001/V0.1 1 Company Name & Complete Address with pin code - Where product is installed Hotel Charriot & Ashoka, Bojogari, Gangtok ( Opposite Shiv Mandir) Sikkim - 737101 ( East ) 2 Contact Person at Site : Name & Mobile No. Shubham Datta, ( 9830598093 ) Alternate Mobile No : 8240572217 3 Contact Person at Site - Email Address** shubham.datta@choruspower.com 4 Product Issue Type (Please select from drop down of column C-9) 5 Are you ready to troubleshoot the issue remotely ? Yes/NO. If Yes, Our technical support engineer will call back to troubleshoot the issue remotely. NO 6 Defective Product Model/Part No (Pls refer FAQ sheet ) 630A 4Pole 36kA MCCB ( NSX ) ( Ref No. C63F46E630 ) : Qty - 1No. 7 Nature of Defect* - Defects Video and Photographs MCCB Malfunctioning ( Tripping on 30A Current ) 8 Shutdown availability if applicable 9 Photograph of product where Serial No/Batch Code or Date of Manufacturing printed - Please refer FAQ sheet to find the Batch code details on the products 10 Proof Of Purchase - Pease attach SE*** Authorised Partner Invoice soft copy along with this check list Attached 11 Name & phone No: of person registering the Service Request Subhasis Das / 9830524272 | 2023-09-09 | 2023-09-23 14:09 | No | Warranty | Hotel Chariot & Ashoka | 12 Bojogari Opposite Shiv Mandir Tadong Pani House Rd | Gangtok | 737102 | Sikkim | India FS ED&I CSP East Team SREYAM SERVICES BHATPARA | AMIT BHATTACHARYA_SREYAM SERVICES BHATPARA | Sreyam Services(8513) | FOUND MCCB REPLACED BY NEW ONE HAND OVER TO PANEL BUILDER DEFFECTIVE MATERIAL COLLECTED IS PENDING. | Repair |  | 8- Service Completed | 2023-09-23 14:09 |  |  | 710 | INR | 710 | ENM POWER PRODUCTS
WO-11234399 | 103909337 | 2023-09-09 20:13 | 2023-09-09 |  | 2023-09-09 16:16 | METSEEM6436HCL10RS | METSEEM6436HCL10RS | METSEEM6436HCL10RS |  | Complaint Form Checklist for Complaint Registration 1 Name of Customer Yadev instryments and Automation 2 Site Address 9/20 1st cross road samrat layout arekere Gate bennuarghatta Road banglore 560076 3 Name of contact person at site 8300652051 4 Contact Phone / Mob. No: METSEEM6436HCL10RS 5 Defective product details 6 Nature of Defect Not Working 7 Shutdown availability if applicable Disconnected 8 Warranty status 9 Commissioned / Installed date 10 Serial No: or DOM of the product 540420227237 11 Name & phone No: of person registering the complaint Ankit Rathod (m)-9998179036 Note : Point Nos: 1 to 9 are compulsory | 2023-09-09 | 2023-09-11 16:00 | No | Warranty | Yadev instruments and Automation Pvt. Ltd | Vinayak Nagar, Sarvobhogam Nagar, Arekere | Bengaluru | 560076 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Mohammad Riyaz_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the reported meter found readings not updating kw and kwh, we checked busbar current found R-19A, Y-19A and B- 19A respectively. So we replaced new meter after that same issue came. We recommended customer to calibrate CT and check PT wirings. We replaced new meter on goodwill basis. There is no issue with our product. So we closed the case. | Repair |  | 9- Service Validated | 2023-09-11 21:04 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11316335 | 104301372 | 2023-09-27 12:40 | 2023-09-27 |  | 2023-09-27 11:56 | Leonardo EV,DX,R407c,EC Fan,TDAV1021A,Downflow With Heater & Humidifier | TDAV1021AN002 | TDAV1021AN002 | NUCU3274 | AMC P: wrong power phase S: AMC | 2023-09-27 | 2023-09-27 15:30 | No | Contract | Ericsson India Global Services Pvt. Ltd. | Knowledge Bouleverd,3rd Floor Plot No A8 Sector 62 | Noida | 201309 | Uttar Pradesh | India FS North2 Cooling CSP D K AIRCON Delhi | Mubarak Ali_D K AIRCON Delhi | DK AIRCON | We have check & found PAC was showing wrong power phase alarm due to RSF (Mulfuntion) faulty Issue. We have New RSF(Voltage Monitoring Relay) replacement work done and testing done. All paramenter check and found ok. Now PAC unit is working OK | Repair |  | 8- Service Completed | 2023-09-28 11:29 |  |  | 16 | INR | 16 | ENM SECURE POWER
WO-11316356 | 104301586 | 2023-09-27 12:32 | 2023-09-27 |  | 2023-09-27 12:03 | TDAV3342AN40-1 | TDAV3342AN40-1 | TDAV3342AN40-1 | JK2033003395 | AMC P: HP Alarm S: AMC | 2023-09-27 | 2023-09-27 14:30 | No | Contract | Ericsson India Global Services Pvt. Ltd. | Knowledge Bouleverd,3rd Floor Plot No A8 Sector 62 | Noida | 201309 | Uttar Pradesh | India FS North2 Cooling CSP D K AIRCON Delhi | Pintu Kumar D K AIRCON Delhi | DK AIRCON | PAC was tripping from HP alarm due to condenser dirty. we have cleanned it with water and testing done. Now PAC is working OK. | Repair |  | 8- Service Completed | 2023-09-28 11:33 |  |  | 16 | INR | 16 | ENM SECURE POWER
WO-11235351 | 103816498 | 2023-09-11 06:05 | 2023-09-14 |  | 2023-09-09 20:27 | LC1E65M7 | LC1E65M7 | LC1E65M7 |  | Service Requisition LC1E65M7 LC1E40M7 operation issue Site Address: McDonald's Family Resturant Town Survey 506, Old Ward 17, New Ward 20, Phoenix Burugu Mall, Block 17, Nagarampalem, GT Road, Srinivasarao Pet, Guntur 522003 Andhra Pradesh phone: Venkatesh +91 6300306535 Alternate: Naveen +91 7899411592 | 2023-09-09 | 2023-09-14 18:30 | No | Warranty | McDonald's Family Resturant | Town Survey 506, Old Ward 17, New Ward 20, Phoenix Burugu Mall, Block 17, Nagarampalem, GT Road, Srinivasarao Pet, null | Guntur | 522003 | Andhra Pradesh | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Contactor Operation issue solved | Repair |  | 9- Service Validated | 2023-09-15 10:23 |  |  | 160 | INR | 160 | ENM POWER PRODUCTS
WO-11316369 | 104301800 | 2023-09-27 12:37 | 2023-09-27 |  | 2023-09-27 12:09 | TDAV3342AN40-1 | TDAV3342AN40-1 | TDAV3342AN40-1 | JK2033003396 | AMC P: HP Alarm S: AMC | 2023-09-27 | 2023-09-27 13:30 | No | Contract | Ericsson India Global Services Pvt. Ltd. | Knowledge Bouleverd,3rd Floor Plot No A8 Sector 62 | Noida | 201309 | Uttar Pradesh | India FS North2 Cooling CSP D K AIRCON Delhi | Pintu Kumar D K AIRCON Delhi | DK AIRCON | PAC was tripping from HP alarm due to condenser coil very dirty. we have clean condenser coil with water and testing done. All parameter check & found ok. Now PAC is working OK. | Repair |  | 8- Service Completed | 2023-09-28 11:44 |  |  | 16 | INR | 16 | ENM SECURE POWER
WO-11240932 | 103911749 | 2023-09-11 13:14 | 2023-09-11 | Replacement has already been given to customer by hi-tech. ZVO booked to Hi -tech marketing surat. | 2023-09-11 10:45 | LUB12 | LUB12 | LUB12 |  | COMPLAIN ? LUB12 - QTY - 02 (JNJ MACHINES PVT. LTD.) Checklist for Complaint Registration 1 Name of Customer M/S JNJ MACHINES PVT. LTD. 2 Site Address 762, OPP, AURO UNIVERSITY GATE NO.2 GIDC, ICHHAPORE, HAZIRA, SURAT, Surat Contact Phone / Mob. No: 9375960626 3 Name of contact person at site MR.SUNIL.PATEL 5 Defective product details LUB12 - QTY - 02 6 Product Make SCHNEIDER-SCREW CLAMP BASE 12A 7 Nature of Defect NOT WORKING 8 Shutdown availability if applicable 9 Warranty status UNDER WARRANTY 10 Commissioned / Installed date 11 Serial No: or DOM of the product BILL NO - : 2479/23-24 DATE - 02-09-2023 12 Name & phone No: of person registering the complaint JOHNSON- 8780431402 13 NOTE Note : Point Nos: 1 to 9 are compulsory | 2023-09-11 | 2023-09-14 04:01 | No | Warranty | JNJ Machines Pvt Ltd | Plot No.762 Opp- Auro University GIDC Ichhapore | Surat | 394510 | Gujarat | India FS ED&I CSP West Team VARDHAMAN ELECTROSOFT Vadodara | MAHENDRA SINGH VARDHAMAN ELECTROSOFT Vadodara | VARDHAMAN ELECTROSOFT | we visited the site and checked LUB 12 found phyisical ok . checked and found manually operation on/off ok. 1.Sr. no. 9186 operating coil A1,A2 open. pole open in on condition. 2. sr. no. 9212 pole open in on condition. | Repair |  | 9- Service Validated | 2023-09-14 18:05 | =S= Consig Fill up 226042793 |  | 60 | INR | 60 | ENM POWER PRODUCTS
WO-11316687 | 104306304 | 2023-09-27 18:58 | 2023-09-27 |  | 2023-09-27 14:14 | Easy UPS 3S 40 kVA 400 V 3:3 UPS for external batteries | E3SUPS40KH | E3SUPS40KH | 9E2219T12804 | Warranty P: FAN INOPERABLE S: AMC | 2023-09-27 | 2023-09-28 15:00 | No | Warranty | CRH ENT | MRI & Diagnostics NH 35, Sector Chi-Phi-3 Greater | Noida | 201310 | Uttar Pradesh | India FS North1 HBN CSP TCS IT Solutions Delhi | Mordwaj M TCS IT Solutions Delhi | TCS IT Solutions | On site visit checked the ups, found fan faulty need to be replace the fan now fan replaced ups working fine | Repair |  | 10- Closed | 2023-09-28 17:08 |  |  | 64 | INR | 64 | ENM SECURE POWER
WO-11241264 | 103919491 | 2023-09-12 13:24 | 2023-09-11 |  | 2023-09-11 11:39 | GCR_CVS_T1_06 | GCR_CVS_T1_06 | GCR_CVS_T1_06 | 10-2023-W18-43623L1 | MCCB complaint LV525333 tripping issue 10-2023-W18-43623L1 Harsoria Healthcare Khasra no. 83/85 Jharmajri Road Near Nimantran Resorts Baddi 173205 Himachal Pradesh India 9056563456 Mr. Vijay | 2023-09-11 | 2023-09-16 15:20 | No | Warranty | Harsoria Healthcare Unit-2 | Khasra no. 83/85 Jharmajri Road Near Nimantran Resorts near by Toll Barrier, | Baddi | 173205 | Himachal Pradesh | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Karnail Singh Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the mccb found not getting on due to mechanism faulty and contactor found plunger stuck issue. Hence faulty replaced shut down not available at site, panel builder will replace the same. When shut down available. LV525333 - 1 Nos. LC1D25M7 - 1 Nos. email : service@eteelectro.com | Repair |  | 9- Service Validated | 2023-09-16 16:12 | ATP check Error in BFS Zfre order booked =S= Free Order 226046833 has been saved |  | 51 | INR | 51 | ENM POWER PRODUCTS
WO-11241355 | 103913839 | 2023-09-11 15:25 | 2023-09-11 | MCCB Voltage Output Issue | 2023-09-11 12:15 | C25N3MA220 | C25N3MA220 | C25N3MA220 | 10-2022-W30-3 | RE: MCCB Replacement Laxmi Mahad, Case: 103814550, [ thread::6_S74pbvfbKU7_sa3LjxfD4:: ] As Per The serial number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Laxmi organic industries ltd. plot no A22 , MIDC Mahad, distt - raigad Mahad 402309 Maharashtra India Contact Person Details:- Contact Person : Pratik Shirke / Prathamesh warang- 9766912464 Product and Issue:- Model number:- C25N3MA220 Serial number:- 10-2022-W30-3 Voltage reading difference in Input and Output terminals. | 2023-09-11 | 2023-09-12 10:52 | No | Warranty | Laxmi organic industries ltd. | plot no A22 , MIDC Mahad, distt - raigad | Mahad | 402309 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Sachin Jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked The MCCB Voltage Output Issue. checked input voltage found ok. but output voltage not getting proper. so problem observed in 1 month before. So MCCB needs to be replaced. Required Material : C25N3MA220- 01 nos | Repair |  | 9- Service Validated | 2023-09-13 16:37 | =S= Consig Fill up 226043439 |  | 165 | INR | 165 | ENM POWER PRODUCTS
WO-11241440 | 103912092 | 2023-09-12 18:37 | 2023-09-11 |  | 2023-09-11 12:42 | LRE21 | LRE21 | LRE21 | 8C2249 | As Per The serial number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- ACS ENGITECH PVT LTD 41,42,43 Barcelona Industrial Estate, Odhav Rd, Odhav, Ahmedabad 382415 Gujarat India Contact Person Details:- Darshil Bhatt Purchase Engineer MO:- 8758878079 Product and Issue:- LRE21------8C22492---NO/NC issue as per customer LC1E1210 F7 LC1E1801M7 Coil issue in contactors Customer also asked to check for MCB. Kindly check at site. | 2023-09-11 | 2023-09-12 18:59 | No | Warranty | ACS ENGITECH PVT LTD | 41,42,43 Barcelona Industrial Estate, Odhav Rd, Odhav, | Ahmedabad | 382415 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | Parthiv Patel JKS Ahmedabad | JKS Engineering Co. | We visit site check contactor on/off found ok check contactor body and terminal side not any damage.check contactor L1 thareding problem 5nos replacement. | Repair |  | 9- Service Validated | 2023-09-13 10:10 | =S= Consig Fill up 226042733 |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11316856 | 104308807 | 2023-09-27 18:17 | 2023-09-27 |  | 2023-09-27 15:27 | Easy UPS 3S 40 kVA 400 V 3:3 UPS for external batteries | E3SUPS40KH | E3SUPS40KH | 9E1934T15129 | AMC P: Fan faulty S: AMC | 2023-09-27 | 2023-09-29 14:54 | No | Contract | BESTCOMM NETWORKS INDIA PVT LTD | 401,3RD FLOOR BALLESHWAR SQUARE, OPP, ISCON TEMPLE, S G HIGHWAY | AHMEDABAD | 380015 | Gujarat | India FS West2 HBN CSP_Mahavir Sys Power Pvt Ltd Ahmedabad | Dhaval Chauhan_Mahavir Sys Power Pvt Ltd Ahmedabad | Mahavir Sys Power Pvt Ltd | Engineer visited the site and check ups, found 3 nos. of fan found faulty so he replace fans and now ups working fine. | Repair |  | 8- Service Completed | 2023-09-29 16:21 |  |  | 5 | INR | 5 | ENM SECURE POWER
WO-11241441 | 103920310 | 2023-09-21 17:35 | 2023-09-12 |  | 2023-09-11 12:42 | 30002568 | 30002568 | 30002568 | 54230240 | RE: Schneider Electric follow-up on Case 103878428 [ thread::qr7f71PReBCPsMSR-BsniT4:: ] Hi Team, As discussed please find the attached images of and video of the Metter and please schedule engineer visit Adress: D-37 sector-63 Noida Regards, Naveen Sharma Admin Department Mobile : 9821121802 iBoss Tech Solutions Pvt. Ltd. iBoss logo Following attachments are linked to this email: | 2023-09-11 | 2023-09-12 13:30 | No | Warranty | Iboss Tech Solutions | D-37,Sector 63 Noida | Noida | 201301 | Uttar Pradesh | India FS ED&I CSP North Team S D Electric Delhi | Arif Raza S D Electric Delhi | S D Electric (500017662) | visited the site. product found ok. | Repair |  | 8- Service Completed | 2023-09-21 17:52 | Hi Team Please change work order assignment to "SD Electric workd,Delhi" |  | 40 | INR | 40 | ENM POWER PRODUCTS
WO-11241504 | 103922396 | 2023-09-11 15:21 | 2023-09-11 |  | 2023-09-11 13:08 | LC1E65M7 | LC1E65M7 | LC1E65M7 | WH2315 | RELIANT DRILLING PVT LTD Reliant Drilling Housing Complex, Old A Type Colony, Dariba, Rajasmand. Pin Code : 313211 Mr Mehul 8905814890 | 2023-09-11 | 2023-09-11 15:24 | No | Warranty | RELIANT DRILLING PVT LTD | Reliant Drilling Housing Complex, Old A Type Colony, Dariba | RAJSAMAND | 313211 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | Checked the contactor found not getting on and vfd found not power up, Hence faulty replaced. LAEX3M7 -1 nos ATV340D18N4- 1nos Email : | Repair |  | 9- Service Validated | 2023-09-11 17:02 | 226035399 |  | 340 | INR | 340 | ENM POWER PRODUCTS
WO-11241508 | 103921720 | 2023-09-12 12:13 | 2023-09-11 |  | 2023-09-11 13:10 | INA_3P33472E | INA_3P33472E | INA_3P33472E | 10222050015 | FW: Issue with CM2 1000A Breaker Warranty INA_3P33472E SL# 10222050015 Issue: UV Coil Failure (switch ON/OFF problem in CM2 MCCB (1000A) incomer) Site Address: Buhler India Pvt ltd E20 Creenfuels Pvt Ltd Dawali-Kalianwali Road Village - Panniwala Ruldu Sirsa 125104 Haryana Subramaniam.M.V (Ph: +91 95000 47375) project@e20greenfuels.com | 2023-09-11 | 2023-09-12 12:14 | No | Warranty | Buhler India Pvt ltd | E20 Greenfuels Pvt Ltd Dawali-Kalianwali Road Village - Panniwala Ruldu | Sirsa | 125104 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Ram Ashish Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the mccb found not getting on due to UVR coil lever dislocated. Set right the same. Now working ok. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-12 12:19 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 255 | INR | 255 | ENM POWER PRODUCTS
WO-11318061 |  | 2023-09-28 10:35 | 2023-09-19 |  | 2023-09-27 18:51 | Easy UPS 3S 30 kVA 400 V 3:3 UPS for external batteries | E3SUPS30KH | E3SUPS30KH | 9E2122T12723 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-27 | 2023-09-28 12:28 | No | Contract | Waaree Energies Limited Survey | No-1934, Nh-48,Nr. Darshan Hotel null | Navsari | 396530 | Gujarat | India FS West2 HBN CSP_Nutech Sales & Support Anand | Dilip Parmar_Nutech Sales & Support Anand | Nutech Sales & Support | Ups Preventive Maintenance activity done and dust filter clean after this ups working fine. Both mode | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-28 12:33 |  |  | 240 | INR | 240 | ENM SECURE POWER
WO-11241716 | 103920945 | 2023-09-11 17:31 | 2023-09-11 |  | 2023-09-11 14:38 | LC1D1506M7 | LC1D1506M7 | LC1D1506M7 |  | LC1D1506M7 SL: 22063 Qty:1 P: Coil Not working | 2023-09-11 | 2023-09-12 13:35 | No | Warranty | Craftsman Automation Pvt Ltd | Plot No.282/9,10 Bommasandra-Jigani Link Road Industrial Area Rajapura Village, Jigani Hobli, Anekal Taluk, Bengaluru, Karnataka | Bangalore | 560105 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | C Gunasekaran_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | We had visited the site and checked the customer reported contactor.Found when 230 V AC given to coil, contactor getting latching and de-latching immediately. So we collected for tex analysis and replacement hand over to customer. | Repair |  | 9- Service Validated | 2023-09-12 23:37 |  |  | 40 | INR | 40 | ENM POWER PRODUCTS
WO-11241727 | 103920579 | 2023-09-11 15:37 | 2023-09-11 |  | 2023-09-11 14:40 | LV563306 | LV563306 | LV563306 |  | FW: DMAK ENERGIA As Per The Invoice copy The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Banas Medical College Civil hospital Bank Colony Palanpur Banaskantha 385001 Gujarat India Contact Person Details:- Jignesh----9712663496 Alternate number:- 6352220969 Product and Issue:- PART REF ? LV563306 Phase missing issue as per customer, Doing Bypass it is running, In few dolly free issue | 2023-09-11 | 2023-09-11 18:50 | No | Warranty | Banas Medical College | Civil hospital Bank Colony Palanpur | Banaskantha | 385001 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | Parthiv Patel JKS Ahmedabad | JKS Engineering Co. | We visit at site check mccb ezc250h4200 on/off working ok check mccb counitinuti working ok mccb physically found ok.check ezc400h4400n mccb on/off not working mccb mechanism stuck check ezc400h4400n check mccb on/off not working so now customer satisfaction 2nos mccb 1time give a replacement. | Repair |  | 9- Service Validated | 2023-09-12 14:54 | =S= Consig Fill up 226042686 |  | 145 | INR | 145 | ENM POWER PRODUCTS
WO-11241936 | 103928536 | 2023-09-11 20:24 | 2023-09-11 |  | 2023-09-11 16:14 | LV434000 | LV434000 | LV434000 | 0000HL22392505992240 | Reg : AWS HYD111 - IFM (LV434000) Communication issue Warranty Part code : LV434000 Serial no : 0000HL22392505992240 IFM Module not communicating Amazon Data Services India Pvt Ltd (HYD-111), Survey No 190, Chandanvelly Village, Hytabad, Shabad Mandal, Rangareddy District, Telangana - 509217 Christo Thomas - 9074737395 8547733458 christo.thomas1@se.com | 2023-09-11 | 2023-09-14 12:00 | No | Warranty | Amazon Data Services India Private Limited | Survey Number 190(P) of Chandanvelly Village / 195(P) of Hythabad Village, Shabad Mandal, Ranga Reddy District, | Shabad Mandal | 501503 | Telangana | India FS ED&I CSP South Team Sumanth Electrical Services Hyderabad | Pramoud Kumar_SUMANTH ELECTRICAL SERVICES HYDERABAD | Sumanth Electrical Services | Visited the Site and Inspected the Schneider Electric- LV434000- 01 No's. Here in our observation we found IFM is not communicating IFE. we have checked missing found OK and Auxiliary supply 240 VAC found OK.We have replaced with New IFM LV434000-01 No's and we have checked the operations which found OK. Complaint is closed. | Repair |  | 9- Service Validated | 2023-09-12 18:01 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 60 | INR | 60 | ENM POWER PRODUCTS
WO-11241944 | 103910594 | 2023-09-12 10:56 | 2023-09-11 |  | 2023-09-11 16:19 | GCR_MVS | GCR_MVS | GCR_MVS |  | 1250A ACB Spring charge Motor is found faulty (TYPE : MVS12N) Checklist for the Registration of Service Request Sr. No Particulars Doc. Ref :- SE/CCC/001/V0.1 1 Company Name & Complete Address with pin code - Where product is installed " M/s. REWA MSW ENERGY SOLUTIONS Pvt. Ltd. " Pahadiya village, Raura B.O Post office, Raipur - Karchuliyan Tehsil, REWA District, Madhya Pradesh - 486114 2 Contact Person at Site : Name & Mobile No. Mr. Saahoo/ 7978937504 Alternate Mobile No : Mr. Senthil/ 9113595682 3 Contact Person at Site - Email Address** 4 Product Issue Type (Please select from drop down of column C-9) Hardware Issue 5 Are you ready to troubleshoot the issue remotely ? Yes/NO. If Yes, Our technical support engineer will call back to troubleshoot the issue remotely. No 6 Defective Product Model/Part No (Pls refer FAQ sheet ) "ACB 1250A, 415V, 3P 4NO+4NC TYPE : MVS12N Qty. 01 ACB Spring charge Motor is found faulty " 7 Nature of Defect* - Defects Video and Photographs photographs attached in the mail 8 Shutdown availability if applicable yes 9 Photograph of product where Serial No/Batch Code or Date of Manufacturing printed - Please refer FAQ sheet to find the Batch code details on the products 10 Proof Of Purchase - Pease attach SE*** Authorised Partner Invoice soft copy along with this check list "MAIYAR INVOICE NO. 7825, date: 06.02.2023 " 11 Name & phone No: of person registering the Service Request PAVAN/ 8892878463 "All fields are mandatory. Free of cost service visit subjected to warranty policy of the product and contract between Schneider Electric and buying party . Warranty will be check either by serial no/Batch code/DOM printed on the product or date of invoice of our authorised partner /Schneider Electric direct invoice or Contract . Warranty policy may be change product to product or contract with the customer. * Kindly share defect symptoms instead of ""Not working"", Please share the link of large files(product photoes or videoes) ** End user will receive a survey asking feedback on service " SE*** - Schneider Electric Please fill above details and send this sheet to customer care, Customer care contact link is give below https://www.se.com/in/en/work/support/customer-care/contact-schneider-electric.jsp Please mention Service Request as key word and Product Name in email subject line e.g for Masterpact NW ACB Service Request - Service Request for Masterpact NW Our web site :- https://www.se.com/in/en/ | 2023-09-11 | 2023-09-13 16:22 | No | Warranty | Rewa MSW Energy Solution Pvt Ltd | Pahadia Village Branch Roura PO Raipur Karchurian Tehsil | Rewa | 486116 | Madhya Pradesh | India FS ED&I CSP West Team ABR Technical Service Indore | Chirag Jain_ABR Tecneical Services Indore | ABR Technical Services (9574) | Reached at site and checked ACB as per customer its spring charging motor not working then we checked ACB and it's spring charging motor wiring not connecting then we connected MCH wiring and found its spring charging properly so as per our observation it's not product issue it's wiring issue so we resolved this issue and now we are close this case | Repair |  | 9- Service Validated | 2023-09-13 16:24 |  |  | 650 | INR | 650 | ENM POWER PRODUCTS
WO-11241954 | 103920582 | 2023-09-11 17:37 | 2023-09-11 |  | 2023-09-11 16:25 | NX160TPNDIE | NX160TPNDIE | NX160TPNDIE |  | Customer details mentioned below. NX160TPNDIE Exide Industries Limited Survey no: 246, Chichuruganapalli village, Sevaganapalli Panchayath,Hosur - 635103 Mr Arul-9789496543 9844526633-Mr Suresh Bangalore@neptuneindia.com | 2023-09-11 | 2023-09-12 11:04 | No | Warranty | Exide Industries Limited | Survey no: 246, Chichuruganapalli village, Sevaganapalli Panchayath,Hosur | Krishnagiri | 635103 | Tamil Nadu | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | C Gunasekaran_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | As per our site visit and checked, Switch disconnector found flash over near terminals. we requesting customer to take approval from SE sales for further replacement,we This is burnt issue. | Repair |  | 9- Service Validated | 2023-09-13 11:16 |  |  | 40 | INR | 40 | ENM POWER PRODUCTS
WO-11242065 | 103930179 | 2023-09-12 10:20 | 2023-09-11 |  | 2023-09-11 17:02 | A9N4P63C | A9N4P63C | A9N4P63C |  | DOP: 12/6/2023 A9N4P63C DD2023-W17-C-5 Qty:1 P: Tripping issue | 2023-09-11 | 2023-09-12 16:36 | No | Warranty | Sri Balaji Steel | B 53 Mayapuri Phase 1 New delhi null | Delhi | 110064 | Delhi | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the MCB and found MCB have tripping issue, we resolve the issue by MCB side sticker clean. Now MCB is ok. Mail Id. chopraelectricals303@gmail.com | Repair |  | 9- Service Validated | 2023-09-12 18:34 |  |  | 37 | INR | 37 | ENM POWER PRODUCTS
WO-11242112 | 103883448 | 2023-09-13 12:46 | 2023-09-11 |  | 2023-09-11 17:18 | GCR_CVS_T1_06 | GCR_CVS_T1_06 | GCR_CVS_T1_06 | inv | Complaint MCCB -GENUS POWER INFRASTRUCTURE LTD JPR Dear sir, New pic found defective,please arrange an engineer to replace the MCCB on site. Items detail are following:- Product Name:- MCCB Make :-SCHNEIDER PART NO- :-MCCB 3P LV563316 QTY. :-01 NOS Name & Address of party:- GENUS POWER INFRASTRUCTURE LTD JPR SPL-3, RIICO INDL.AREA, SITAPURA, TONK ROAD, JAIPUR - 302022 CONTACT PERSON.- 1.Mr.ASHISH SHARMA MOB.-9784015105 2.SUNDER JANGID (8058296513) We have attached an invoice copy of the Drive. Please find the attachment. With Regards, Ramesh Kumar Salodia Mob.-9950566600 For EL-TRONICS 86-87A, Dhuleshwar Garden, Jaipur-302001 Tel:- 0141 - 4073216 | 2023-09-11 | 2023-09-13 12:48 | No | Warranty | Genus Power Infrastructures Ltd. | SPL 3, RIICO Industrial Area, Sitapura, Tonk Road | Jaipur | 302022 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Sunny Sharma Sharma Electric Jaipur | Sharma Electric Works | Checked the mccb found working ok. Email : id not provided by customer . | Repair |  | 9- Service Validated | 2023-09-13 12:56 |  |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11321881 |  | 2023-09-30 16:16 | 2023-09-30 |  | 2023-09-28 11:36 | LeonardoEVCW ( 1LDD10A302000AA ) 2Way PIBCV Valve Upflow with Heater Humidier & |  |  | C22023003036 | PM Approval from Sankar Ganesh | 2023-09-28 | 2023-09-30 16:17 | No | Pending Contract | Accenture Solutions Pvt Ltd | Block 14 Tritech Park Spacial Economic Zone Outer Ring Road Belandur Varthur Hobli Adugodi Road | Bangalore | 560103 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Akash MP_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-30 16:19 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11242226 | 103892704 | 2023-09-12 06:42 | 2023-09-11 |  | 2023-09-11 17:45 | GCR_NSX100_630 | GCR_NSX100_630 | GCR_NSX100_630 | 1023 | nsx400f mccb tp issue in utility panel at embassy hub Complaint Registration 1 Name of Customer M/s. Embassy Business Hub 2 Site Address Venkatala Village Chowdeshwari Layout Venkatala Bengaluru - 560064 3 Name of contact person at site Mr. Imran 4 Contact Phone / Mob. No: 7022193583 5 Defective product details MCCB, NSX400F, TP 6 Nature of Defect One Pole malfunctioning. ( RCA required ) 7 Warranty status Under warranty 8 Commissioned / Installed date Under commissioning 9 Name & phone No: of person registering the complaint Mahntesh: 9844725556 Complaint Date: 08-09-23 | 2023-09-11 | 2023-09-16 15:00 | No | Warranty | Embassy Business Hub | Plot 12 R T Nagar Venkatala Village Chowdeshwari Layout Venkatala | Bengaluru | 560064 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Mohammad Riyaz_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | i had visited the site and checked the customer reported mccb, the problem found was R phase continuity issue, so we replaced new and checked found working ok. | Repair |  | 9- Service Validated | 2023-09-17 10:14 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11321877 |  | 2023-09-30 16:12 | 2023-09-28 |  | 2023-09-28 11:33 | LeonardoEVCW ( 1LDD10A302000AA ) 2Way PIBCV Valve Upflow with Heater Humidier & | TUCV0700AN002 | TUCV0700AN002 | C22023003149 | PM Approval from Sankar Ganesh | 2023-09-28 | 2023-09-30 16:12 | No | Pending Contract | Accenture Solutions Pvt Ltd | Block 14 Tritech Park Spacial Economic Zone Outer Ring Road Belandur Varthur Hobli Adugodi Road | Bangalore | 560103 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Akash MP_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-30 16:15 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11321879 |  | 2023-09-30 16:07 | 2023-09-30 |  | 2023-09-28 11:35 | LEO. EVDXR407CEC FANTDAV0711A (1LAD11A100020AA) UPFLW WITH "H" VER. (F4) | TUAV0711AN005 | TUAV0711AN005 | C21730005577 | PM Approval from Sankar Ganesh | 2023-09-28 | 2023-09-30 16:07 | No | Pending Contract | Accenture Solutions Pvt Ltd | Block 14 Tritech Park Spacial Economic Zone Outer Ring Road Belandur Varthur Hobli Adugodi Road | Bangalore | 560103 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Akash MP_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-30 16:11 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11242348 | 103928925 | 2023-09-12 11:11 | 2023-09-11 |  | 2023-09-11 18:22 | GCR_LV_APFC | GCR_LV_APFC | GCR_LV_APFC |  | DOP: 12/6/2023 GCR_LV_APFC Qty:1 P: Not Working M/S- AGRIFINITY INDUSTRIES PRIVATE LIMITED E2, NEW INDUSTRIAL AREA II, MANDIDEEP RAISEN, MADHYA PRADESH- 462046 CONTACT PERSON- MR. SACHINE MOB. NO. - 8602664018 | 2023-09-11 | 2023-09-13 10:47 | No | Warranty | AGRIFINITY INDUSTRIES PVT. LTD | E-2, NEW INDUSTRIAL AREA-II, MANDIDEEP, RAISEN | BHOPAL | 462046 | Madhya Pradesh | India FS ED&I CSP West Team ABR Technical Service Indore | Lalu Sen_ABR Tecneical Services Indore | ABR Technical Services (9574) | Reached at site and checked APFC relay and as per customer not run/ working properly and not turn ON step then we checked relay and found its C/K :- 0.15 then we change 0.04 and CT ratio 600/5 , I/P supply use R &Y phase CT installed in B - Phase and then we operated relay manually turn ON all step working ok then we change some step wiring and set steps 10 to 11 and after all changes its working ok and as per our observation its not product issue its wiring and parameters issue so we resolved issue and we are close this case . | Repair |  | 9- Service Validated | 2023-09-14 10:50 |  |  | 220 | INR | 220 | ENM POWER PRODUCTS
WO-11321880 |  | 2023-09-30 16:01 | 2023-09-30 |  | 2023-09-28 11:36 | LEO. EVDXR407CEC FANTDAV0711A (1LAD11A100020AA) UPFLW WITH "H" VER. (F4) | TUAV0711AN005 | TUAV0711AN005 | C21728000260 | PM Approval from Sankar Ganesh | 2023-09-28 | 2023-09-30 16:02 | No | Pending Contract | Accenture Solutions Pvt Ltd | Block 14 Tritech Park Spacial Economic Zone Outer Ring Road Belandur Varthur Hobli Adugodi Road | Bangalore | 560103 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Akash MP_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-30 16:03 |  |  | 0 | INR | 0 | ENM SECURE POWER
WO-11242350 | 103930870 | 2023-09-12 16:11 | 2023-09-11 |  | 2023-09-11 18:24 | LV510307 | LV510307 | LV510307 | 10-2022-W34 | Failure MCCB 100A/TP As Per The serial number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- SHARMA ENTERPRISES khatoni.no. 629, Village Sambhli, Nissing Bypass, kila no. 6 Karnal 132001 Haryana India Contact Person Details:- Suresh Ji Contact No.: 88160 50300 Product and Issue:- LV510307 Serial number:- 10-2022-W34 Phase failure as per customer | 2023-09-11 | 2023-09-12 16:18 | No | Warranty | SHARMA ENTERPRISES | khatoni.no. 629, Village Sambhli, Nissing Bypass, kila no. 6 null | Karnal | 132001 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the MCCB found working ok. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-12 16:23 |  |  | 130 | INR | 130 | ENM POWER PRODUCTS
WO-11321882 |  | 2023-09-30 15:58 | 2023-09-30 |  | 2023-09-28 11:37 | LEONARDO EVTCDXR407C TDTV0921A (4LAD11A100C20AA) DOWNFLOW WITH "H" VERSION HOT | TDTV0921AN004 | TDTV0921AN004 | JK2028005035 | PM Approval from Sankar Ganesh | 2023-09-28 | 2023-09-30 15:58 | No | Pending Contract | Accenture Solutions Pvt Ltd | Block 14 Tritech Park Spacial Economic Zone Outer Ring Road Belandur Varthur Hobli Adugodi Road | Bangalore | 560103 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Akash MP_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-30 16:01 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11321886 |  | 2023-09-30 15:53 | 2023-09-30 |  | 2023-09-28 11:38 | LEONARDO EVTCDXR407C TDTV0921A (4LAD11A100C20AA) DOWNFLOW WITH "H" VERSION HOT | TDTV0921AN004 | TDTV0921AN004 | C22023002442 | PM Approval from Sankar Ganesh | 2023-09-28 | 2023-09-30 15:53 | No | Pending Contract | Accenture Solutions Pvt Ltd | Block 14 Tritech Park Spacial Economic Zone Outer Ring Road Belandur Varthur Hobli Adugodi Road | Bangalore | 560103 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Akash MP_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-30 15:57 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11246321 | 103951410 | 2023-09-12 12:05 | 2023-09-12 |  | 2023-09-12 10:53 | GCR_CVS_T1_06 | GCR_CVS_T1_06 | GCR_CVS_T1_06 |  | Invoice Copy Re: Service Request, Case: 103891288, [ thread::dhlvBv-vdo-sy0a28Ec12T4:: ] Checklist for Complaint Registration 1 Name of Customer : M/s.INDIA YAMAHA MOTOR PVT LTD, 2 Site Address : VV1, Sipcot Industrial Park, Vallam Vadagal, Taluk, Sriperumbudur, CHENNAI. Tamil Nadu 3 Name of Contact Person at Site : K.SARAVANANAKUMAR 4 Contact Phone / Mob. No : 9600070685 5 Defective Product Details : 400A 4P MCCB-CVS 6 Product Make : Schneider- 7 Nature of Defect : TRIPPING 8 Shutdown availability if applicable : Yes 9 Commissioned / Installed Date : Commission 10 Serial No: or DOM of the Product/OA No./Invoice Details : MAIYAR - Invoice No.2540 dated 08.07.2023 11 Name & Phone No: of the Person Registering the Complaint : V.Radhakrishnan - 9994306854 Note : Point Nos: 1 to 9 are compulsory | 2023-09-12 | 2023-09-12 18:00 | No | Warranty | India Yamaha Motors Private Limited | Plot No VV-1, SIPCOT Industrial Park,Vallan- Nadagal, sriperambattur Taluk Dist, Kanchipuram | Chennai | 631604 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Visited done | Repair |  | 9- Service Validated | 2023-09-13 12:08 |  |  | 44 | INR | 44 | ENM POWER PRODUCTS
WO-11321888 |  | 2023-09-30 15:49 | 2023-09-30 |  | 2023-09-28 11:38 | LEONARDO EVTCDXR407C TDTV0921A (4LAD11A100C20AA) DOWNFLOW WITH "H" VERSION HOT | TDTV0921AN004 | TDTV0921AN004 | C22024000459 | PM Approval from Sankar Ganesh | 2023-09-28 | 2023-09-30 15:50 | No | Pending Contract | Accenture Solutions Pvt Ltd | Block 14 Tritech Park Spacial Economic Zone Outer Ring Road Belandur Varthur Hobli Adugodi Road | Bangalore | 560103 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Akash MP_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-30 15:52 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11246856 | 103954197 | 2023-09-14 11:20 | 2023-09-12 |  | 2023-09-12 11:36 | MEHVCSDY250A44PB | MEHVCSDY250A44PB | MEHVCSDY250A44PB | ME-M2074057 | DOP: 26/5/2023 ME-M2074057 MEHVCSDY250A44PB Qty:1 P: Swell issue | 2023-09-12 | 2023-09-14 14:23 | No | Warranty | Frontier Alloys Steels Ltd | Jamniwala rd Jambookala Badrinagar Paonta Sahib null | Sirmaur | 173025 | Himachal Pradesh | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the capacitors found Terminals burnt due to improper termination. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-16 11:43 |  |  | 125 | INR | 125 | ENM POWER PRODUCTS
WO-11321889 |  | 2023-09-30 15:45 | 2023-09-30 |  | 2023-09-28 11:39 | LEONARDO EVTCDXR407C TDTV0921A (4LAD11A100C20AA) DOWNFLOW WITH "H" VERSION HOT | TDTV0921AN004 | TDTV0921AN004 | JK2133000452 | PM Approval from Sankar Ganesh | 2023-09-28 | 2023-09-30 15:46 | No | Pending Contract | Accenture Solutions Pvt Ltd | Block 14 Tritech Park Spacial Economic Zone Outer Ring Road Belandur Varthur Hobli Adugodi Road | Bangalore | 560103 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Akash MP_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-30 15:48 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11246874 | 103951234 | 2023-09-12 16:25 | 2023-09-12 |  | 2023-09-12 11:44 | GCR_APFC_DPIBS | GCR_APFC_DPIBS | GCR_APFC_DPIBS | 2023 | Team, Please depute engineer:- Name of the Customer:- E-20 Greenfuels Pvt. Ltd Site Address: Village Panniwala Ruldu, Dabwali Kalanwali Road, Tehsil Mandi Dabwali, Dist- Sirsa, Harwana -125105 Name of the Contact Person at Site : Mr. Sachin Panwar Contact Phone Number / Mob. No:- +91- 7503107872 Defective Product Detail:- 800KVAR APFC (Panel details enclosed) Nature of Defect : Not working in Auto mode Shutdown availability if applicable :- Yes Warranty Status : In Warranty Commissioned / Installed date : Dec 2022 Dealer Name /OA no./Invoice Details: Rexel India Serial No. or DOM of the product : Name & phone number of the person registering the complaint: Pankaj Lakhera Regards Pankaj Lakhera 9915466099 | 2023-09-12 | 2023-09-12 16:31 | No | Warranty | E20 Greenfuels Pvt Ltd | Village-Panniwala, Rudu Dabwali Tehsil-Mandi | Sirsa | 125104 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Ram Ashish Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the P.F Bank 800 KVR found working ok. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-12 17:20 |  |  | 255 | INR | 255 | ENM POWER PRODUCTS
WO-11321890 |  | 2023-09-30 15:42 | 2023-09-30 |  | 2023-09-28 11:40 | LEONARDO EVTCDXR407C TDTV0921A (4LAD11A100C20AA) DOWNFLOW WITH "H" VERSION HOT | TDTV0921AN004 | TDTV0921AN004 | JK2028005034 | PM Approval from Sankar Ganesh | 2023-09-28 | 2023-09-30 15:43 | No | Pending Contract | Accenture Solutions Pvt Ltd | Block 14 Tritech Park Spacial Economic Zone Outer Ring Road Belandur Varthur Hobli Adugodi Road | Bangalore | 560103 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Akash MP_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-30 15:45 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-10928337 | 102065259 | 2023-09-07 17:23 | 2023-06-28 |  | 2023-06-28 13:14 | SRV2KL-IN | SRV2KL-IN | SRV2KL-IN | 9S2308A00908 | DOP: 22-Jun-2023 P: Smart UPS Installation with SNMP card S; Installation | 2023-06-28 | 2023-09-07 17:36 | No | Commercial Action - Sales | ABBOTT HEALTHCARE PRIVATE LIMITED | 1st Floor, Y R Complex,9th cross, JP Nagar 2nd phase | Bangalore | 560078 | Karnataka | India FS South1 HBN CSP Central Data SystemsPvt.Ltd. Bangalore | Shambu Central Data SystemsPvt.Ltd. Bangalore | Central Data Systems Pvt Ltd-BLR004 | Installation has been done. UPS is working fine.. | Commissioning & Installation | Start-up | 10- Closed | 2023-09-07 17:39 |  |  | 3 | INR | 3 | ENM SECURE POWER
WO-11321891 |  | 2023-09-30 15:36 | 2023-09-30 |  | 2023-09-28 11:40 | LEONARDO EVTCDXR407C TDTV0921A (4LAD11A100C20AA) DOWNFLOW WITH "H" VERSION HOT | TDTV0921AN004 | TDTV0921AN004 | C22023001677 | PM Approval from Sankar Ganesh | 2023-09-28 | 2023-09-30 15:37 | No | Pending Contract | Accenture Solutions Pvt Ltd | Block 14 Tritech Park Spacial Economic Zone Outer Ring Road Belandur Varthur Hobli Adugodi Road | Bangalore | 560103 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Akash MP_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-30 15:40 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11247823 | 103963777 | 2023-09-12 17:19 | 2023-09-12 |  | 2023-09-12 15:40 | 30003005D | 30003005D | 30003005D |  | PM5560 Sr no- 600180007 DOM-22-03-2022 ref- 30003005D - 4 no Pm meter dispaly current is not sensing | 2023-09-12 | 2023-09-15 16:16 | No | Warranty | Aequs SEZ Private Limited | Aequs SEZ, Aequs Koppal Toy Cluster. Sy No 30 , Bhanapur and Talbal Villages, Kukanur Taluka null | Koppal | 583238 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | C Gunasekaran_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported meter the problem found was meter voltage reading not updating in B phase, due to internal hardware issue NTR. Remaining two meters found working ok. So we arranged 1nos meter to the customer. | Repair |  | 9- Service Validated | 2023-09-15 21:34 |  |  | 380 | INR | 380 | ENM POWER PRODUCTS
WO-11321953 | 104309846 | 2023-09-28 14:56 | 2023-09-28 |  | 2023-09-28 12:13 | Leonardo Ev,DX,R407c,TDAV0721A, Downflow With Heater and Humidifier | TDAV0721AN002 | TDAV0721AN002 | NUCW4352 | AMC P: Water leakage S: AMC | 2023-09-28 | 2023-09-30 10:00 | No | Contract | Vardhman Textiles Limited | Chandigarh Rd, Karam Colony, Ludhiana | Ludhiana | 141010 | Punjab | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Abhishek Sharma Freezeotech Airconditioning & Refrigeration Chandigarh | Freezeotech Refrigeartion & Air Conditioning Corporation | found water leakage issue we resolved it by cleaning of drain pipe now unit is working ok | Repair |  | 9- Service Validated | 2023-09-30 10:00 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two persons is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 105 | INR | 105 | ENM SECURE POWER
WO-11248042 | 103963206 | 2023-09-13 12:29 | 2023-09-12 |  | 2023-09-12 17:04 | LTMR100EBD | LTMR100EBD | LTMR100EBD | AA3330051388 | LTMR relay is Defective --2 Nos (Not working) As Per The Invoice number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Customer Code: CIN03270 Schneider Electric India Private Limited L&T Electrical & Automation Electrical Systems & Equipment (ESE) Manufacturing Facility L&T Bypass Road, Malumichampatti, Coimbatore 641 050 Contact Person Details:- Suresh Ji Mobile: +91-9790009087 Product and Issue:- LTMR100EBD AA3330051388 -- 29.03.2023 Not Powering Up by supplied voltage Faulty Quantity---2 | 2023-09-12 | 2023-09-14 22:19 | No | Warranty | Schneider Electric India Private Limited | Electrical Systems and Equipment ESE Manufacturing Facility, L and T Bypass Road,Malumichampatti | coimbatore | 641050 | Tamil Nadu | India FS ED&I CSP South Team Power Pro Engineering Services Coimbatore | KV ARUNKUMAR_POWER PRO ENGINEERIG SERVICES COIMBATORE | Powerpro Engineering Services | WE HAVE VISITED THE SITE AND INSPECTED WE FOUND LTMR RELAY POWER ON ISSUE WE HAVE CHECKED THE LTMR RELAY FOUND ALL ARE OK WE SUSPECT DUE TO THIS INTERNAL HARDWARE ISSUE WE HAVE COLLECTED THE DETAILS FOR FURTHER ACTION AND ARRAGING FREE REPALCEMENT FOR THIS | Repair |  | 8- Service Completed | 2023-09-19 19:24 |  |  | 21 | INR | 21 | ENM POWER PRODUCTS
WO-10877977 |  | 2023-08-30 09:57 | 2023-08-30 |  | 2023-06-19 08:46 | MISCELLANEOUS ANCILLARY EQUIPMENT | ANC-MISC | ANC-MISC | IK-RAC-35A-SS-BF-5960 | pm | 2023-06-19 | 2023-09-14 15:30 | No | Commercial Action - Service Ops | HDFC Bank Ltd | HDFC Bank Premises Main At Road Plot No 5/56 Vikas Nagar null | Dehradun | 248198 | Uttarakhand | India FS North2 Cooling CSP DTC System Uttrakhand | Devendra Kumar_DTC System Uttrakhand | DTC System | PM Work done | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-29 07:20 |  |  | 200 | INR | 200 | ENM SECURE POWER
WO-11248071 | 103966650 | 2023-09-14 11:44 | 2023-09-12 |  | 2023-09-12 17:17 | 33671 | GCR_NW_CB | GCR_NW_CB | WX-2023-W17-5 | 33671 - WX-2023-W17-5 operation issue Site Address: Gupta Metal Industries 38,Fourier Shankar Link Road, Jagadhri. Yamuna Nagar 135003 Haryana Mr. Sunil Kumar 9996805611 | 2023-09-12 | 2023-09-15 11:12 | No | Warranty | Gupta Metal Industries | 38,Fourier Shankar Link Road, Jagadhri. | Yamuna Nagar | 135003 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the ACB found coil is not getting on and burnt due to wrong voltage. As per product serial number is out of warranty. Hence no replacement given to customer. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-16 11:41 |  |  | 105 | INR | 105 | ENM POWER PRODUCTS
WO-11248093 | 103965744 | 2023-09-12 19:36 | 2023-09-12 |  | 2023-09-12 17:30 | LV540306 | LV540306 | LV540306 |  | DOP: 28/1/2023 LV540306 Qty:1 P: MCCB not switching off to open panel door Sanzyme Pharma MCH No.7-4-115, Survey No. 258 & 259 Gagan Pahad (V), Rajendranagar, Ranga Reddy Dist. Hyderabad-500052 Sravan Kumar 9912814494 | 2023-09-12 | 2023-09-19 12:00 | No | Warranty | Sanzyme Pharma | MCH No.7-4-115, Survey No. 258 & 259 Gagan Pahad (V), Rajendranagar, Ranga Reddy | Hyderabad | 500052 | Telangana | India FS ED&I CSP South Team Sumanth Electrical Services Hyderabad | Madhu Mantena_SUMANTH ELECTRICAL SERVICES HYDERABAD | Sumanth Electrical Services | Visited Site and Inspected Schneider Electric CVS MCCBs and in our observation we found that MCCB is having One Pole Continuity Problem and MCCB out going side major short circuit cleared by MCCB and MCCB Burnt out we have replaced with New MCCBs and Problem Got Resolved and Faulty MCCBs Collected Back to ASC CSP and Complaint Work order is Closed | Repair |  | 9- Service Validated | 2023-09-19 10:05 |  |  | 15 | INR | 15 | ENM POWER PRODUCTS
WO-11322542 |  | 2023-09-29 16:13 | 2023-09-29 |  | 2023-09-28 16:34 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | JK1941001292 | PM | 2023-09-28 | 2023-09-30 18:30 | No | Contract | Reliance Jio Infocomm limited | Village Vishram Nagar,Jalalabad null | shahjahanpur | 242221 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Karuna Tripathi Freezeotech Airconditioning & Refrigeration Lucknow | Freezeotech Airconditioning & Refrigeration Corporation | pm done clean the filter condenser unit with jet pump check all parameter unit is working ok | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-30 10:00 |  |  | 202 | INR | 202 | ENM SECURE POWER
WO-10877976 |  | 2023-08-30 10:01 | 2023-08-30 |  | 2023-06-19 08:46 | ANC-MISC | ANC-MISC | ANC-MISC | IK-RAC-35A-SS-BF-5896 | pm | 2023-06-19 | 2023-09-14 15:30 | No | Commercial Action - Service Ops | HDFC Bank Ltd | HDFC Bank Premises F End Unit 1st Open Market New Tehri Distt Tehri Garhwal Uttrakhand null | Garhwal | 249001 | Uttarakhand | India FS North2 Cooling CSP DTC System Uttrakhand | Padam Singh_DTC System Uttrakhand | DTC System | Pm Work Done | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-29 07:26 |  |  | 245 | INR | 245 | ENM SECURE POWER
WO-11248107 | 103960013 | 2023-09-12 17:51 | 2023-09-12 |  | 2023-09-12 17:37 | METSEPM1130HCL05RD | METSEPM1130HCL05RD | METSEPM1130HCL05RD |  | DOP: 8/9/2023 METSEPM1130HCL05RD Qty:1 P: Display issue Venuprasad HG, Cell: 9880660668 NIDHI CONTROLS No.04, 1st floor, Sir M. Vishweshwaraiah industrial Layout, Avalahalli Village, Anjanapura Post, Bangalore - 560062 | 2023-09-12 | 2023-09-13 15:57 | No | Warranty | NIDHI CONTROLS | NIDHI CONTROLS No.14, 1st floor, Sir M. Vishweshwaraiah industrial Layout, Avalahalli Village, Uttarahalli Hobli, Anjanapura Post, - . | Bangalore | 560062 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Mohammad Riyaz_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | i had visted the site and checked the customer reported the problem found was meter display not getting on so we had arenged the replacement from our stock . | Repair |  | 9- Service Validated | 2023-09-14 09:02 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11322543 |  | 2023-09-29 16:19 | 2023-09-29 |  | 2023-09-28 16:34 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | JK1942007650 | PM | 2023-09-28 | 2023-09-30 18:30 | No | Contract | Reliance Jio infocomm Ltd | JC, Gond 01, Plot No 892, Gopal Tower, Village Pathwalia null | Gonda | 271001 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Karuna Tripathi Freezeotech Airconditioning & Refrigeration Lucknow | Freezeotech Airconditioning & Refrigeration Corporation | pm done clean the filter condenser unit with jet pump check all parameter unit is working ok | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-30 10:05 |  |  | 202 | INR | 202 | ENM SECURE POWER
WO-11248137 | 103952443 | 2023-09-13 16:54 | 2023-09-12 |  | 2023-09-12 17:53 | LC1E12004M5WBIN | LC1E12004M5WBIN | LC1E12004M5WBIN |  | not working. LC1E12004M5WBIN operation issue Site Address: Core Metal Krafts Ltd Dera Bassi,Vill:Saidpura Mohali 140507 Punjab Mr. Sumit 9056656638 | 2023-09-12 | 2023-09-14 11:51 | No | Warranty | Core Metal Krafts Ltd.(105184) | Dera Bassi,Vill:Saidpura | Mohali | 140507 | Punjab | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Karnail Singh Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the contactor found coil not working. Hence faulty replaced. LAEX1TM5WB - 2 Nos. email : quality2@cmkl.co.in | Repair |  | 9- Service Validated | 2023-09-14 14:17 |  |  | 25 | INR | 25 | ENM POWER PRODUCTS
WO-11322547 | 104339804 | 2023-09-28 18:37 | 2023-09-28 |  | 2023-09-28 16:36 | Leonardo EV,DX,R407c,EC Fan,TDAV1622A(double Skin)Downflow With Heater & Humidif | TDAV1622AN004 | TDAV1622AN004 | ZK1548008425 | AMC P: High condensing pressure OR Compr Contactor Failed. S: AMC | 2023-09-28 | 2023-09-30 18:21 | No | Contract | VODAFONE GLOBAL SERVICES PRIVATE LIMITED | *Unit 1 A&B, Creator Building | BANGALORE | 560066 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Akash MP_UCS Projects and services Bangalore | UCS Projects & Services | EVD replacment | Repair |  | 8- Service Completed | 2023-09-30 18:25 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11248159 | 103965408 | 2023-09-13 09:15 | 2023-09-13 |  | 2023-09-12 18:02 | LC1D1506M7 | LC1D1506M7 | LC1D1506M7 |  | Complaint - LC1D1506M7 M M Forgings Ltd, Viralimalai Orion 6600, Sl.No.248 (BFW) As Per The Invoice copy The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- M/s M M Forgings Limited Plant 2 BUDAKUDI VILLAGE, KULATHUR VILLAGE, PUDUKOTTAI DIST. VIRALIMALAI - 621316 Contact Person Details:- Mr. Rajesh Kumar Mob No. : 73974 98495 Aruna BR Mob: 8884559336 Product and Issue:- LC1D1506M7 - 01 Coil issue Invoice No. 222313485 Date : 15-02-2023 | 2023-09-12 | 2023-09-21 18:00 | No | Warranty | M M FORGINGS LIMITED (PLANT-2) | BOOTHAKUDI VILLAGE KULATHUR TALUK VIRALIMALAI | PUDUKKOTTAI | 621316 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | George KJ_Omicon Engineering Madurai | Omicon Engineering | Site Visit Done | Repair |  | 9- Service Validated | 2023-09-22 09:25 |  |  | 101 | INR | 101 | ENM POWER PRODUCTS
WO-11253033 | 103992049 | 2023-09-13 13:26 | 2023-09-13 |  | 2023-09-13 12:02 | LC1D65AKUE | LC1D65AKUE | LC1D65AKUE |  | 103824439 - Wo Creation...!!! LC1D65AKUE Qty:2 No's Site Address: M/s Equitas Healthcare foundation, S.No81 /1B2, Gowrivakkam Village, Tambaram-Velachery Main Road, Chennai-600073. Contact Person: Mr. Jayakumar Mobile No: 98409 59542 | 2023-09-13 | 2023-09-13 17:30 | No | Warranty | Shri Vaari Electricals Pvt. Ltd. | M/S.Equitas Healthcare Foundation, No.81/1 B2, Gowrivakkam Village, | Chennai | 600073 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Visited Done | Repair |  | 9- Service Validated | 2023-09-13 17:53 |  |  | 33 | INR | 33 | ENM POWER PRODUCTS
WO-11252937 | 103991519 | 2023-09-13 12:27 | 2023-09-13 |  | 2023-09-13 11:19 | METSEEM6438HCL10RS | METSEEM6438HCL10RS | METSEEM6438HCL10RS |  | Dual Source Energy Meter is not working METSEEM6438HCL10RS - invoice shared Site Address: Manyavar SN G1/A & G1/B, GF, Fortune Monarch Mall, Road No 36, Jubilee Hills, Hyderabad, Telangana 500033 Contact Details : V Jitendra, 8885244246 | 2023-09-13 | 2023-09-17 12:00 | No | Warranty | Manyavar | SN G1/A & G1/B, GF, Fortune Monarch Mall, Rd Number 36, opposite N Grill, Jubilee Hills, | Hyderabad | 500033 | Telangana | India FS ED&I CSP South Team Sumanth Electrical Services Hyderabad | Madhu Mantena_SUMANTH ELECTRICAL SERVICES HYDERABAD | Sumanth Electrical Services | Visited the Site Inspected the Schneider Electric- METSEEM6438HCL10RS-01 No's. Here in our observation Meter Communication issue. We have replaced with New Meter and we have checked the ON/OFF operations which found OK. Complaint is closed. We Have Checked With Mod scan Software and Energy Meter is Getting Communicated with Mod Scan Software same was updated to End Customer and Panel Builder Elecon Power and Work order has been Closed | Repair |  | 9- Service Validated | 2023-09-18 14:50 |  |  | 20 | INR | 20 | ENM POWER PRODUCTS
WO-11253118 | 103930211 | 2023-09-13 14:21 | 2023-09-13 |  | 2023-09-13 12:47 | PCSP300D5IP00 | PCSP300D5IP00 | PCSP300D5IP00 | U22216002500 | Problem Facing-Over temperature Shutdown -Accusine PCS+(300A) PCSP300D5IP00 U22216002500 overheating issue Site Address: Mundra Solar Energy Limited(Adani Solar), Survey NO:180/P & Others,Village:Tunda,Taluk:Mundra,Kutch,Gujarat-370435 Mr. DARWIN I Mob No:+91-7708098901 | 2023-09-13 | 2023-09-18 10:11 | No | Warranty | Mundra Solar Energy Limited (Akshar Elecinfra) | Survey No 180 P and Others,, Village Tunda, Taluka Mundra | Kachchh | 370421 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Mohammad Aasif Anik Engineering Ahmedabad | Anik Engineering (554) | Visited site and checked the product observed physically ok. PCSP300DSIP00 obsreved ok and we open the product cover check the product observed lightly dust in side ( alrady shut down availabls ) . we observed cooling fan for control section bearing damage & dusting on fan. we replace the cooling fan and take trial ahf working ok. give cooling fan for replacement for customer satisfaction . | Repair |  | 9- Service Validated | 2023-09-20 10:13 | =S= Consig Fill up 226050185 |  | 380 | INR | 380 | ENM POWER PRODUCTS
WO-11253378 | 103997457 | 2023-09-14 11:22 | 2023-09-13 |  | 2023-09-13 14:13 | LC1D09M7 | LC1D09M7 | LC1D09M7 | 102140 | Complaint of a commector LC1D09M7 - 102140 operation issue Site address: SAMRIDHI FOODS VILLAGE KUTAIL, DISTRICT KARNAL 132001 HARYANA SITE PERSON NAME :- AMIT CONTACT NUMBER -9996142688 OR 9034436522 | 2023-09-13 | 2023-09-14 11:24 | No | Warranty | samruddhi foods | H2W3, Kutel road, Near Petrol pump | Karnal | 132114 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the contactor found working ok. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-14 11:37 |  |  | 130 | INR | 130 | ENM POWER PRODUCTS
WO-11327187 | 104360827 | 2023-09-29 13:12 | 2023-09-29 |  | 2023-09-29 12:43 | Amico 6 Tr,R22,Downflow with Heater & Hum. | SDA0601AN001 | SDA0601AN001 | NUCT1934 | DOP : AMC P : Outdoor Fan Faulty S : AMC/SIB | 2023-09-29 | 2023-09-29 17:30 | No | Contract | India Glycols Limited | PLOT NO 2B, SECTOR 126 | Gautam Buddha Nagar | 201304 | Uttar Pradesh | India FS North2 Cooling CSP D K AIRCON Delhi | Ajay Kumar_D K AIRCON Delhi | DK AIRCON | We have check & found PAC was showing high sound due to outdoor Fan Motor (High Sound) faulty Issue. We have Outdoor Fan dia 450mm(Hi-Cool) replacement work done and testing done. All paramenter check and found ok. Now PAC unit is working OK | Repair |  | 8- Service Completed | 2023-09-30 10:12 |  |  | 18 | INR | 18 | ENM SECURE POWER
WO-11327658 | 104367910 | 2023-09-30 09:40 | 2023-09-30 |  | 2023-09-29 16:35 | Leonardo EVDXR407cEC FanTUAV0611AUpflow With Heater Humidifier & Damper | TUAV0611AN004 | TUAV0611AN004 | JK2313001530 | DOP: In warranty P: PAC - Water Leakage Issue S: Onsite | 2023-09-29 | 2023-09-30 11:51 | No | Warranty | Orient Fashion Exports India Pvt Ltd | E-45/14, PHASE-II, OKHLA INDUSTRIAL AREA | New Delhi | 110020 | Delhi | India FS North1 Cooling CSP Hitech solutions New Delhi | Arvind Kumar_Hitech solutions New Delhi | Hitech Solutions-New Delhi-Delhi | checked the unit and found filter chocked due to cloth dust .clean the air filter and unit working ok . | Repair |  | 10- Closed | 2023-09-30 12:02 |  |  | 38 | INR | 38 | ENM SECURE POWER
WO-11253439 | 103996404 | 2023-09-13 14:47 | 2023-09-13 | NA | 2023-09-13 14:35 | GV4PE50N6 | GV4PE50N6 | GV4PE50N6 |  | DOP: 9/6/2023 9008595237 GV4PE50N6 Qty:1 P: Terminal Thread not working Royco Engineering Pvt Ltd UNIT - 2: GREEN PARK, HANSPUKUR, BAKRAHAT ROAD,KOLKATA - 700104 Mr Debarati Dubey 9038627955 | 2023-09-13 | 2023-09-21 15:30 | No | Warranty | Royco Engineering | Unit 2 , Green park, Hanspukur, Bakrahat Road, Bonogram | Kolkata | 700104 | West Bengal | India FS ED&I CSP East Team B.D Electroservices Kolkata | RAHUL RAY_B.D Electroservices Kolkata | B.D Electroservices(500017330) | New material hand over to customer and defective material collect from site. | Repair |  | 9- Service Validated | 2023-09-21 17:04 |  |  | 12 | INR | 12 | ENM POWER PRODUCTS
WO-11253691 | 103995821 | 2023-09-15 10:42 | 2023-09-13 |  | 2023-09-13 16:14 | LV563306 | LV563306 | LV563306 |  | Fwd: SHREE OM MINERALS As Per The Invoice The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- SHREE OM MINERALS Khasra no. 160,160/2, Vill. Basni hari Singh Tehsil. Bhopalgarh jodhpur 342901 Rajasthan India Contact Person Details:- Contact Person Contact: +91 9703651000 +91 9462721024 Product and Issue:- 630A 3P 36KA MCCB LV563306 MCCB is that it start tripping and shuts down due to heating while working | 2023-09-13 | 2023-09-15 10:46 | No | Warranty | SHREE OM MINERALS | Khasra no. 160,160/2, Vill. Basni hari Singh Tehsil. Bhopalgarh | jodhpur | 342901 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Amarjeet Singh Sharma Electric Jaipur | Sharma Electric Works | Checked the Mccb found working ok.R phase terminal heating too much due to loose termination, Hence no replacement given to customer. Email : id not provided by customer. | Repair |  | 9- Service Validated | 2023-09-15 17:07 |  |  | 338 | INR | 338 | ENM POWER PRODUCTS
WO-11253787 | 104004336 | 2023-09-15 10:34 | 2023-09-13 |  | 2023-09-13 16:55 | LC1D50AM7 | LC1D50AM7 | LC1D50AM7 | 8B22461 | Contactor B phase missing As Per The serial number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- RKGCOT YARNS PVT. LTD. CWMG+24X, Karbri Village, Nearby HP gas godown Panipat 132103 Haryana India Contact Person Details:- Sunder kashyap 7292095716 Product and Issue:- LC1D50AM7 SERIAL NUMBER:- 8B22461 B phase Output missing | 2023-09-13 | 2023-09-15 10:40 | No | Warranty | RKGCOT YARNS PVT. LTD. | CWMG+24X, Karbri Village, Nearby HP gas godown null | Panipat | 132103 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the contactor found B phase Output missing. Hence faulty replaced. LC1D50AM7 - 1 Nos. email : sundervelly@gmail.com | Repair |  | 9- Service Validated | 2023-09-16 13:29 |  |  | 165 | INR | 165 | ENM POWER PRODUCTS
WO-11253872 | 104004630 | 2023-09-15 14:37 | 2023-09-13 |  | 2023-09-13 17:27 | LC1E0910M7 | LC1E0910M7 | LC1E0910M7 |  | Complaint/Problem in Schneider Contactor As Per The Invoice The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Divine rising Food Pvt. Ltd. Shop No. - A - 62, Eastwood Village (Near Jalandhar Haveli), Jalandhar Phagwara GT Road KAPURTHALA 144411 Punjab India Contact Person Details:- Jaspal Singh 9518295125 Product and Issue:- LC1E0910M7, Phase Output Issue | 2023-09-13 | 2023-09-15 16:56 | No | Warranty | Divine rising Food Pvt. Ltd. | Shop No. - A - 62, Eastwood Village (Near Jalandhar Haveli), Jalandhar Phagwara GT Road null | KAPURTHALA | 144411 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | checked the contactor found phase missing Hence faulty, replaced. LC1E0910M7 - 1 Nos. Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-16 10:30 |  |  | 85 | INR | 85 | ENM POWER PRODUCTS
WO-11253935 | 104004154 | 2023-09-14 16:17 | 2023-09-13 |  | 2023-09-13 17:45 | LRD3359 | LRD3359 | LRD3359 |  | RELAY COMPLAINT As Per The invoice copy The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- HARSH ENGINEERING WORKS G-1-9 RIICO INDUSTRIAL AREA, UDAIPUR ? 313004 ( Raj ) Contact Person Details:- Contact person ? Keshu Ji ? 9636043098 Product and Issue:- LRD3359 SR-0444926 0121 01Nos \phase missing problem found | 2023-09-13 | 2023-09-14 16:19 | No | Warranty | HARSH ENGINEERING WORKS | G-1-9 RIICO INDUSTRIAL AREA null | UDAIPUR | 313004 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | checked the contactor and OLR Relay found working ok. On site dust and moisture present on product. and also found out of warranty from serial number. hence no replacement given to customer. Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-14 16:24 |  |  | 398 | INR | 398 | ENM POWER PRODUCTS
WO-11254006 | 103997720 | 2023-09-14 10:15 | 2023-09-13 | Contactor pole open issue | 2023-09-13 18:07 | LC1DT20BD | LC1DT20BD | LC1DT20BD |  | Re: CONTACTOR NOT WORKING, Case: 103956197, [ thread::mDM2wroScCmMUB47pS018j4:: ] LC1DT20BD operation issue Site Address: Drihten Technology Private Limited S no. 3/4, Tanishk Colony, Vishal Nagar, Pimple Nilakh, Pimpri-Chinchwad, Pune 411027 Maharashtra Mr. Vinod Shedole 8983418706 | 2023-09-13 | 2023-09-14 15:18 | No | Warranty | Drihten Technology Private Limited | S no. 3/4, Tanishk Colony, Vishal Nagar, Pimple Nilakh, Pimpri-Chinchwad, | Pune | 411027 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Sachin Jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the Contactor pole open issue. we given supply to contactor and taken on/off operation found ok. But L1 & T1 Pole found open. so it's problem is not repairable. So Contactor needs to be replaced. Required Material : LC1DT20BD - 01 nos | Repair |  | 9- Service Validated | 2023-09-15 13:00 | =S= Consig Fill up 226042159 |  | 40 | INR | 40 | ENM POWER PRODUCTS
WO-10928480 | 102067418 | 2023-09-07 17:43 | 2023-06-28 |  | 2023-06-28 13:59 | SRCE6KUXI | SRCE6KUXI | SRCE6KUXI | B22230005422 | DOP -20-06-2023 P -Smart UPS - installation S -installation | 2023-06-28 | 2023-09-07 17:45 | No | Commercial Action - Sales | MP Filtri India Pvt Ltd | Plot No 117 & 118 Aerospace Sector Hitech Defence & Aero Space park Devanahalli Bangalore null | Bangalore | 562129 | Karnataka | India FS South1 HBN CSP Central Data SystemsPvt.Ltd. Bangalore | Ramesh Central Data SystemsPvt.Ltd. Bangalore | Central Data Systems Pvt Ltd-BLR004 | Installation has been done. UPS is working fine.. | Commissioning & Installation | Start-up | 10- Closed | 2023-09-07 17:47 |  |  | 46 | INR | 46 | ENM SECURE POWER
WO-11254128 | 103992204 | 2023-09-14 09:49 | 2023-09-13 |  | 2023-09-13 18:37 | LV525303 | LV525303 | LV525303 |  | FW: ELECTRO MEK CONTROL LV525303 MCCB COMPLAINT LV525303 tripping issue Site Address: SHRI BHAGWATI STONEX PAIKI PLOT NO - 34, NEW BLOCK NO - 870, DHUNDHAR ROAD,DHUNDHAR,HIMATNAGAR, SABARKANTHA,383030 Mr. Mahendra Kumar 82391 71826 | 2023-09-13 | 2023-09-15 14:18 | No | Warranty | SHRI BHAGWATI STONEX | Plot No 34, Dhundhar, New Block No 870, Dhundhar Road Himatnagar null | Sabarkantha | 383030 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Mistri Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physicallly observed ok. according to customer mccb trip within 1-2 hours when on the motor. we observed customer used distribution application type mccb. its not suitable for motor application. we observed high corrosion on terminal screw & viser. we suggest to customer use ma trip unit typr mccb and replace serouces wiser. we start the motor starting current 200a & normal curent 45a motor working near 1.15 hours no tripping obsrved. RY 441 , YB 438 , BR 443 | Repair |  | 8- Service Completed | 2023-09-15 14:18 |  |  | 80 | INR | 80 | ENM POWER PRODUCTS
WO-11254233 | 104004273 | 2023-09-15 13:01 | 2023-09-13 |  | 2023-09-13 18:40 | PAS600 | PAS600 | PAS600 | 542248410035 | PAS600 S.NO : 542248410035 Qty:1 P: 1. Device not getting ON.( Display not getting On) VPN AGENCIIES M/S. VPN AGENCIIES Sales Off # 5, Corporation Shopping Complex, Avinashi Road, Coimbatore 641018 Mr.ARUL 9791866253 | 2023-09-13 | 2023-09-19 18:55 | No | Warranty | VPN Agenciies - 500017482 | 5, Ground Floor 1, Midland Complex | Salem | 636009 | Tamil Nadu | India FS ED&I CSP South Team Power Pro Engineering Services Coimbatore | KV ARUNKUMAR_POWER PRO ENGINEERIG SERVICES COIMBATORE | Powerpro Engineering Services | WE HAVE VISITED THE SITE AND INSPECTE WE FOUND PAS600 NOT GETTING POWER ON WE HAVE CHECKED THE POWER SUPLLY FOUND OK WE SUSPECT DUE TO PAS600 RELY INTERNAL HARDWARE MALL-FUNCTIOING COLLECTED THE DETAILS FOR FURTHER ACTION AND ARRAGING FOR FREE REPLACEMENT FOR THIS AND COLLECTED THE DEFECETIVE | Repair |  | 9- Service Validated | 2023-09-19 19:08 |  |  | 200 | INR | 200 | ENM POWER PRODUCTS
WO-11256820 | 104002808 | 2023-09-15 13:04 | 2023-09-14 |  | 2023-09-14 09:36 | EM7230 | EM7230 | EM7230 | 54512292 | DOM: 16-11-22 EM7230 S.NO : 54512292 Meter not getting ON.( Display not getting On) M/S. SOUTHERN ELECTRIC CONTROLS INDIA PRIVATE LIMITED SF.No.390/1,2 & 3, Kathir Naickenpalayam, K. Vadamadurai, Coimbatore, Tamil Nadu 641017 Mr.Kumar 9159519997 | 2023-09-14 | 2023-09-21 15:57 | No | Warranty | Southern Electric Controls India Pvt Ltd | 1/414A, Kothari Nagar K Vadamadurai Post | Coimbatore | 641017 | Tamil Nadu | India FS ED&I CSP South Team Power Pro Engineering Services Coimbatore | KV ARUNKUMAR_POWER PRO ENGINEERIG SERVICES COIMBATORE | Powerpro Engineering Services | WE HAVE VISITED THE SITE AND INSPECTE WE FOUND METER NOT GETTING POWE RON WE HAVE CHECKED THE POWER SUPLLY FOUND OK WE SUSPECT DUE TO METER INTERNAL HARDWARE MALL-FUNCTIOING COLLECTED THE DETAILS FOR FURTHER ACTION AND ARRAGING FOR FREE REPLACEMENT FOR THIS AND COLLECTED THE DEFECETIVE | Repair |  | 9- Service Validated | 2023-09-21 15:59 | Hi Team, Material booked zfre Zvo : 226055967 |  | 31 | INR | 31 | ENM POWER PRODUCTS
WO-11256854 | 104005714 | 2023-09-14 15:39 | 2023-09-14 |  | 2023-09-14 10:07 | LC1DMKM7 | LC1DMKM7 | LC1DMKM7 |  | Re: Replacement, Case: 102370262, kindly replace again | 2023-09-14 | 2023-09-16 16:56 | No | Warranty | JS Spintex limited | VILLAGE FATEHPUR PATIALA ROAD SAMANA PB 147101 | Samana | 147101 | Punjab | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Ram Ashish Sharma Electric Chandigarh | Sharma Electric works(1003) | checked the cap duty contactor found burnt. hence faulty, Harmonic level in current in very high so refuse for replacement. email : id not provided by the customer. | Repair |  | 8- Service Completed | 2023-09-16 16:56 |  |  | 125 | INR | 125 | ENM POWER PRODUCTS
WO-11258498 | 104024006 | 2023-09-14 13:07 | 2023-09-15 | During the inspection, we have observed the below points. 1. The new AHF is Not yet commissioned. 2. during the commissioning time, AHF gave the error Contcator not closed alarm. 3. We have found inside AHF Power board, Control board, and Filter board assy occupied some water/liquid/Rat urine and etc. 4. This is purely related to the material storage related issue. Please find the attached details, FYI. In this case, if any sales approval is there please let us know for the material booking | 2023-09-14 11:01 | PCSP300D5IP00 | PCSP300D5IP00 | PCSP300D5IP00 | U22149001240 | PCSP300D5IP00 U22149001240 Qty:1 P: AHF showing Contactor not Closed SKP HITECH CITY Silpa Gram Craft Village HITEC City Hyderabad, Telangana 500081 PRADEEP PATIL, KRISHNA, 9701558538, 9844501311 | 2023-09-14 | 2023-09-15 18:58 | No | Warranty | SKP HITECH CITY | Silpa Gram Craft Village HITEC City | Hyderabad | 500081 | Telangana | India FS ED&I CSP South Team ENERPRO ENGINEERING SOLUTIONS Vijayawada | ES Chowdary_ENERPRO ENGINEERING SOLUTIONS VIJAYAWADA | Enerpro Engineering Solutions - 500012682 | AHF CONTACTOR NOT CLOSING | Repair |  | 9- Service Validated | 2023-09-15 19:21 |  |  | 232 | INR | 232 | ENM POWER PRODUCTS
WO-11259058 | 104030800 | 2023-09-14 15:27 | 2023-09-14 |  | 2023-09-14 14:29 | LC1D80AM7 | LC1D80AM7 | LC1D80AM7 | 8B22273001015 | LC1D80AM7--Phase missing Issue As Per The serial number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- SHREE DHYANYOGIJI WELFARE FOUNDATION. ANANDIMAA MEDICAL CENTER DHYANIDHAM ASHRAM AT PO NIKORA Bharuch 392031 Gujarat India Contact Person Details:- Mr. HIREN SONI 9978343064 Product and Issue:- LC1D80AM7 SERIAL NUMBER:- 8B22273001015 phase Output missing | 2023-09-14 | 2023-09-15 14:57 | No | Warranty | SHREE DHYANYOGIJI WELFARE FOUNDATION. | ANANDIMAA MEDICAL CENTER DHYANIDHAM ASHRAM AT PO NIKORA | Bharuch | 392031 | Gujarat | India FS ED&I CSP West Team Jay Services Vadodara | Ghanshyam Kachiya_Jay Services Vadodara | Jay Services | we checked that contactor physically ok , incoming and out going terminals are ok but it is not on due to plunger not operate properly and contactor coil issue it is not repaireble now we replaced from our distributor stock .Measure coil voltage found 232V found ok . | Repair |  | 9- Service Validated | 2023-09-15 14:58 | =S= Consig Fill up 226057004 |  | 94 | INR | 94 | ENM POWER PRODUCTS
WO-11259258 | 104031929 | 2023-09-15 13:06 | 2023-09-14 |  | 2023-09-14 15:53 | LV540309 | LV540309 | LV540309 | 1023037 | REG : MCCB Not Working LV540309 - 1023037 pole continuity issue Site Address: Sri Ram Engg Product and services Near Renga Apparels,Pazhani Goundenpudur, Pannimadai Road,Coimbatore-641017 Mr. Sureshkumar / 9865704301 9345344150 | 2023-09-14 | 2023-09-21 15:55 | No | Warranty | SRI RAM ENGG PRODUCTS & SERVICES | Kurunthachalam Complex, 5/171-4, Near Renga Apparels, Pazhani Gounden Pudur, Pannimadai Road null | Coimbatore | 641017 | Tamil Nadu | India FS ED&I CSP South Team Power Pro Engineering Services Coimbatore | KV ARUNKUMAR_POWER PRO ENGINEERIG SERVICES COIMBATORE | Powerpro Engineering Services | WE HAVE VISITED THE SITE AND INSPECTE WE FOUND MCCB TRIP UNIT SCREW NOT TIGHT FULLY POLE OPEN CIRCUITED WHEN CONNECTING LOAD WE HAVE COLLECTED THE DETAILS FOR FURTHER ACTION AND ARRANGING FOR FRE REPALCEMENT FOR THIS AND COLLECTED THE DEFECTIVE | Repair |  | 9- Service Validated | 2023-09-21 15:57 |  |  | 31 | INR | 31 | ENM POWER PRODUCTS
WO-11259402 | 104026942 | 2023-09-14 19:09 | 2023-09-14 |  | 2023-09-14 17:09 | LC1E3210M7 | LC1E3210M7 | LC1E3210M7 |  | Plz Book Complaint minal electrical Dear team, please book direct complaint for below details Customer name :- MINAL ELECTRICAL MODEL ? LC1E3210M7 Address :- B-10, Karma Estate, Trikampura Patiya, GIDC, Vatva, Ahmedabad. Contact person Name :- Narendra Dhandhukiya Contact Person Mobile No :- +91 97732 96330 Problem Observed :- Contact Problems Brisk Invoice no. :- 107303 Brisk Invoice Date :- 10/08/2023 Please do needful for the same asap. Regards, Vidit Mewada Engineer, Marketing Brisk Electronics Pvt. Ltd., 304, Gala Argos,Near Harikrupa Tower, Kalgi Cross Road,Ellisbridge, Ahmedabad - 380006. Cell No. : +91 85111 48902. Tel: +91-79 35114713, Email: vidit.mewada@briskelectronics.com Website: www.briskelectronics.com | 2023-09-14 | 2023-09-15 10:05 | No | Warranty | Minal Electricals | 10/B, Karma estate, Trikampura patia, GIDC, vatva | ahmedabad | 382405 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | Parthiv Patel JKS Ahmedabad | JKS Engineering Co. | We visit at site check contactor on/off found ok.check contactor body and terminal found ok.check contactor l1 thared issue.1nos contactor replacement. | Repair |  | 9- Service Validated | 2023-09-15 16:50 | =S= Consig Fill up 226059581 |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11259543 | 104026358 | 2023-09-16 10:27 | 2023-09-14 | Meter not getting power up | 2023-09-14 18:25 | METSEEM6436HCL10RS | METSEEM6436HCL10RS | METSEEM6436HCL10RS | 140822 | COMPLAINT OF EM6436H METSEEM6436HCL10RS - 140822 display issue Site Address: Eternis Fine Chem limited D/9, MIDC Kurkumbh, Tal- Daund, Dist- Pune Pune 413802 Maharashtra Mr. Sidharth Mobile number- +9193370 32083 | 2023-09-14 | 2023-09-18 11:35 | No | Warranty | Eternis Fine Chemical Limited | D/9, MIDC Kurkumbh, Tal- Daund, Dist- Pune | Pune | 413802 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Samadhan S_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the Meter not getting power up. checked on/off operation but meter not getting power up. we checked voltage at terminal proper. so problem observed in meter. meter needs to be replaced. required material : METSEEM6436HCl10RS - 01 nos | Repair |  | 9- Service Validated | 2023-09-18 16:53 | =S= Consig Fill up 226042359 |  | 90 | INR | 90 | ENM POWER PRODUCTS
WO-11260289 | 104038497 | 2023-09-14 19:46 | 2023-09-14 |  | 2023-09-14 18:58 | LC1D95BD | LC1D95BD | LC1D95BD | PK2310400190 | Comaplint - Siddeshwara Controls LC1D95BD As Per The serial numberThe Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Pooja Power Products (1385) No.371 & 372, 10th cross road 4th phase Peenya Indl. Area, Bangalore-560058 Contact Person Details:- Mr. Arun Mob No. : 8884559336 Product and Issue:- LC1D95BD SCREW ISSUE Yes Nil PK2310400190 | 2023-09-14 | 2023-09-21 16:30 | No | Warranty | Pooja Power Products (1385) | 371 & 372, First floor, 10th cross, 4th phase, Penya industrial area | Bangalore | 560055 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | MANOJ GANESAN SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported 95A 3P contactor, screw threading issue at 2T1, so we had arranged for the replacement and zvo directly booked to pooja power products. | Repair |  | 9- Service Validated | 2023-09-21 21:55 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11262604 | 104039013 | 2023-09-15 10:59 | 2023-09-15 | NA | 2023-09-15 09:38 | A9N3P32C | A9N3P32C | A9N3P32C |  | We are purchase some MCB 32 AMP 3 POLE make Schneider on 10/07/2023 for our Factory Bead mill machine of paint from ARB Supply Syndicate (Invoice No. ARB/0495/23-24) at Kolkata, West Bengal. After electrical connection our Bead Mill machine are not work, electrician check and found the above MCB is defected. Please take into the matter very urgent basis. Thanking you from AG Fibrotech Pvt. Ltd. Dalim Banerjee Ph. 6290419976 | 2023-09-15 | 2023-09-16 14:45 | No | Warranty | A G Fibrotech Pvt Ltd | 12 C Naurbad, Chak Rajumolla, Near HP Petrol Bunk | SOUTH 24 PARGANAS | 700104 | West Bengal | India FS ED&I CSP East Team B.D Electroservices Kolkata | RAHUL RAY_B.D Electroservices Kolkata | B.D Electroservices(500017330) | Defective material replace with new one and checked on load ite working properly. | Repair |  | 9- Service Validated | 2023-09-16 16:18 |  |  | 20 | INR | 20 | ENM POWER PRODUCTS
WO-11264319 | 104035736 | 2023-09-16 10:00 | 2023-09-15 |  | 2023-09-15 11:42 | LC1D32M7 | LC1D32M7 | LC1D32M7 |  | As Per The serial number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Gupta Enterprises Shop No.: 3/W, Near Rama Stamp Paper, Model Town, Opp. D.C. Colony, Hissar, Hisar 125005 Haryana India Contact Person Details:- Nitin Ji Mobile +91-9215507886 Product and Issue:- 1. LC1D32 contactor 32A (sch.) 1pcs 220V supplied voltage Contactor plunger stuck Batch No. 10 2321 1 | 2023-09-15 | 2023-09-16 15:56 | No | Warranty | Gupta Enterprises | Shop No.: 3/W, Near Rama Stamp Paper, Model Town, Opp. D.C. Colony, Hissar, | Hisar | 125005 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Rakesh Kumar Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the contactor found "Y" Phase missing. Hence faulty replaced. LC1D32M7- 1 Nos. email : id not provided by the customer. | Repair |  | 8- Service Completed | 2023-09-18 09:57 |  |  | 255 | INR | 255 | ENM POWER PRODUCTS
WO-11264340 | 104056553 | 2023-09-16 16:44 | 2023-09-15 |  | 2023-09-15 11:51 | LV510307 | LV510307 | LV510307 | 10-2023-W14-3 | LV510307---Phase missing Issue As Per The serial number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- RISHABH MINERALS K. No.:- 478, Village:- Sankotra, Aandhi, Jamwa Ramgarh Jaipur 303101 Rajasthan India Contact Person Details:- Rishi Jain 9782136007 Product and Issue:- LV510307 Serial number:- 10-2023-W14-3 2 phase output Issue in MCCB | 2023-09-15 | 2023-09-15 16:46 | No | Warranty | RISHABH MINERALS | K. No.:- 478, Village:- Sankotra, Aandhi, Jamwa Ramgarh null | Jaipur | 303101 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Sunny Sharma Sharma Electric Jaipur | Sharma Electric Works | Checked the mccb found phase missing, Hence faulty replaced. LV510307 - 1 nos Email : rishjain05@gmail.com | Repair |  | 8- Service Completed | 2023-09-19 12:27 |  |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11264600 | 104059143 | 2023-09-16 12:47 | 2023-09-15 |  | 2023-09-15 13:14 | MEHVCSDY250A44PB | MEHVCSDY250A44PB | MEHVCSDY250A44PB |  | Capacitor 25 KVAR not working MEHVCSDY250A44PB Purchased from jagdamba electrical panipat dated on 21 Dec 2022 | 2023-09-15 | 2023-09-19 16:54 | No | Warranty | Rahul rahul | near power house , kabri raod , shre shya,m testile | Panipat | 132102 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the capacitor found derated & buldged. Hence faulty replaced. MEHVCSDY250A44 - 1 Nos. email : id not provided by the customer. | Repair |  | 8- Service Completed | 2023-09-19 17:13 |  |  | 165 | INR | 165 | ENM POWER PRODUCTS
WO-11265254 | 104061930 | 2023-09-15 18:28 | 2023-09-15 |  | 2023-09-15 17:35 | LC1E40M7 | LC1E40M7 | LC1E40M7 |  | Book Complaint - CESS CONTROLS As Per The Invoice The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Cess Controls 42/1, Ahmedabad Building Material Assciation, Near Stovec Industries, NIDC, Narol ? Lambha Road, Lambha Village Ahmedabad 382405 Gujarat India Contact Person Details:- Contact Person : Mr.Jagdishbhai, +917435086579 Product and Issue:- Product : LC1E40M7 (1 NOS.) Fault : Not working properly. | 2023-09-15 | 2023-09-16 14:07 | No | Warranty | Cess Controls | 42/1, Ahmedabad Building Material Assciation, Near Stovec Industries, NIDC, Narol ? Lambha Road, Lambha Village | Ahmedabad | 382405 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | Parthiv Patel JKS Ahmedabad | JKS Engineering Co. | We visit at site check contactors body and terminal side not any damage.check contector coil burning.check coil customer supplay to high voltage and coil burning as per not a product problem so we have not consider in worranty and give back to customer | Repair |  | 9- Service Validated | 2023-09-16 14:14 |  |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-10878948 |  | 2023-09-21 07:58 | 2023-06-19 |  | 2023-06-19 14:22 | SRCE6KUXI | SRCE6KUXI | SRCE6KUXI | B21738002773 | approved by Shankar Ganesh PM | 2023-06-19 | 2023-09-21 21:17 | No | Pending Contract | TCS Eservs International Ltd | 2nd Floor Unit 2,3,4 Saipress Building Asences IT Park Plot #18 MIDC SEZ 3 Hinjewadi null | Pune | 411057 | Maharashtra | India FS West1 HBN CSP_United Solutions Pune | Hamid Sayyad_United Solutions Pune | United Solutions | Done PM. check ups . ups is working fine | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-21 21:18 |  |  | 0 | INR | 0 | ENM SECURE POWER
WO-11265316 | 104065663 | 2023-09-16 15:06 | 2023-09-15 |  | 2023-09-15 18:08 | LC1D115M7 | LC1D115M7 | LC1D115M7 | PK22493 | Complaint of LC1D115M7 at Shree Ram Mega Structure Pvt Ltd. As Per The serial number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Shree Ram Mega Structure Khasra No. 630/2, Gram Panchayat Gidani, Chandarmool, Tehsil Mozamabad Jaipur 303348 Rajasthan India Contact Person Details:- Contact Person : Mr. Manish (Ph:93140-87654) Product and Issue:- LC1D115M7 PK22493 1 NOS. O/P Phase loss | 2023-09-15 | 2023-09-16 15:08 | No | Warranty | Shree Ram Mega Structure | Khasra No. 630/2, Gram Panchayat Gidani, Chandarmool, Tehsil Mozamabad null | Jaipur | 303348 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | checked the contactor found working ok. Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-16 15:11 |  |  | 55 | INR | 55 | ENM POWER PRODUCTS
WO-11267725 | 104076724 | 2023-09-16 12:30 | 2023-09-16 |  | 2023-09-16 10:05 | LV432894 | LV432894 | LV432894 | 1021471 | Pragathi Controls 6/a 4th main JC industrial area Kanakapura Main Road Bangalore -560 062 GIRISH 9844501311 LV432894 & LV432641 , 32493 Schneider Electric 1 SET NOT WORKING Yes Yes 10Days (AA331003951 or 1021471) & AA3310123212 M/s VIDYA 9353678519 | 2023-09-16 | 2023-09-19 10:17 | No | Warranty | Pragathi Controls | Unit -2, 9/16, 4th Main,J.C Industrial Layout, Yelachenahalli,Kanakapura Main Road | Bangalore | 560062 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | C Gunasekaran_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | we had visited the panal builder place and observed MCCB get burnt at R-phase input side and motor mech also burnt.Due to external fault and not in end customer place,we unable to arrange the free replacement and rejected replacement. | Repair |  | 9- Service Validated | 2023-09-19 22:21 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11267739 | 104076778 | 2023-09-16 14:29 | 2023-09-16 |  | 2023-09-16 10:29 | LC1D40AM7 | LC1D40AM7 | LC1D40AM7 | 8B 23161 | Product : LC1D40A M7 Sr No. 8B 23161 DOM April 2023 Issue: Contactor is not getting ON Coil Failure Patial Electricals and Electronics Shop No. 5-6,Abhi Enclave,Main Road, Block C,Isher Nagar, Backside,GNE College,Ludhiana. Pin 143526 Mr.Nirmal 8283000125 patialelectrical@gmail.com | 2023-09-16 | 2023-09-16 14:34 | No | Warranty | Patial Electricals and Electronics | Shop No. 5-6, Abhi Enclave, Main Road, Block C, Isher Nagar, Backside, GNE College | Ludhiana | 141006 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the contactor found phase missing and vfd found not power up. Hence faulty replaced. LC1D40AM7 - 1 Nos. ATV310HD11N4E - 1 Nos. Email : id not provided by the customer. | Repair |  | 8- Service Completed | 2023-09-16 16:45 |  |  | 25 | INR | 25 | ENM POWER PRODUCTS
WO-11268440 | 104068410 | 2023-09-19 10:35 | 2023-09-16 |  | 2023-09-16 10:48 | METSEEM6433HCL10RS | METSEEM6433HCL10RS | METSEEM6433HCL10RS | 28 06 2022 | Re: Faulty Meter- EM6433, Case: 103933703, [ thread::_YkLJnlTeRWtoQLJ2nebyD4:: ] METSEEM6433HCL10RS - 280622 Display issue Site Address: Unitech -Power Opp. Rajasthan Patrika, Sundarwas, UDAIPUR 313002 Rajasthan Mr. Lal Singh 9636043098 | 2023-09-16 | 2023-09-19 10:37 | No | Warranty | Unitech -Power | Opp. Rajasthan Patrika, Sundarwas, | UDAIPUR | 313002 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | Checked the meter found communication issue, Hence faulty replaced. METSEEM6433HCL10RS- 1 nos Email : id not provided by customer . | Repair |  | 8- Service Completed | 2023-09-19 12:25 |  |  | 395 | INR | 395 | ENM POWER PRODUCTS
WO-11269379 | 104064981 | 2023-09-18 10:57 | 2023-09-16 |  | 2023-09-16 12:13 | CA2KN22M7 | CA2KN22M7 | CA2KN22M7 | 8B22157 | Regarding 2 Nos 2R2 TX control contractor mechanical issue faced at Air Product Rai Bareilly Site CA2KN22M7 - 8B22157 contact changeover issue Site Address: PRODAIR AIR PRODUCTS INDIA PVT. LTD., C/O INOX AIR PRODUCTS PVT. LTD., PLOT NO A-10-SITE-2-INDUSTRIAL AREA, DHAUHARAVA, TEHSIL RAEBARELI, PIN CODE ? 229001(U.P.) Mr. Mohammed Ashish 9663843006 | 2023-09-16 | 2023-09-23 14:54 | No | Warranty | Inox air product private limited | Plot no A10 52 Industrial area Dhauharava Tehsil | Raebareli | 229001 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Aman Khare_Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found control contactor having internal issue so we replaced. | Repair |  | 8- Service Completed | 2023-09-23 15:08 |  |  | 110 | INR | 110 | ENM POWER PRODUCTS
WO-11269505 | 104076905 | 2023-09-16 16:28 | 2023-09-16 |  | 2023-09-16 15:51 | 30003008D | 30003008D | 30003008D |  | Repair/Replace Material as earlier as Possible As Per The Invoice The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Mutech Engineers 437/2, GIDC Estate, Makarpura, Behind Manjalpur Police Station, Vadodara 390010 Gujarat India Contact Person Details: Name of the Contact Person at Site : Mr. Dharmesh Makwana. Contact Phone Number / Mob. No : +91 9726763627 Product and Issue:- Defective Product Details : POWER METER(PM5560) Part NO. : 30003008D(PM5560) Invoice No. : AA3330075238 Invoice Date. : 20-05-23 Sys Doc No. : 9008564399 SOA No. : 225704738 No. of pieces : 1 Nature of Defect : POWER METER DISPLAY NOT WORKING . | 2023-09-16 | 2023-09-18 15:31 | No | Warranty | Mutech Engineers | 437/2, GIDC Estate, Makarpura, Behind Manjalpur Police Station, | Vadodara | 390010 | Gujarat | India FS ED&I CSP West Team Jay Services Vadodara | Ghanshyam Kachiya_Jay Services Vadodara | Jay Services | We visited at site & checked that meter physically ok.but are gine - 230v Ac then mcb trip It is internaly short. Now We replaced mater from our distributor stock. | Repair |  | 9- Service Validated | 2023-09-18 15:32 | =S= Consig Fill up 226013727 |  | 7 | INR | 7 | ENM POWER PRODUCTS
WO-11269533 | 104077049 | 2023-09-16 21:11 | 2023-09-16 |  | 2023-09-16 16:50 | EM7280 | EM7280 | EM7280 | 44881 | EM7230 METER NOT WORKING EM7280 - 16Nov2022 button issue/Hardware issue Site Address: MV METAL MART PVT LD SF No; 1/2A, 1/2B,1/2C, NAICKER THOTTAM ROAD SEELANACKEN PATTI BYE PASS-SELAM-636-201 Mr : PRANESH- 7598992569 97866246484 | 2023-09-16 | 2023-09-21 15:47 | No | Warranty | MV METAL MART PVT LTD | SF No. 1/2A, 1/2B, 1/2C, NAICKER THOTTAM ROAD, SEELANACKEN PATTI BYPASS | SALEM | 636201 | Tamil Nadu | India FS ED&I CSP South Team Power Pro Engineering Services Coimbatore | KV ARUNKUMAR_POWER PRO ENGINEERIG SERVICES COIMBATORE | Powerpro Engineering Services | WE HAVE VISITED THE SITE AND INSPECTED WE FOUND METER BUTTON ISSUE NOT CHNAGING THE PARA METER WE SUSPECT DUE TO THIS INTERNAL METER MALL-FUCNTIOING COLLECTED THE DETAILS FOR FURTHER ACTION AND ARRANGING FOR FREE REPLCEMENT FOR THIS AND COLLECTED THE DEFECTIVE | Repair |  | 9- Service Validated | 2023-09-21 15:53 |  |  | 198 | INR | 198 | ENM POWER PRODUCTS
WO-11269556 | 104077689 | 2023-09-19 15:35 | 2023-09-16 |  | 2023-09-16 17:38 | LC1D65AF7 | LC1D65AF7 | LC1D65AF7 | 8B2304 | Contactor 65A LC1D65A not working As Per The serial number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Classic Automation Plot No 60,Sub division 25,Metal box compound, NIT Faridabad 121001 Haryana India Contact Person Details:- Vinay Upadhyay 9911777473 Product and Issue:- Model number:- LC1D65AF7 SN :- 8B23045 Plunger not moving by giving voltage supply | 2023-09-16 | 2023-09-19 15:39 | No | Warranty | Classic Automation | Plot No 60,Sub division 25,Metal box compound, NIT | Faridabad | 121001 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the contactor found coil burnt due abnormal voltage, Hence no replacement given to customer. Email : id not provided by customer . | Repair |  | 8- Service Completed | 2023-09-19 15:58 |  |  | 45 | INR | 45 | ENM POWER PRODUCTS
WO-11269566 | 104077678 | 2023-09-16 19:22 | 2023-09-16 |  | 2023-09-16 17:46 | LC1D50AM7 | LC1D50AM7 | LC1D50AM7 |  | COMPLAIN - DT 16.09.2023 As Per The Invoice copy The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Premier Automation GS-7/3, Raghuveer Complex, Nr, Quick Metal Bus Stand Odhav Road Ahmedabad 382415 Gujarat India Contact Person Details:- CONTACT : Mr. Sanjaybhai ( Mob : 9662139007 ) Product and Issue:- 1. LC1D50AM7 ----- contact not working 2. LC1D09M7 ------- contact not working 3. A9N3P06C ------- pole open | 2023-09-16 | 2023-09-19 16:28 | No | Warranty | Premier Automation | GS-7/3, Raghuveer Complex, Nr, Quick Metal Bus Stand Odhav Road | Ahmedabad | 382415 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | Parthiv Patel JKS Ahmedabad | JKS Engineering Co. | Check mcb a9kf71310 2th pole open check mcb a9n4p63c 1st pole open.check lc1e2510m7 l3 and t3 pole open check laen11 auxilay contact not cannect not working | Repair |  | 9- Service Validated | 2023-09-20 10:40 | 226064783 |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11271184 | 104077652 | 2023-09-17 16:22 | 2023-09-19 |  | 2023-09-16 19:47 | METSEEM1220HCL5 | METSEEM1220HCL5 | METSEEM1220HCL5 | 40923 | BOOK DIRECT COMPLAINT -- OPTIMIZED SOLUTIONS LIMITED METSEEM1220HCL5 - 040923 button issue/Hardware issue Site Address: Havells India Pvt Ltd Opp old banyan tree lane, Central Expy, Appaiahpalem, Sri City, Tirupati 522041 Andhra Pradesh Mr. Ashwani Nair +91 98984 76047 | 2023-09-16 | 2023-09-27 17:00 | No | Warranty | Havells India Pvt Ltd | Opp old banyan tree lane, Central Expy, Appaiahpalem, Sri City, | Tirupati | 522041 | Andhra Pradesh | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Site Visit Done | Repair |  | 8- Service Completed | 2023-09-27 18:48 |  |  | 95 | INR | 95 | ENM POWER PRODUCTS
WO-11275107 | 104078888 | 2023-09-19 18:39 | 2023-09-18 |  | 2023-09-18 10:28 | TPRST009 | TPRST009 | TPRST009 |  | acing too many issues for production and as well as to the equipment. Pl arrange the support immediately to find out the root cause. Its very urgent now, since it is in production. Model No TeSys island Starter 9 A / 4 kW TPRST009 Customer Address : Lakshmi Snacks ,Pij Chokdi, Tundel(V), Nadiad(T), ,Kheda(D), Gujarath - 387230 ,Kheda Contact Person : Mr. Dhanush - 9912938699 | 2023-09-18 | 2023-09-25 14:07 | No | Warranty | Lakshmi Snacks | Pij Chokdi, Tundel(V), Nadiad | Kheda | 387230 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Mohammad Aasif Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked TPRST009 SR NO : 002F72317280094, 002F2230580060 physically observed ok. connect with bus coupler and the somove but one starter working ok in face mode. but 2 Nos starter not working in force mode. also one nos starter having red led continous. in previous visit we talk with customer give a supply to bus coupler through seprate power supply but customer not give a seprate power to bus coupler. suggested to customer please give a supply to bus coupler otherwise warranty is void. one time free replacemnet for customer satisfaction. | Repair |  | 9- Service Validated | 2023-09-25 14:07 | =S= Consig Fill up 226079527 |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11279301 | 104094738 | 2023-09-20 10:33 | 2023-09-19 |  | 2023-09-19 09:57 | LC1D32M7 | LC1D32M7 | LC1D32M7 |  | Doc. Ref :- SE/CCC/001 Sachin Electrical & Maintainance Works X-367, MIDC Area, Waluj Aurangabad-431136 Siddheshwar Desale 9766595113 1) LC1D32M7?1NO.2) LC1D09M7?1 NO.3)A9N4P40C?1 Contactor 1pole open. MCB dolly free 0 S.K.Traders Invoice No: 241656 dated 24/08/23 Kothale S.S 9373169403 | 2023-09-19 | 2023-09-25 15:00 | No | Warranty | Sachin Electrical & Mantinace Works | X-367, MIDC, Waluj, | Aurangabad | 431136 | Maharashtra | India FS ED&I CSP West Team Vaishnavi Electricals Nashik | Sagar Mane_Vaishnavi electrical Nashik | Vaishnavi Electricals (1364) | as per problem reported by customer is contactor & MCB pole is open. we have checked the contactor and giving auxiliary supply we have found LC1D09M7 contactor found OK. we have checked A9N4P04C 1 Qty its found OK. also we have checked LC2D32F7 we observed B pole continuity open after 2 3 operations & also needs to press from top side . to get the continuity . LC1D32F7 needs to be replace. We have arrange the contactor from S K traders same given to the customer. so we are closing this case. | Repair |  | 9- Service Validated | 2023-09-25 15:00 | =S= Consig Fill up 226068334 |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11279851 | 104086630 | 2023-09-19 18:27 | 2023-09-19 |  | 2023-09-19 10:44 | EZC250H4250 | EZC250H4250 | EZC250H4250 |  | #COMPLAIN LETTER As Per The serial number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Ahmedabad Electric Corporation SHED NO 25 AND 38, ADARSH INDUSTRIAL PARK, B/H G.V.M.M NR, ABHI SHREE ESTATE, NAVA ODHAV Ahmedabad 382415 Gujarat India Contact Person Details:- CON NUM-+91 91736 89721 Product and Issue:- EZC250H4250 EZC630H3600N > TRIPPING PROBLEM IN EZC250 3> SWITCH PROBLEM IN EZC630 | 2023-09-19 | 2023-09-20 09:53 | No | Warranty | Ahmedabad Electric Corporation | SHED NO 25 AND 38, ADARSH INDUSTRIAL PARK, B/H G.V.M.M NR, ABHI SHREE ESTATE, NAVA ODHAV | Ahmedabad | 382415 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Mohammad Aasif Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physically observed ok. EZC630H3600H SR NO : TC 2023 W07 on off mechasnism problme (1 Nos ) so free replacement. EZE250H4 250 SR NO : 2022 W14 observed on off mechanism problem so free replacement. A9KF71210 SR NO : D2225 observed mcb dolly free so free replacement. LC1E0910F7 SR NO : 1021230 observed screw thread problem customer give invoice so free replacement. Check the above drive physically osberved ok. ATV320U15N4C SR NO : HL2307031147 below igbt and rectifier section observed ok. so as per customer control card contact problem. so we collect the drive at out asc for further action. we checked connector pin found damaged. as per our primary observation it may be damage due to mishandling by customer . for customer satisfaction replace the control card from rts drive. | Repair |  | 9- Service Validated | 2023-09-20 09:53 | =S= Consig Fill up 226068972 |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11279852 | 104113541 | 2023-09-20 17:15 | 2023-09-19 |  | 2023-09-19 10:44 | LC1D25M7 | LC1D25M7 | LC1D25M7 | 1021414 | LC1D25M7 - 1021414 operation issue Site Address: NSW INDIA LIMITED Plot No. 43-44, Sector-34 EHTP, Gurgaon, Haryana. GURGAON 122001 Haryana Mr. Yogesh 9718692277 | 2023-09-19 | 2023-09-20 17:18 | No | Warranty | NSW INDIA LIMITED | Plot No. 43-44, Sector-34 EHTP, Gurgaon, Haryana. | GURGAON | 122001 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the contactor found not getting on due contact stuck but as per serial number out of warranty, Hence no replacement given to customer. Email : id not provided by customer. | Repair |  | 8- Service Completed | 2023-09-20 17:21 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11280055 | 104055628 | 2023-09-19 12:01 | 2023-09-19 |  | 2023-09-19 10:48 | LV510315 | LV510315 | LV510315 |  | LV510315 10-2023-W18-6-2563L1 P: Rotary broken TESLA CONTROLS INDIA PRIVATE LIMITED Emsy Square" No.4, Saranya Nagar, Thirumudivakkam-Kundrathur Main Road, Chennai - 600 044 Contact Person: Manavalan Mobile No: 84284 69586 | 2023-09-19 | 2023-09-19 18:00 | No | Warranty | TESLA CONTROLS (I) PVT LTD | Emsy square,No.4,Saranya nagar,Thirumudivakkam | chennai | 600044 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Site Visit Done | Repair |  | 9- Service Validated | 2023-09-19 21:26 |  |  | 18 | INR | 18 | ENM POWER PRODUCTS
WO-11034815 | 102805953 | 2023-07-27 10:57 | 2023-07-26 |  | 2023-07-26 11:59 | SRV6KL-IN | SRV6KL-IN | SRV6KL-IN | 9S2310A07919 | DOP: 10/05/2023 P: UPS installation S: Installation Mail from Indukala Ramu | 2023-07-26 | 2023-09-02 15:30 | No | Commercial Action - Sales | Government Medical College | East Yakkara Kunnathurmedu Post Office null | Palakkad | 678013 | Kerala | India FS South2 HBN CSP SouthernAssociates Thrissur | Shuhaib P H SouthernAssociates Thrissur | SOUTHERN ASSOCIATES | Ups installation and battery configuration done. | Commissioning & Installation | Start-up | 10- Closed | 2023-09-18 14:44 |  |  | 72 | INR | 72 | ENM SECURE POWER
WO-11280092 | 104084203 | 2023-09-19 11:36 | 2023-09-19 |  | 2023-09-19 11:12 | Masterpact NW | GCR_NW_CB | GCR_NW_CB | 10231810411 | Urgent Complaint Registration -EAP As Per The SO number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Electro Allied Products "SUALATI, P.O.: DHULAGORI, SANKRAIL, HOWRAH , Pin : 711302 , West Bengal" Contact Person Details:- Amitava Singha Roy 6291879250 Product and Issue:- NW32H13PEDO6.0A Outoing Terminals when being meggered showing as zero ( Showign as shorted) | 2023-09-19 | 2023-09-23 14:04 | No | Warranty | Electro Allied Products | Regd. Office & Works:- VILL: SULATI, P.O.: DHULAGORI, SANKRAIL, HOWRAH, PIN ? 711302 Sales Office:- 14, Gulmohr Building, 6/C, Middleton Street, Kolkata ? 700 071 | Kolkata | 700104 | West Bengal | India FS ED&I CSP East Team SREYAM SERVICES BHATPARA | AMIT BHATTACHARYA_SREYAM SERVICES BHATPARA | Sreyam Services(8513) | AFTER SITE VISIT FOUND DEFFECTIVE MICROLOGIC REPLACED BY NEW ONE AND DEFFECTIVE MATERIAL IS COLLECTED. | Repair |  | 8- Service Completed | 2023-09-25 08:10 |  |  | 25 | INR | 25 | ENM POWER PRODUCTS
WO-11280352 | 104095914 | 2023-09-19 13:33 | 2023-09-19 |  | 2023-09-19 12:54 | Compact NS > 630A | Compact NS > 630A-LV equipment - LV switch - disconnector |  | PP212641211 | RE: complaint number required Yotta Data Center Plot no. : 7 Tusiana Village, Knowledge Park V,Greater Noida Mr. Ashutosh Pareek 9599952643 Product : GCR-NS1600NA3P Serial Number : PP212641211 Phase Missing | 2023-09-19 | 2023-09-19 13:34 | No | Warranty | Yotta Data Center | HF2M+HF6, Greater Noida West Link Rd, Tusiana Village, Knowledge Park V, | Greater Noida | 201306 | Uttar Pradesh | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mccb found working ok. Email: | Repair |  | 8- Service Completed | 2023-09-19 15:59 |  |  | 65 | INR | 65 | ENM POWER PRODUCTS
WO-11280579 | 104119453 | 2023-09-19 20:02 | 2023-09-19 |  | 2023-09-19 13:58 | LV432641 | LV432641 | LV432641 |  | Motor Mechanism is not working in Auto mode--LV432641 As Per The serial number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- SHANMUKH SAI POWER CONTROL #115, 8th Cross, Naidu Layout, Hongasandra,Devarchikkanahalli Road Bangalore 560068 Karnataka India Contact Person Details:- Mr. Shivananda B 9901370970 Product and Issue:- LV432641 TC-2023-W13-4 Motor Mechanism is not working in Auto mode | 2023-09-19 | 2023-09-20 16:54 | No | Warranty | SHANMUKH SAI POWER CONTROL | #115, 8th Cross, Naidu Layout, Hongasandra,Devarchikkanahalli Road | Bangalore | 560068 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | MANOJ GANESAN SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported the problem found mccb motor mechanism not working in auto mode due to closing and open coil failure we checked control wirering found ok so we arranged the replacement found working ok | Repair |  | 9- Service Validated | 2023-09-20 22:00 |  |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11283261 | 104114687 | 2023-09-21 10:43 | 2023-09-20 |  | 2023-09-20 09:31 | LC1DPKM7 | LC1DPKM7 | LC1DPKM7 |  | DOP: 9/8/2023 LC1DPKM7 Qty:1 P: Burnt issue SBT Textiles Pvt Ltd Chandra Kumar Bisen (9111005115) 589, URLA INDUSTRIAL AREA RAIPUR,CHHATTISGARH Chandra Kumar Bisen (9111005115) | 2023-09-20 | 2023-09-25 12:00 | No | Warranty | SBT Textiles Pvt Ltd | Plot No-539,Nr. Dainik Bhaskar Press, Urla Industrial Area, Urla, | Raipur | 492001 | chhattisgarh | India FS ED&I CSP East Team SOMDEV & COMPANY RAIPUR | SOUMYA BEHERA_SOMDEV & COMPANY RAIPUR | Somdev & Company | the contactor is burnt so we replace the same. | Repair |  | 8- Service Completed | 2023-09-25 12:00 |  |  | 12 | INR | 12 | ENM POWER PRODUCTS
WO-11283321 | 104124706 | 2023-09-20 12:39 | 2023-09-21 |  | 2023-09-20 10:18 | GCR_NSX | GCR_NSX | GCR_NSX |  | Service Engineer Support As Per The Invoice The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Bundy India Limited Building No B,300A , Plot No 165, IndoSpace Industrial Park,Oragadam Phase II,Venpakkam Village,Walajabad Taluk Kanchipuram 631604 Tamil Nadu India Contact Person Details:- Contact Person Name : KUMARAN Contact Number: 99627 24222 80561 62621 Product and Issue:- Invoice No : 9008551998 Ref No : LV429387 As per customer trip button is not working for manual trip When we fix the Shunt, release the Switch on the Breaker, the breaker will automatically trip. The Shunt release Lever is not fixing properly | 2023-09-20 | 2023-09-23 17:00 | No | Warranty | Bundy India Limited | Building No B,300A , Plot No 165, IndoSpace Industrial Park,Oragadam Phase II,Venpakkam Village,Walajabad Taluk | Kanchipuram | 631604 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Visited at site and mentioned product LV563309 DOM: 1022526 MCCB ON time tripping and shunt coil release not working customer reported to me. Today visited at site we have checked MCCB ON/OFF trip without shunt coil found ok. Now checked MCCB tripping leaser bent condition. Shunt coil not fixing properly. I have bent adjusted right position and shunt coil fixing ON/OFF trip found ok. Electrical shunt trip found ok. Shunt coil no any issue. | Repair |  | 9- Service Validated | 2023-09-23 17:26 |  |  | 51 | INR | 51 | ENM POWER PRODUCTS
WO-11283342 | 104144081 | 2023-09-21 09:20 | 2023-09-20 |  | 2023-09-20 10:30 | MS23AI22N5 | MS23AI22N5 | MS23AI22N5 |  | MS23AI22N5 - start delta starter relay problem . Purchased on august 2023 from MK electricla Ptna | 2023-09-20 | 2023-09-21 10:02 | No | Warranty | Ravi Ghameja | D 3 ,EPIP ,industrial area , hajipur | Vaishali | 844101 | Bihar | India FS ED&I CSP East Team Vidya Enterprises Lucknow | Rana Ranjan_Vidya Enterprises Lucknow | Vidya Enterprises | As per customer complaint visited the site and check the 22 kw 30 HP starter found not working. open the cover nd found rely is on trip position. check the power supply found ok. check the starter without motor connection starter is working normally. connect the motor to starter and start the starter found working ok. | Repair |  | 8- Service Completed | 2023-09-21 10:03 |  |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11285208 | 103920719 | 2023-09-21 09:22 | 2023-09-20 |  | 2023-09-20 12:48 | MS23AI23N5 | MS23AI23N5 | MS23AI23N5 |  | Purchased from Om prakash power patna nov 2022 35 Hp starter star delta relay not working inside and also issue with timerc. | 2023-09-20 | 2023-09-28 20:30 | No | Warranty | Roshan Agarwal | bakri bazar , landmark st paul school , | Begusarai | 848201 |  | India FS ED&I CSP East Team Vidya Enterprises Lucknow | Rana Ranjan_Vidya Enterprises Lucknow | Vidya Enterprises | As per customer complaint visited the site and check the star delta starter. We found timmer relay and over load relay not working. Also not change the position during normal position. Due to urjent requirements we replaced timmer and over load relay from delear stock. Know starter is working normally as per customer satisfaction. We book the part at delear address. | Repair |  | 8- Service Completed | 2023-09-28 20:30 |  |  | 160 | INR | 160 | ENM POWER PRODUCTS
WO-11285283 | 104129903 | 2023-09-21 11:00 | 2023-09-20 | NA | 2023-09-20 13:15 | METSEEM6400NGRSCL5 | METSEEM6400NGRSCL5 | METSEEM6400NGRSCL5 | 16012023 | Current Rating is not showing in the MFM installed in one of the LT Panel commissioned at our customer site - KOLKATA Dear Sir / Madam, With reference to the above subject of Quality issue noitced in one of the MFM installed in one of the panel commissioned at our customer site in KOLKATA, refer the below details of the quality issue noticed. 1. Istrument : MFM Meter 2. Quality Issue Reported : Ampere is not shoowing in the MFM Meter 2. Instrument Serial Number : 540180308758 & DOM:15012023 3. Site Engineer Contact Name : Mr.Yadav 4. Site Engineer Contact Number:8318169892 5. Site Address: M/S INNOVATIVE CONCEPTS PRIVATE LIMITED (BIGBASKET) R.S. DAG NO.907 and 908, Mouza Nalmuri KOLKATA, WEST BENGAL - 743502 Note : Refer the attached photograph of complaint received MFM Thanks and Regards Rudhramuni SARAVANA SWITCHGEARS Plot No.29, Shed No. F, 4th Cross, Bommasandra Industrial Area, KIADB, Behind ICICI Bank, Bangalore-560 099. Mobile: +91-80952 55059 Email: contractssg@yahoo.co.in | 2023-09-20 | 2023-09-21 16:00 | No | Warranty | Innovative Retails Concepts Pvt Ltd | (BIGBASKET) R.S. DAG NO.907 and 908, Mouza Nalmuri Near Aero Geo College | Kolkata | 700107 | West Bengal | India FS ED&I CSP East Team B.D Electroservices Kolkata | RAHUL RAY_B.D Electroservices Kolkata | B.D Electroservices(500017330) | According to customer, the meter ampere reading not matching. So checked the meter with cross check meter anad found that there is no reading mismatch. Photograph taken of both meter reading. No fault found at meter | Repair |  | 9- Service Validated | 2023-09-21 18:38 |  |  | 37 | INR | 37 | ENM POWER PRODUCTS
WO-11285480 | 104150673 | 2023-09-21 13:53 | 2023-09-20 |  | 2023-09-20 14:14 | LC1D18M7 | LC1D18M7 | LC1D18M7 | 1022154 | LC1D18M7 - 1022154, LC1D09M7 - 1023104 operation issue Site Address: LORD KRISHNA ELECTRICAL ROHTAK OPP LPS PLANT 2 NEAR SBI BANK ROHTAK 124001 Haryana Mr. Chaudhary 7015821113 | 2023-09-20 | 2023-09-25 18:11 | No | Warranty | LORD KRISHNA ELECTRICAL | ROHTAK OPP LPS PLANT 2 NEAR SBI BANK null | ROHTAK | 124001 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the contactor found phase missing , Hence faulty replaced. LC1D09F7 - 1 nos LC1D18F7 - 1 nos Email : kunalarora444448@gmail.com | Repair |  | 8- Service Completed | 2023-09-26 15:14 |  |  | 70 | INR | 70 | ENM POWER PRODUCTS
WO-11285501 | 104147525 | 2023-09-20 17:19 | 2023-09-21 |  | 2023-09-20 14:20 | GCR_NSX | GCR_NSX | GCR_NSX |  | DOP: 14/7/2023 LV429387 Qty:1 P: Shunt not fixing in MCCB | 2023-09-20 | 2023-09-21 17:30 | No | Warranty | Formo Plastic Controls Pvt Ltd | Plot No G 15A, SIDCO Industrial Estate Kakkalur, | Thiruvallur | 602003 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Visited Done | Repair |  | 9- Service Validated | 2023-09-21 17:54 |  |  | 40 | INR | 40 | ENM POWER PRODUCTS
WO-11285936 | 104147564 | 2023-09-20 16:24 | 2023-09-20 |  | 2023-09-20 16:10 | LRE14 | LRE14 | LRE14 | 82308 | COMPLAIN BOOKING (SHRI RAGHUVIR LRE14) Checklist for Complaint Registration 1 Name of Customer SHRI RAGHUVIR ELECTRIC 2 Site Address B/H SORATHIYAWADI CHOCK ,OPP/YADAV RESTORENT 80FT ROAD RAJKOT - 360002 Dist.-RAJKOT-360002(Gujarat) India. 3 Name of contact person at site JAYESHBHAI 4 Contact Phone / Mob. No: 9723889154 5 Defective product details LRE14 6 Nature of Defect POLE OPEN 7 Shutdown availability if applicable Yes 8 Warranty status Under Warranty 9 Commissioned / Installed date Aug-23 10 Serial No: or DOM of the product 8C2308 11 Name & phone No: of person registering the complaint RUSHI PATEL :- 93743-44414 Note : Point Nos: 1 to 9 are compulsory | 2023-09-20 | 2023-09-22 18:33 | No | Warranty | Shree Raghuvir Electricals | 80 feet Road,Opp.Yadav Restorant,Sorathiyawadi Chowk,Rajkot | Rajkot | 360001 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | RAHUL PARMAR JKS Rajkot | JKS Engineering Co. | We have visit at side & check product under warranty & new installation product check relay on/off found ok not any product side issue relay on/off working ok. | Repair |  | 9- Service Validated | 2023-09-22 18:42 |  |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11285978 | 103953157 | 2023-09-20 17:56 | 2023-09-20 |  | 2023-09-20 16:28 |  |  |  |  | RMA_103953157 RO 61370191 | 2023-09-20 | 2023-09-27 12:00 | No | Warranty | P. M. Mercantiles | Registered Office: Pandit Mansion, Shop No 8, 1st Floor Operating Office: Ground Floor, Saibal Nursing Home Building Bidhan Market Road | Siliguri | 734001 | West Bengal | India FS ED&I CSP East Team B.D Electroservices Kolkata | KOUSHIK MONDAL_B.D Electroservices Kolkata | B.D Electroservices(500017330) | =S= Free Order 226090652 has been saved | Assessment/ Inspection | Data Collection | 8- Service Completed | 2023-09-27 21:17 | =S= Free Order 226090652 has been saved |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11289248 | 104174270 | 2023-09-21 12:25 | 2023-09-21 |  | 2023-09-21 10:24 | GV2ME06 | GV2ME06 | GV2ME06 |  | Product GV2ME06 MPCB Sr No : TH 2207 DOM Feb 2022 Yes, in Warranty Not passing Current in one pole Metalink Engineers 3636, Sector 32 A Chandigarh Road Ludhiana 145526 Mr Ashwani 6284763485,9023506414 Mail Id : aakash@nmaindia.com | 2023-09-21 | 2023-09-21 13:16 | No | Warranty | Metalink Engineers | Sector 32-A ,3636 Chandigarh Road | Ludhiana | 141010 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the MPCB found Not passing Current in one pole and capacitor found derated. Hence faulty replaced, GV2ME06 - 1 Nos. MEHVBHDY331A52 - 1 Nos. email : aakash@nmaindia.com | Repair |  | 8- Service Completed | 2023-09-21 14:21 |  |  | 25 | INR | 25 | ENM POWER PRODUCTS
WO-11289255 | 104174316 | 2023-09-21 12:01 | 2023-09-21 |  | 2023-09-21 10:28 | LC1E1201M7 | LC1E1201M7 | LC1E1201M7 |  | Product : LC1E1201M7 12A Contactor Sr No.8C2305 6 Warranty YES DOM Jan 2023 Not Getting On / Coil Burnt roduct : LC1E1201M7 12A Contactor Sr No.8C2305 6 Warranty YES DOM Jan 2023 Not Getting On / Coil Burnt Bobby Verma Railway Workshop JDA Circle Near PWD Colony jodhpur 342001 Mr Bobby 8700736064 | 2023-09-21 | 2023-09-21 13:03 | No | Warranty | Bobby Verma | Railway Workshop JDA Circle Near PWD Colony | Jodhpur | 342001 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Amarjeet Singh Sharma Electric Jaipur | Sharma Electric Works | Checked the contactor found not getting on due to phase missing and mccb found not getting on/off due to mechanism issue, Hence faulty replaced. LC1E1210M7 - 1 nos LC1DWK12M7 - 2 nos LV525333 - 1 nos Email : | Repair |  | 8- Service Completed | 2023-09-21 14:11 |  |  | 338 | INR | 338 | ENM POWER PRODUCTS
WO-11290077 | 104152101 | 2023-09-21 12:27 | 2023-09-21 | It is repair and now it's working fine. | 2023-09-21 12:01 | GCR_CVS_T1_19 | GCR_CVS_T1_19 | GCR_CVS_T1_19 |  | COMPLAIN ? LV429387 - QTY - 01 (V D AUTOMATION & ENGINEERING.) Checklist for Complaint Registration 1 Name of Customer M/S V D AUTOMATION & ENGINEERING 2 Site Address Plot No. 196, kalathiya ind. estate-2 Diamond nagar, Kholwad, Kamrej, Surat, Gujarat 395006 Contact Phone / Mob. No: 7405510581 3 Name of contact person at site MR.RASIK BHAI 5 Defective product details LV429387 - QTY - 01 6 Product Make SCHNEIDER-SHUNT RELEASE 7 Nature of Defect NOT WORKING PROPERLY (TRIPPING PROBLEM) 8 Shutdown availability if applicable 9 Warranty status UNDER WARRANTY 10 Commissioned / Installed date 11 Serial No: or DOM of the product BILL NO - : 5427/22-23 DATE - 23-09-2022 12 Name & phone No: of person registering the complaint JOHNSON- 8780431402 | 2023-09-21 | 2023-09-21 11:42 | No | Warranty | M/S V D AUTOMATION & ENGINEERING | Plot No. 196, kalathiya ind. estate-2 Diamond nagar,PLOT NO. G-3/6 & G-3/7, Growone one tech pvt ltd Special Economic zone (SEZ) Sachin HOJIWALA INDUSTRIAL ESTATE, NR. BHATIA TOLL PLAZA null | Surat | 394230 | Gujarat | India FS ED&I CSP West Team VARDHAMAN ELECTROSOFT Vadodara | MAHENDRA SINGH VARDHAMAN ELECTROSOFT Vadodara | VARDHAMAN ELECTROSOFT | we visited the site and check the MCCB and found that the MCCB trip as soon as switch on . The reason for this was internal shunt coil alignment .I opened the front cover of MCCB and repair it . After that the MCCB working fine . | Repair |  | 8- Service Completed | 2023-09-22 11:48 |  |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11290105 | 104156399 | 2023-09-21 12:54 | 2023-09-21 |  | 2023-09-21 12:18 | LC1E0910M7 | LC1E0910M7 | LC1E0910M7 | 1023154 | #COMPLAIN LETTER LC1E0910M7 1023154 LC1E2510M7 1023243 pole continuity issue Site address: Ahmedabad Electric Corporation ADDRESS- 1492 MAHADEV NO KHANCHO, MAMUNAYAK, POLE,GANDHI ROAD,AHMEDABAD Gujarat - 380001, India CON NUM- +91 98248 65283 | 2023-09-21 | 2023-09-25 14:01 | No | Warranty | MCB CENTRE | 1492/2, MAHADEV'S KHANCHO, MAMUNAYAK'S POLE, Nr. MUNICIPAL HOSPITAL, GANDHI ROAD, AHMEDABAD | AHMEDABAD | 380001 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Mistri Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physically observed ok. LC1E0910M7 SR NO : 102315 102354 102343 observed as per customer contactor having problem ( 3 Nos ) so we collect the contactor for testing at our asc. | Repair |  | 9- Service Validated | 2023-09-25 14:01 | =S= Consig Fill up 226079615 |  | 10 | INR | 10 | ENM POWER PRODUCTS
WO-11290455 | 104160149 | 2023-09-21 15:14 | 2023-09-21 |  | 2023-09-21 14:31 | LV432413 | LV432413 | LV432413 | 1022171 | 400A MCCB tripping issue in Medical Equipment panel. LV432413 - 1022171 tripping issue Site Address: KIMS Hospital Begumpet 1-8-31/1 Minister Rd, Krishna Nagar, RamgopalpeT Secunderabad Hyderabad 500003 Telangana Mr. Naveen 9640003444 | 2023-09-21 | 2023-09-25 12:00 | No | Warranty | KIMS hospital | Begumpet 1-8-31/1 Minister Rd, Krishna Nagar, RamgopalpeT Secunderabad | Hyderabad | 500003 | Telangana | India FS ED&I CSP South Team Sumanth Electrical Services Hyderabad | Basanth Reddy_SUMANTH ELECTRICAL SERVICES HYDERABAD | Sumanth Electrical Services | Visited the Site and Inspected the Schneider Electric-C40736E400-03 No's. Here in our observation we found that the MCCB tripping issue. So. we have replaced with MCCB C40736E400-03 No's and we have checked the operations which found OK. Complaint is closed. | Repair |  | 9- Service Validated | 2023-09-25 12:25 |  |  | 20 | INR | 20 | ENM POWER PRODUCTS
WO-11290528 | 104160342 | 2023-09-22 10:59 | 2023-09-21 | ACB Trip In IG Fault | 2023-09-21 15:02 | GCR_MVS | GCR_MVS | GCR_MVS | 1023 | Complaint against ACB Dear Sir, Pl issue complaint no. 1. Name of Customer: Mahabal Metals Pvt.Ltd. 2. Site Address: - PLOT NO.23, 24 & 57 MIRAJ MIDC BLOCK MIRAJ, MIRAJ 416410 3. Name of contact person at site :- Mr.Sardar Mali 4. Contact Phone / Mob. No: - 9689723077 5. Defective product details:-,Ref no- MVS25N4NW6L 6. Product Make:-Schneider Electric 7. Nature of Defect: ACB triping from IG Fault Unit 8. Shutdown availability if applicable :nil 9. Serial No: or DOM of the product- 10. Dealer Name /OA no. /Invoice Details: - K 1982 11. Commissioned / Installed date:- new material 12. Name & phone No: of person registering the complaint: - Mustak Panhalkar ¦ 7720028577 Thanks & Regards, ____________________________________________________________________________ Mustak Panhalkar ¦ Mobile:- +917720028577, SHIVAM ENGINEERS ¦ Shop No.1 , Bhagwan Complex, Sr. No.580/6, Behind Shriram Foundry, MIDC Shiroli-416122, Kolhapur. Authorised Distributor : KEI, Schneider, Polycab. | 2023-09-21 | 2023-09-26 17:21 | No | Warranty | Mahabal Metals Pvt Ltd | Plot No.23,24 & 57, MIDC Miraj Block , Miraj | Sangli | 416410 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Sachin S_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the ACB Trip In IG Fault. checked on/off load trial found ok. removed old microlgic and installed new micrologic 6.0A and get ACB Trip In IG Fault. we observed Y phase CT is malfunctioning and ACB trip on unbalance current. so Problem observed in ACB . ACB Needs to be replaced. Required Material : MVS25N4NW6L - 01 nos | Repair |  | 9- Service Validated | 2023-09-26 17:27 | =S= Free Order 226082177 has been saved |  | 280 | INR | 280 | ENM POWER PRODUCTS
WO-11290625 | 104174693 | 2023-09-22 08:21 | 2023-09-22 |  | 2023-09-21 15:54 | LC1DWK12M7 | LC1DWK12M7 | LC1DWK12M7 | PK23193 | Capacitor contactor issue - Reg Dear Sir, Good Morning!!! We purchased the Schneider Capacitor contactor model LC1DWK12M7, and the serial number & product image are attached to this email. During de-energization, the contactor encountered an issue that was not fully released. Since it is used for the capacitor bank switching function. Please resolve the problem as soon as possible. Thanks & Regards., Sabarirajan M ¦ Engineer ¦ Engineering department Mobile: +91 8667889927 ¦ Email: sabarirajan@cp-india.com C P Aquaculture (India) Private Limited, No 104, G.N.T Road, Sholovaram post, Nallur-Vijaynallur Village, Redhills, Chennai-600067. | 2023-09-21 | 2023-09-22 17:00 | No | Warranty | C.P Aquaculture India Pvt Ltd | # 104 G.N.T Rd Nallur Vijay Nallur Village Post Sholavaram Redhills | Tiruvallur | 600067 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Visited the site and inspect the above mentioned product customer told me the capacitor duty contactor LC1DWK12M7 is not working. Today we visit the site and check the product we give external 230V AC supply to the contactor it gets charted after that we clean the two wire and give the AC supply now it works normally and continuity between the poles and NO-NC changes are found OK. There is no product issue observed. | Repair |  | 9- Service Validated | 2023-09-22 17:25 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11290857 | 104183216 | 2023-09-21 18:04 | 2023-09-21 |  | 2023-09-21 17:45 | GCR_NW_CB | GCR_NW_CB | GCR_NW_CB | 10223440029 | Regarding 1 No ACB protection release 6.0E display reading digit cutting Schneider Problem at Amazon MDEA Project Gurgaon Site Warranty GCR_NW_CB Sl#10223440029 Issue:display reading digit cutting (display) Problem Site Address: Amazon transportation Services Pvt Ltd Indos Pace Logistic Park Tauru Project- MDEA Near Sohna, Haryana Mr Kuldeep sagar 8800369468 kulsaga@amazon.com | 2023-09-21 | 2023-09-27 15:30 | No | Warranty | Amazon Transportation Services Pvt Ltd | Indos pace logistic park,Tauru Project-MDEA Near Sohna | GURGAON | 122103 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the micrologic found that digit not proper showing, Hence faulty replaced . 47603 - 1 nos | Repair |  | 8- Service Completed | 2023-09-27 15:33 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 75 | INR | 75 | ENM POWER PRODUCTS
WO-11292169 | 104175064 | 2023-09-22 08:43 | 2023-09-21 |  | 2023-09-21 21:31 | NX063TPNDI | NX063TPNDI | NX063TPNDI | 09-22 E 045 | COMPLAINT BOOK FOR -NX063TPNDI-SRF LTD. NX063TPNDI - 09-22 E 045 pole continuity issue Site Address: SRF LIMITED PLOT NO. D-2/1, GIDC, PHASE II, PCPIR, VILLAGE- DAHEJ, TAL: VAGRA, DAHEJ.PIN- 392130. DIST: BHARUCH. STATE: GUJARAT. MR.ANKIT KACKER 7069050170, 8171254204. | 2023-09-21 | 2023-09-22 15:27 | No | Warranty | SRF Ltd | SRF Ltd Plot No D 2/1 Daheg Industial Area | Bharuch | 392130 | Gujarat | India FS ED&I CSP West Team Jay Services Vadodara | Ghanshyam Kachiya_Jay Services Vadodara | Jay Services | We visited at site & checked SDF Physically Found ok. checked Input & Out going Terminals cable connections Found Ok. We Test SDF ON - OFF Operation Found Working ok. We Observed - out voltage Not Available During SDF 'ON' position. Also Checked All Fused are ok. Found All pole continuity Open . SDF mechanism working but contact open-. Now We replaced form our Distributor stock. | Repair |  | 9- Service Validated | 2023-09-22 15:28 | =S= Consig Fill up 226078843 |  | 118 | INR | 118 | ENM POWER PRODUCTS
WO-11150493 | 103448032 | 2023-08-22 18:23 | 2023-08-22 |  | 2023-08-22 16:17 | TDAV1021AN009 | TDAV1021AN009 | TDAV1021AN009 | C21734001979 | P:-EVD Fault Under AMC P:C21734001979--EVD Fault S:AMC | 2023-08-22 | 2023-09-02 13:03 | No | Contract | Reliance Jio | Engima Complex, Plot no 1,E52 Housing Colony Rawalpur, Sant nagar,Tehsil & Dist. Srinagar | Srinagar | 190005 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | Site visit and checked unit found EVD faulty. Replaced the EVD then check unit, tested ok. unit working fine. | Repair |  | 10- Closed | 2023-09-04 11:11 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 320 | INR | 320 | ENM SECURE POWER
WO-11150508 |  | 2023-09-26 18:18 | 2023-09-01 |  | 2023-08-22 16:28 | PRODUCT UNIFLAIR LEONARDO DX IDAV0811 DOWNFLOW R410A DBL SKN WITHOUT HTR AND HUM | TDAVQ | TDAVQ | JK2109002425 | PM | 2023-08-22 | 2023-09-26 18:19 | No | Commercial Action - Sales | Reliance Jio Infocomm Ltd. | Aacharya Atre Pratisthan, Pargaon Road,Saswad null | PUNE | 411043 | Maharashtra | India FS West2 Cooling CSP Gale HVAC Pune | Gaurav More_Gale HVAC Pune | GALE HVAC | We have clean the airfilter, condenser coil, checked all electrical connections tighten the same, checked parameter settings of the unit, servicing done, unit working normally | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-26 18:20 |  |  | 0 | INR | 0 | ENM SECURE POWER
WO-11295037 | 104186495 | 2023-09-22 15:39 | 2023-09-22 |  | 2023-09-22 10:48 | GCR_NW_CB | GCR_NW_CB | GCR_NW_CB | 2023 | Tripping & noise problem in ACB NW40H14PEDO6.0E Dear team, Pls. log the Complaint & send Service Engg for Solution Customer : Amazon Wood Pvt. Ltd. Address :- Waka Mauja , Vill- Hafizpur , The Radour Yamuna Nagar Haryana Product Ref : ACB NW40H14PEDO6.0E Warranty : Under Warranty Problem : Tripping & noise problem Contact person Mr. Mukesh Kapor ? MB 9355223960 Regards | 2023-09-22 | 2023-09-22 15:42 | No | Warranty | Amazon Wood Pvt Ltd | Village Hafizpur Dist Yamuna nagar Haryana | Yamunanagar | 135133 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Karnail Singh Sharma Electric Chandigarh | Sharma Electric works(1003) | checked the ACB found working ok. Email: id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-22 15:48 |  |  | 105 | INR | 105 | ENM POWER PRODUCTS
WO-11295178 | 104188992 | 2023-09-22 14:08 | 2023-09-22 | Part order request validated by Mr. Pradeep Patil Sir | 2023-09-22 11:23 | LC1F1504 | LC1F1504 | LC1F1504 | PK2209200100487 | Complaint - M/s. Rewa MSW Wnergy Solutions Pvt Ltd Checklist for Complaint Registration 1 Site Name & Complete Address M/s. Rewa MSW Energy Solutions Pvt Ltd (Alptech Controls Pvt Ltd) Pahadiya Village, RauraB.O Post Office, Raipur - Karchliyan Tehsli, Rewa District, Madya Pradesh - 486114 2 Site Contact Name & Mob# Mr. Sahoo Mob No. 7978937504, 9113595682. 3 Site Contact Email Address** 4 Defective Product Model/Part No LC1F1504 5 Nature of Defect* Not working 6 Shutdown availability if applicable Yes 7 Distributor Name,Invoice # & Date Nil 8 Serial No: or DOM of the product PK2209200100487 9 Name & phone No: of person registering the complaint Aruna BR Mob: 8884559336 "Points 1,2,4,5 & (7or8) are mandatory. Point 7 not applicable for Industry Business * Kindly share defect symptoms instead of ""Not working"" ** End user will receive a survey asking feedback on service" | 2023-09-22 | 2023-09-23 17:01 | No | Warranty | Rewa MSW Energy Solution Pvt Ltd | Pahadia Village Branch Roura PO Raipur Karchurian Tehsil | Rewa | 486116 | Madhya Pradesh | India FS ED&I CSP West Team ABR Technical Service Indore | Mayank Patidar_ABR Technical Services Indore | ABR Technical Services (9574) | Reached at site and as per customer contactor not holding then we check on/off operation and found contactor not holding then we check coil resistance and found (1.347 m ohm) then we check coil voltage and found (17 VAC) as per our primary observation coil burnt due to low voltage but only for customer satisfaction we replace 1 nos. Contactor coil. Replaced form our stock and now we are closing this case. | Repair |  | 9- Service Validated | 2023-09-25 17:05 | 226061037 |  | 720 | INR | 720 | ENM POWER PRODUCTS
WO-11310217 | 104247745 | 2023-09-26 14:24 | 2023-09-26 |  | 2023-09-26 11:43 | C11E44V100B | C11E44V100B | C11E44V100B |  | Fwd: Emailing: complaint form 1 Name of CustomerB2:C12C8B2:C11A2:C14B2:C1B2:C12 IMA-PG India Private Limited 2 Site Address "Plot No 396/1 & 396/2, Sanwer Road, Village Limbodagari, Tehsil Hatod,Dist. INDORE - 453 111(M.P.) (M.P.), India " 3 Name of contact person at site Ajeet kumar 4 Contact Phone / Mob. No: 9540587450 5 Defective products details 6 Product Make Schneider 7 Nature of Defect 1) GV4AE11, 2) LV426804, 3) C11E44V100B (Undervoltage release Unit Not Working ) 8 Shutdown availability if applicable YES 9 Warranty status yes 10 Commissioned / Installed date 11 Serial No: or DOM of the product (Electrocare Invoice no SI202324/660 dated 02/05/2023) 12 Name & phone No: of person registering the complaint Ajeet kumar (9540587450) Note : Point Nos: 1 to 9 are compulsory | 2023-09-26 | 2023-09-26 10:25 | No | Warranty | IMA pg india pvt ltd | 396,taver road,village limbodha,tehsil hatod, | Indore | 453111 | Madhya Pradesh | India FS ED&I CSP West Team ABR Technical Service Indore | Lalu Sen_ABR Tecneical Services Indore | ABR Technical Services (9574) | Reached at site and checked MCCB and found as per customer its not turn ON. Then we checked and found UV installed and found its supply not proper. Then we connected proper UV Coil supply .Then turn ON MCCB but again its not turn ON. Then we checked UV Coil reset plunzer and found its Tilt. Then we try to repair and its repaired .then again turn on MCCB and found its working OK. we checked ON/OFF Trip operation ok and we are close this case. | Repair |  | 9- Service Validated | 2023-09-27 10:31 | VIP FSR= No 1. Preferred VIP FSR not available in that Particular Region. |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11310316 | 104249085 | 2023-09-26 14:16 | 2023-09-26 | NA | 2023-09-26 12:14 | PM5000 series-PM5560-Relay, Control & Measurement - measuring, monitoring device | PM5000 series-PM5560-Relay, Control & Measurement - measuring, monitoring device |  |  | Warning: Email body is too large and was truncated at 32 000 characters. Information may have been lost. P margin-top:0;margin-bottom:0; Dear Team, Please find trail mail Rejection from plant. Po no. 25262/SD/0041 Invoice No : AA3330113439 Type No : PM5560 Problem : Meter getting ON , but meter display showing blank ( blank white screen ).Internal fault. S/N= 600224929. Qty : 1 Nos Kindly arrange replacement & Service engineer below mention address: Site Address- M/s. Marine Electricals (I) Pvt Ltd. PLOT NO. N-51,52,59 & 60, PHASE IV, VERNA INDUSTRIAL ESTATE, VERNA, SALCETE, GOA - 403722. Contact : Mr. Azad Sharma 9170964617 | 2023-09-26 | 2023-09-27 12:53 | No | Warranty | Marine Electricals Goa-2 | MARINE ELECTRICALS (INDIA) PVT. LTD. PLOT NO.51,52,59 & 60, PHASE IV, VERNA INDUSTRIAL ESTATE, SALCETE, GOA ? 403 722. | Goa | 403722 | Goa | India FS ED&I CSP West Team East India Power Engineers Mumbai | Abhishek Parab_East India Power engineers Mumbai | East India Power Engineers (5043) | Visited the site & inspected the PM5560 meter and found that the display getting OM but the digit not showing the display showing balance. | Repair |  | 8- Service Completed | 2023-09-28 13:28 | =S= Consig Fill up 226090161 |  | 36 | INR | 36 | ENM POWER PRODUCTS
WO-11310342 | 104269903 | 2023-09-26 16:15 | 2023-09-26 |  | 2023-09-26 12:16 | LC1D32M7 | LC1D32M7 | LC1D32M7 | 8B22121 | plunger stuck having display issue Dear sir, Model - LC1D32M7 Serial no - 8B22121 Problem - Plunger stuck so plzz dispute the service engineer to check the contactor and resolve the issue as soon as possible customer Name - energy industries contact person - Santosh khare ji contact no - 9412193718 Address - NH 730C. Shahpur Nvidia . Karta Shahjahanpur 242301 | 2023-09-26 | 2023-09-26 16:16 | No | Warranty | Energy Industries | NH 730C. Shahpur Nvidia . Karta | Shahjahanpur | 242301 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Abhishek Patel Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found contactor is ok , contactor working fine | Repair |  | 8- Service Completed | 2023-09-26 16:19 |  |  | 215 | INR | 215 | ENM POWER PRODUCTS
WO-11310934 | 104277524 | 2023-09-26 17:01 | 2023-09-26 |  | 2023-09-26 15:43 | LV563316 | LV563316 | LV563316 | 102212 5 | Fwd: Case : 104155180 dt. 21.9.23 Dear Sir, Bharat City Indraprastha yojana Tela mod, loni Ghaziabad Mr Ankit 9643895376 Product : LV563316 Serial Number : 102212 5 Pole open issue -- *WITH REGARDS-* Sarabjit Singh | 2023-09-26 | 2023-09-29 17:07 | No | Warranty | Bharat City Indraprastha yojana | Tela mod, loni | Ghaziabad | 201001 | Uttar Pradesh | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mccb found phase missing, Hence faulty replaced LV563316 - 1 nos Email : id not provided by customer . | Repair |  | 8- Service Completed | 2023-09-29 17:07 |  |  | 52 | INR | 52 | ENM POWER PRODUCTS
WO-11311204 | 104281588 | 2023-09-27 10:47 | 2023-09-26 |  | 2023-09-26 17:51 | LC1D50 | LC1D50 | LC1D50 |  | Fwd: Case : 104209513 dt. 22.9.23 Dear Sir, Resident C348, DSIDC Industrial Area, Complex, Delhi, 1 MD Ajmer 9354228061 Product : LC1D50 Sr. No : 8B23051 Phase Missing -- *WITH REGARDS-* Sarabjit Singh | 2023-09-26 | 2023-09-27 11:04 | No | Warranty | Resident | c348, DSIDC Industrial Area, Complex | Delhi | 110040 | Delhi | India FS ED&I CSP North Team Sharma Electric Works Delhi | Pradeep Sharma_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the contactor found contact weld issue due to heavy dust inside the contactor , Hence no replacement given to customer . Email : id not provided by customer . | Repair |  | 8- Service Completed | 2023-09-27 11:09 |  |  | 20 | INR | 20 | ENM POWER PRODUCTS
WO-10741762 | 100977013 | 2023-05-25 15:28 | 2023-05-25 |  | 2023-05-25 14:49 | Active harmonic filter - 300 A 380..480 V AC - IP00 enclosure | PCSP300D5IP00 | PCSP300D5IP00 | U21812000196 | FW: Approval for WO Creation share WO under inspection category. Product :PCSP300D5IP00 SL:U21812000196 Issue : Filter trip error after replacing power board. Customer : Amazon BLR7 Address: Amazon seller services private limited, sy. No. 524/1, 526/6 of madivala village, sy. Mom 51/1, thattanhalli village kasabahobli anekal taluk Bengaluru, 562107 SELVAUMAR P 9787226421 perumase@amazon.com> RME BLR 7 | 2023-05-25 | 2023-09-27 22:41 | No | Commercial Action - Service Ops | Amazon Seller Services Private Limited | RKV Developers, Located At Sy No 524/1,526/6,Of Madivala Village Sy No 51/1 Of Thatanahalli,Village Kasaba Hobli,Anekal Taluk Thatanahalli Village Kasaba Hobli Anekal Taluk | Bangalore | 562107 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | C Gunasekaran_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | As per our site visit along with SE engineer balakumar,power board replaced and after that checked,as per team balakumar confirmation we close this WO. | Assessment/ Inspection | Data Collection | 8- Service Completed | 2023-09-27 22:45 |  |  | 45 | INR | 45 | ENM POWER PRODUCTS
WO-11312793 | 104249720 | 2023-09-27 10:52 | 2023-09-26 | BP20 Socket hardware problem | 2023-09-26 21:31 |  |  |  |  | RMA 104249720 _RO 61368591 | 2023-09-26 | 2023-09-27 16:28 | No | Warranty | Shiv Engineers | Shop No.2 Shreeyash Industrial Prem | Pune | 411019 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Swamesh S_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the BP20 Socket hardware problem. the hardware is tightness using cable fitting in terminal found ok. we observed wire holding tube loose. so we change it and then taken operation found ok. | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-27 16:34 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11313022 | 104174588 | 2023-09-27 10:55 | 2023-09-26 | BP20 Socket hardware problem. | 2023-09-26 22:31 |  |  |  |  | RMA 104174588 _RO 61372241 | 2023-09-26 | 2023-09-27 16:36 | No | Warranty | Shiv Engineers | Shop No.2 Shreeyash Industrial Prem | Pune | 411019 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Sachin Jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the BP20 Socket hardware problem. the hardware is tightness using cable fitting in terminal found ok. we observed wire for tightening condition checked there hardware got stiped. not get tight properly. so it is needs to be replaced. Required Material : BP20- 12 nos =S= Free Order 226085633 has been saved | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-27 20:55 | =S= Free Order 226085633 has been saved |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11035048 | 102808652 | 2023-07-26 16:08 | 2023-07-26 |  | 2023-07-26 12:58 | SRV6KL-IN | SRV6KL-IN | SRV6KL-IN | 9S2310A07906 | DOP: 10/05/2023 P: UPS installation S: Installation Mail from Indukala Ramu | 2023-07-26 | 2023-09-02 13:00 | No | Commercial Action - Sales | Government Medical College | East Yakkara Kunnathurmedu Post Office null | Palakkad | 678013 | Kerala | India FS South2 HBN CSP SouthernAssociates Thrissur | Shuhaib P H SouthernAssociates Thrissur | SOUTHERN ASSOCIATES | ups installation and battery configuration done. | Commissioning & Installation | Start-up | 10- Closed | 2023-09-18 14:49 |  |  | 72 | INR | 72 | ENM SECURE POWER
WO-11316260 | 104279660 | 2023-09-27 12:26 | 2023-09-27 |  | 2023-09-27 11:29 | C25N3MA220 | C25N3MA220 | C25N3MA220 |  | Dear Sir, Please issue Complaint No. M/s Piccadily Agro Industries Ltd Village- Bhadson, Umri-Indri Road Tehsil- Indri, Dist- Karnal Haryana-132117 Site Contact Number :- Mr Prince Yadav Mobile No. 7526067726 ) Product : C25N3MA220 - 1NOS Serial Number : 10-2022-W46-1-6750L3 Problem: Not Passing Current Regards Mukesh Kumar | 2023-09-27 | 2023-09-29 15:08 | No | Warranty | M/s Piccadily Agro Industries Ltd | Village- Bhadson, Umri-Indri Road Tehsil- Indri null | Karnal | 132117 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | data collected from the site. | Repair |  | 8- Service Completed | 2023-09-29 15:10 |  |  | 135 | INR | 135 | ENM POWER PRODUCTS
WO-11316466 | 104303054 | 2023-09-27 15:14 | 2023-09-27 |  | 2023-09-27 12:50 | LC1D09M7 | LC1D09M7 | LC1D09M7 |  | Fwd: Case : 104210762 dt. 22.9.23 3A Yantra Inc Plot 3 , Khasra No 56 57,Garhi, Near Vardan Hospital Ghaziabad Mr. Veenesh Choudhary 9643644131 Product : LC1D09M7- 2 nos Serial Number : 1022476L100173,1023176L102139 Coil fault / Stuck Issue | 2023-09-27 | 2023-09-27 15:15 | No | Warranty | 3A Yantra Inc | Plot 3 , Khasra No 56 57, Garhi, Near Vardan Hospital | Ghaziabad | 201003 | Uttar Pradesh | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the contactor found working ok. Email : id not provided by customer. | Repair |  | 8- Service Completed | 2023-09-27 15:40 |  |  | 52 | INR | 52 | ENM POWER PRODUCTS
WO-11316704 | 104302914 | 2023-09-27 17:43 | 2023-09-27 |  | 2023-09-27 14:28 | B2ADTLB30160KD | B2ADTLB30160KD | B2ADTLB30160KD | 2101250489221A0J0011 | FW: RE: In process rejection report of ATS?s Clamp & Cable Dear CCC, Pls create WO under Inspection and assessment. ATS Ref:- B2ADTLB30160KD SL No:- 2101250489221A0J0011 Under warranty:- Yes Problem:- Mounting clamps missing in new ATS box. Customer details:- Tricolite Electrical Industries Ltd Unit 1-Plot No 18/1A,Site 4, Sahibabad Ghaziabad UP 201010 REKHA BAGHEL Engineer QA 8595491204 qualitysbd@tricolite.com Thanks & Regards _________________________________________________________________________________________________ Nagabhushan K M | 2023-09-27 | 2023-09-27 18:06 | No | Warranty | Tricolite Electrical Industries Limited Site-IV. | Plot No- 18/1-A, Industrial Area | Sahibabad | 201010 | Uttar Pradesh | India FS ED&I CSP North Team Total Solution Services Delhi | Praveen Poswal Total Solution Services Delhi | Total Solution Services(500054203) | We Have Visit the Site and Check 05 NOs ATS ( 230 Series ) and Found that ( 01 NOS ATS Controller Sensing wire Missing 03 NOS ATS Controller Panel Clams are Missing/ Out 05 NOS ATS ( 230 Series ) | Assessment/ Inspection | Data Collection | 8- Service Completed | 2023-09-27 18:13 |  |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11317171 | 104309203 | 2023-09-29 10:02 | 2023-09-27 |  | 2023-09-27 16:57 | LC1D80AT7 | LC1D80AT7 | LC1D80AT7 |  | RE: Contactor Not working [ thread::QiVRpn2Sd0qMwWy5LQ-NKT4:: ] previous WO number : WO-11211646 We have registered the below complaint of the Schneider Contactors with you. Your engineer visited our place and rectified the contactors. He had not replaced anything, as everything was okay and there was a fitment problem. After the rectification, he showed the working of the contactors to us. That was working fine. That was actually a quality problem. And the same problem was there with every contactor in the complete lot. We have put the rectified contactor in our electrical panel, which is under testing on our premises. Now, the same contactors are malfunctioning once every day in the morning, when we start our panel first in the morning. If we dispatch the panel to the customer in Orissa, we will be in huge trouble. Kindly escalate the problem to the highest level, so that the actual problem can be addressed. Also, please arrange to replace the ?3 Pole Contractor (415V) ? LC1D80A? ? 02 nos. at the earliest. The replacement of the coil alone will not work. We want to replace the faulty contactors with the completely new sets (LC1D80A ? 2 nos.). We have been using Schneider contactors & MCBs for the last 25 years, but we got this problem after a long time. with Best Regards, Ashish Goel (Mob: +91 9927068841, 9870965814) Pacific Dynamics, Roorkee | 2023-09-27 | 2023-09-30 10:25 | No | Warranty | Pacific Dynamics | Khasra No.- 986M & 987, Salempur Rajputan Industrial Area, | Roorkee | 247667 | Uttarakhand | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | checked the contactor found working ok. Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-30 10:31 |  |  | 210 | INR | 210 | ENM POWER PRODUCTS
WO-11317195 | 104306849 | 2023-09-28 10:33 | 2023-09-27 |  | 2023-09-27 17:13 | GCR_ASCO_S7000 | GCR_ASCO_S7000 | GCR_ASCO_S7000 |  | Hi CCC, Please create WO for the complaint. ATS Ref:- H07ATBC31000K500; Pls use GCR_ASCO_S7000 if part ref not available. SL No:- 2132845WE Under warranty: yes Problem:- Not working in Auto. Customer address:- Chaudhary Charan Singh International Airport Amausi, Lucknow, Uttar Pradesh 226009 service.mak02@gmail.com Aditya singh 7007219604 Thanks & Regards _________________________________________________________________________________________________ Nagabhushan K M Senior Manager ASCO Services - INDIA ASCO Power TechnologiesSchneider Electric India Pvt Ltd M +91 9886760260E Nagabhushana.km@se.com JP Techno Park, Mezzanine Floor,Millers Tank Bund Road,Vasanth NagarBengaluru, India - 560052 Internal From: Service Mak Engineeers Inc <service.mak02@gmail.com> Sent: 26 September 2023 17:48To: Nagabhushana K M <Nagabhushana.KM@se.com>; SM APA Customercare IN <Customercare.IN@schneider-electric.com>Cc: Anil <mis@stambhindia.com>; rupali <rupali@stambhindia.com>; Bhavishya Sharma <bhavishya@mak-engineers.in>; Rajesh Khanna <rajesh@stambhindia.com>Subject: Re: Required engineer vist for ATS Commssning [External email: Use caution with links and attachments] Dear sir, ATS is not working in auto mode. Kindly resolve the issue as soon as possible. Photo attached for your reference. Thanks & Regards Aditya singh 7007219604 On Sat, 16 Sept 2023, 11:18 am Service Mak Engineeers Inc, <service.mak02@gmail.com> wrote: Dear sir, We have installed A ASSCO (ASCO7000 Series)ATS in our panel at Lucknow Airport. Kindly arrange the Service Engineer visit or arrange a video call with our service engineer mithun kumar (6394109608).kindly take it seriously because it's urgent work. Thanks Aditya singh 7007219604 | 2023-09-27 | 2023-09-28 12:24 | No | Warranty | Airport Lucknow | Chaudary Charan Singh Airport | Lucknow | 226023 | Uttar Pradesh | India FS ED&I CSP North Team Total Solution Services Delhi | Rahul Kumar Total Solution Services Delhi | Total Solution Services(500054203) | WE Have Visit the Site and Checked the 01 NOS ATS. I Found That ATS not working in auto mode some controlling issue we have done the proper connection and this time ATS working ok | Repair |  | 8- Service Completed | 2023-09-28 12:27 |  |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11317243 | 104312387 | 2023-09-28 11:02 | 2023-09-27 |  | 2023-09-27 17:39 | GCR_ASCO_S7000 | GCR_ASCO_S7000 | GCR_ASCO_S7000 | 2551710-001WE | ASCO Complaint/Delhi Dear CCC team, Please create WO for the complaint. ATS ref:- G07ATBC33000K500 SL No:- 2551710-001WE Under warranty:- Yes Problem:- NO/NC not changing as per switch requirement Customer details:- Tricolite Electrical Industries Ltd Unit 1-Plot No 18/1A,Site 4, Sahibabad Ghaziabad UP 201010 REKHA BAGHEL Engineer QA 8595491204 qualitysbd@tricolite.com Thanks & Regards _________________________________________________________________________________________________ Nagabhushan K M | 2023-09-27 | 2023-09-28 12:28 | No | Warranty | Tricolite Electrical Industries Limited Site-IV. | Plot No- 18/1-A, Industrial Area | Sahibabad | 201010 | Uttar Pradesh | India FS ED&I CSP North Team Total Solution Services Delhi | Satendra Yadav Total Solution Services Delhi | Total Solution Services(500054203) | We Have Visit Site and Check 01 Nos 7000 Series ATS and Found that The Controller of ATS is Doing Malfuction. So we check the Proper Connection of Wire between Controller and ATS Also Doing Proper Setting of Controller. This Time Controller Working ok with ATS On Load | Repair |  | 8- Service Completed | 2023-09-28 12:41 |  |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11322568 | 104338338 | 2023-09-28 17:14 | 2023-09-28 |  | 2023-09-28 16:47 | METSEEM6436HCL10RS | METSEEM6436HCL10RS | METSEEM6436HCL10RS |  | Reg:-Lock complaint against Faulty MFM meters Dear Schneider team, Please find attached photos of faulty MFM meters. Sr.no of faulty meters - 1) 540420239261 2) 540250286034 3)540250285988 Total ? 03 No?s of meters having same issues. Issues ? Meter(Easy Logic PM2200)display not showing any value not working after giving 230V Aux supply. Site Address:- Blue star Limited C/0,L & W construction Pvt.Ltd,RMZ Nexity, Survey #83/1,Hyderabad knowledge city,raidurg village Serilingampally, Md,Hyderabad Contact person:- Mr. Manoj- +91- 9205618322 Kindly arrange service person site visit urgently as its project handover stage too much critical. Please do the needful at the earliest. | 2023-09-28 | 2023-09-29 19:48 | No | Warranty | Blue star Limited | RMZ Nexity, Survey #83/1,Hyderabad knowledge city,raidurg village Serilingampally, Md | Hyderabad | 500019 | Telangana | India FS ED&I CSP South Team Master Electrical Solutions Hyderabad | VEERESH KUMAR Master Electrical Solutions SECUNDERABAD | Master Electrical Solutions | Visited the site for the inspection of Schneider electric MESTSEPM223OD-3 NO'S METSEPM113OHCLOSRD-7 NO'S In the total, Here in our observation following are noted ~Main lift panel-40 incomer- meter ampere values are not showing as any CT reference values CT need to checked ~Common area lighting panel - 40 Y phase CT reference not showing CT need to be checked ~Main ventilation panel - Tower 30 altradamus meter CT's need to be checked ~L&W RMZ Office - R&Y Phase CT's need to be checked ~Main ventilation panel -40- B Phase CT' need to be checked ~ In PHE Room incomer meter auxiliary reading at the meter is 408 VAC observed display is not working But recommended voltage from Schinder electrical 48-277v-+ 10%~ :<4VA,50/60-+5Hz. Meter will be not cover under warranty | Repair |  | 8- Service Completed | 2023-09-29 20:12 |  |  | 25 | INR | 25 | ENM POWER PRODUCTS
WO-11323232 | 104314860 | 2023-09-29 15:02 | 2023-09-28 | Contactor not operating | 2023-09-28 18:47 | SQD-LC1D65AM7 | SQD-LC1D65AM7 | SQD-LC1D65AM7 |  | Re: Subject : Quality problem in Contactor TVS 50/60Hz 400V [ thread::8Ien0VCOf0SPiOW6ZRxddT4:: ] We purchased your Part Ref. No. LC1D65AM7 on 26th September, 2023 from Param Enterprises, Pune : 411 062 having GST Registration Number : 27AWQPA26398B1ZR against Invoice No. C1519/23-24 dt. 26/09/2023. After purchasing the same, we connected to our Injection Molding Machine and within two hours of operation, its stop the functioning as per requirement and switch is not responding to on- off mode. PREMIER PLAST, Gat No. 70(1), Chikhali Sonawane Wasti Road, Jyotibanagar, Talawade, Pune : 411062. Contact No. Narayan Sawant : 898381165 Pravin Sabale : 7620227809 | 2023-09-28 | 2023-09-30 15:44 | No | Warranty | PREMIER PLAST | Gat No. 70(1), Chikhali Sonawane Wasti Road, Jyotibanagar, Talawade, null | Pune | 411062 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Swamesh S_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the Contactor not operating. contactor coil found burn due to voltage imbalanced under voltage case. customer installed UV & OV Protection relay but setting is not set properly.so we set the new setting properly. we reject the warranty of product due to voltage problem observed. | Repair |  | 8- Service Completed | 2023-09-30 15:50 |  |  | 50 | INR | 50 | ENM POWER PRODUCTS
WO-11327533 | 104360191 | 2023-09-29 17:04 | 2023-09-29 |  | 2023-09-29 15:13 | LC1D80AM7 | LC1D80AM7 | LC1D80AM7 | 8B22182 | Dear Team,Advance Panel & Switchgear Pvt. Ltd.Plot No. 30 & 31, Sector - 5, I.I.E. Ranipur, SIDCUL,Haridwar UttarakhandMr. Ashish6392578145Product : LC1D80AM7Sr : 8B22182Phase missing-- *WITH REGARDS-*Sarabjit SinghSHARMA ELECTRIC WORKS I CHANDIGARH I ADMIN. AUTH. SERVICE & SPARESDEALER : CROMPTON GREAVES & SCHNEIDER ELECTRIC INDIA*Tele FAX 0172-4629871E MAIL : complaints@sharmaelectricworks.com *Address : PLOT NO. 279, GF, INDUSTRIAL AREA,**PHASE-II, CHANDIGARH-160002 , Website : www.sharmaelectricworks.com**** Please consider the environment before printing this e-mail | 2023-09-29 | 2023-09-30 10:01 | No | Warranty | Advance Panel & Switchgear Pvt. Ltd. | Plot No. 30 & 31, Sector - 5, I.I.E. Ranipur, SIDCUL, | Haridwar | 249403 | Uttarakhand | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the contactor found "y" phase missing. Hence faulty , replaced. LC1D80AM7 - 1 Nos. email : qchrd@advancepanels.com | Repair |  | 8- Service Completed | 2023-09-30 10:03 |  |  | 210 | INR | 210 | ENM POWER PRODUCTS
WO-11035205 | 102809078 | 2023-07-26 16:09 | 2023-07-26 |  | 2023-07-26 13:49 | SRV6KL-IN | SRV6KL-IN | SRV6KL-IN | 9S2310A07954 | DOP: 10/05/2023 P: UPS installation S: Installation Mail from Indukala Ramu | 2023-07-26 | 2023-09-02 23:00 | No | Commercial Action - Sales | Government Medical College | East Yakkara Kunnathurmedu Post Office null | Palakkad | 678013 | Kerala | India FS South2 HBN CSP SouthernAssociates Thrissur | Shuhaib P H SouthernAssociates Thrissur | SOUTHERN ASSOCIATES | ups installation done. Now ups working normal on both modes | Commissioning & Installation | Start-up | 10- Closed | 2023-09-08 16:08 |  |  | 72 | INR | 72 | ENM SECURE POWER
WO-11327723 | 104368606 | 2023-09-30 10:06 | 2023-09-30 |  | 2023-09-29 17:01 | METSEPM2230D | METSEPM2230D | METSEPM2230D |  | Godrej Complaint Godrej Electricals & Electronics RMZ ONE PARAMOUNT C/O Godrej Electricals & Electronics No.110, Mount Ponamalle Road. Blue star Job site L&W Building SOLN P LTD. tmalai@godrej.com Mr. Raja Gopal 7995007913 METSEPM2230D during installation and operation the values are not showing in the meter NA YES 9008509298/Dt: 06.04.2023 Ms. Jisha Nair. Tel No- 9594940045 E-mail ID - procurement@elecare.in | 2023-09-29 | 2023-09-30 15:00 | No | Warranty | Godrej Electricals & Electronics | RMZ ONE PARAMOUNT C/O Godrej Electricals & Electronics No.110, Mount Ponamalle Road | Chennai | 600116 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Visited Done and resolved the issues. | Repair |  | 8- Service Completed | 2023-09-30 16:37 |  |  | 52 | INR | 52 | ENM POWER PRODUCTS
WO-11065207 | 102930562 | 2023-08-02 13:53 | 2023-08-02 |  | 2023-08-02 12:57 | MVS25N4NW6L | MVS25N4NW6L | MVS25N4NW6L | 1023046 | Re: Complaint ACB 2500A Model:MVS25N4NW6L Sl No 1023046 Date of purchase 23.05.2023 Problem:We have faced the problem the breaker is getting trip in 1200A set point is 0.8 time delay 2SEC I request kindly send service engineer immediately. Customer details Laurus labs Limited Contact person:Satya Kishore Contact No-9963659885 Trivikrim- 9398664070 | 2023-08-02 | 2023-09-02 16:28 | No | Warranty | Laurus Labs Private Limited | Jawaharlal Nehru Pharma City Parawada | Visakhapatnam | 561021 | Andhra Pradesh | India FS ED&I CSP South Team Voltamp Electrical Works Visakhapatnam | Chinni SaiKumar_VOLT AMP ELECTRICAL WORKS Visakhapatnam | Voltamp Electrical Works | As per previous visit we know that ACB EASY PACT MVS 2500A up ACB NUISANCE tripping so for that today we have tested with spare micro logic ETAG TRIP system release found ok since under warranty we are recommending to replace the micro logic release to resvolve the issue so we are Chang the new ACB and testing ok so we are close the issue | Repair |  | 9- Service Validated | 2023-09-02 16:34 | Hi Team, Material booked zfre Zvo : 225936313 | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 45 | INR | 45 | ENM POWER PRODUCTS
WO-10879242 | 101726603 | 2023-06-19 16:44 | 2023-06-19 |  | 2023-06-19 16:24 | GCR_MTZ2_CB | GCR_MTZ2_CB | GCR_MTZ2_CB | 10232120571 | FW: JSW services support for Micrologic and shunt@Dynam.. Top priority Kindly refer below approval share WO number under installation category. Product: MTZ208H16.0X3PED, SL:10232120571. Customer: Dynamo Controls A/C of Diginova . Contact : Sekar , 9845148235 Site Address: Address: 108,CN Dwaraka layout 80 feet main road, Bannerghatta Main Rd, Anjanapura 11th Block, Lal Bahadur Shastri Nagar, Bengaluru, Karnataka 560083 Regards, P.BALAKUMAR, Field Service Team, Schneider Electric , PH: 7428380635, Bangalore. | 2023-06-19 | 2023-09-11 16:49 | No | Commercial Action - Sales | Dynamo Controls | 108,CN Dwaraka layout 80 feet main road, Bannerghatta Main Rd, Anjanapura 11th Block, Lal Bahadur Shastri Nagar null | Bengaluru | 560083 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Santhosh DP_P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | VISITED THE SITE AND INSPECTED THE REF:MTZ208H16.OX3PED =ACB'S 1) CUSTOMER RECEIVED ONLY MICROLOGIC UNIT AND COILS , OTHER ACCESSORIES NOT AVAILABLE FOR MICROLOGIC INSTALLATION. 2) AT MICROLOGIC NEAR VT CONNECTION WHITE INSULATION PAPER IS NOT AVAILABLE 3) AT MICROLOGIC BACK COVER NOT AVAILABLE 4) AT MICROLOGIC ISOLATION MODULE NOT AVAILABLE, COMMUNICATION CABLE BETWEEN MICROLIOGIC ISOLATION MODULE AND CABLE NOT AVAILABLE. | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-11 16:50 | Hi Team, Material booked zfre Zvo : 225844328 |  | 20 | INR | 20 | ENM POWER PRODUCTS
WO-10956395 | 102256196 | 2023-07-07 15:27 | 2023-07-07 |  | 2023-07-05 15:48 | APC Easy UPS On-Line SRV 3000VA RT 230V India - No Battery | SRVPM3KRIL-IN | SRVPM3KRIL-IN | 9S2126A84100 | Approved by Swarup Das DOP: 31/5/2022 P:Smart UPS--Installation C:NA T:NA S:Installation Mail from Jay | 2023-07-05 | 2023-09-28 11:03 | No | Commercial Action - Sales | Qualcomm India Pvt. Ltd. | IDF-4th Floor , B#6 , Raheja IT Park , Hitech City Hitech city | Hyderabad | 500081 | Telangana | India FS South3 HBN CSP LaserSystemsPvtLtd Secunderabad | Vasanth kumar LaserSystemsPvtLtd Secunderabad | LASER SYSTEMS LIMITED. - SECUNDERABAD - HYDERABAD | installation completed. UPS working fine. | Commissioning & Installation | Start-up | 8- Service Completed | 2023-09-28 11:03 | installation completed. UPS working fine. |  | 12 | INR | 12 | ENM SECURE POWER
WO-11033577 |  | 2023-08-09 10:35 | 2023-09-29 |  | 2023-07-26 08:42 | Unisplit,R407,14.5 kW,25UCA0481, ,Indoor (with PCO1 controller + RS485 CARD) | UCA0481CWCAN2 | UCA0481CWCAN2 | ZK1434009974 | pm | 2023-07-26 | 2023-09-22 14:51 | No | Commercial Action - Service Ops | Idea Cellular Limited | VKEI Industrial Area Badharna Delhi-Jaipur Higway | Jaipur | 302013 | Rajasthan | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | ANKIT A Freezeotech Airconditioning & Refrigeration GZB | Freezeotech Airconditioning & Refrigeration Corporation | We visited the site and do the wet PM of Unit , check gas pressure , clean ODU and IDU coils and tighten loose points , check unit operation its working ok | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-22 14:54 |  |  | 45 | INR | 45 | ENM SECURE POWER
WO-10956399 | 102256353 | 2023-07-07 15:35 | 2023-07-07 |  | 2023-07-05 15:48 | APC Easy UPS On-Line SRV 3000VA RT 230V India - No Battery | SRVPM3KRIL-IN | SRVPM3KRIL-IN | 9S2126A84084 | Approved by Swarup Das DOP: 31/5/2022 P:Smart UPS--Installation C:NA T:NA S:Installation Mail from Jay | 2023-07-05 | 2023-09-28 11:24 | No | Commercial Action - Sales | Qualcomm India Pvt. Ltd. | IDF-4th Floor , B#6 , Raheja IT Park , Hitech City Hitech city | Hyderabad | 500081 | Telangana | India FS South3 HBN CSP LaserSystemsPvtLtd Secunderabad | SATHISH KUMAR LaserSystemsPvtLtd Secunderabad | LASER SYSTEMS LIMITED. - SECUNDERABAD - HYDERABAD | installation done. UPS working fine. | Commissioning & Installation | Start-up | 8- Service Completed | 2023-09-28 11:24 | installation done. UPS working fine. |  | 12 | INR | 12 | ENM SECURE POWER
WO-11013801 | 102564609 | 2023-07-21 12:20 | 2023-07-20 |  | 2023-07-20 10:58 | LD2000 | LD2000 | LD2000 | 83222302500677 | Approved by Swarup Das DOP:31/03/2023 P commissioning C NA T NA S commissioning | 2023-07-20 | 2023-09-22 14:53 | No | Commercial Action - Sales | District Deputy Director | Anaimalai Tiger Reserve NO- 365/1 Meenkarai Road Pollachi null | COIMBATORE | 642001 | Tamil Nadu | India FS South2 HBN CSP GRControlSystems Coimbatore | Edison V GRControlSystems Coimbatore | GR Control Systems-Coimbatore | Installation done Unit & Battery working fine call closed | Commissioning & Installation | Start-up | 10- Closed | 2023-09-22 14:56 |  |  | 48 | INR | 48 | ENM SECURE POWER
WO-11158220 | 103513123 | 2023-08-24 12:00 | 2023-08-24 |  | 2023-08-24 11:30 | APC Symmetra LX 16kVA N+1 Ext. Run Tower Frame, 220/230/240V or 380/400/415V | SYAF16KXR9I | SYAF16KXR9I | QD0826360020 | FW: IM02975886 UP-NOD-05 UPS INYELLIGENCE MODULE AND POWER MODULE ISSUE Site code: IM02975886 UP-NOD-05 UPS INYELLIGENCE MODULE AND POWER MODULE ISSUE Serial# QD0826360020 P: UPS intelligence module and power module issue. S: AMC | 2023-08-24 | 2023-09-01 15:31 | No | Contract | Central Board of Excise & Customs-CBEC | Noida Complex Division I E-5 Sector 1 | Noida | 201301 | Uttar Pradesh | India FS North1 HBN CSP Martech Systems & Services Noida | Uttam Yadav_Martech Systems & Services Noida | Martech Systems & Services-Noida | SYBT5-IN/SYPM4KIQ 5D2306T66799 / AQ1649210336 Part replaced at site so call closed | Repair |  | 10- Closed | 2023-09-01 17:09 |  |  | 22 | INR | 22 | ENM SECURE POWER
WO-11158474 | 103515318 | 2023-08-24 17:28 | 2023-08-24 |  | 2023-08-24 13:16 | APC Symmetra LX 16kVA N+1 Tower Frame, 220/230/240V or 380/400/415V | SYAF16KI | SYAF16KI | QD0738280248 | FW: IM02976545 PB-LUH-05 UPS BATTERY MODULE ISSUE Site code: IM02976545 PB-LUH-05 UPS BATTERY MODULE ISSUE Serial# QD0738280248 P: UPS battery module issue. S: AMC | 2023-08-24 | 2023-09-01 17:30 | No | Contract | Central Board of Excise & Customs-CBEC | Fortune Plaza 2nd floor NH-1,OPP. Hero Cycle Near Monga Tyres Geaspur Chock G.T. Road | Ludhiana | 141003 | Punjab | India FS North2 HBN CSP Essar Engineers Chandigarh | Karan Singh Essar Engineers Chandigarh | Essar Engineers | Checked the UPS and found SYBT5-IN 3 no. is giving alarm of faulty battery module sr. no. 5D2116T64097 , 5D2116T66976 , 5D1912T60206. Calibrated the UPS, its working okay | Repair |  | 10- Closed | 2023-09-01 23:12 |  |  | 110 | INR | 110 | ENM SECURE POWER
WO-11126203 | 103312333 | 2023-08-16 19:45 | 2023-08-16 |  | 2023-08-16 16:11 | GV2ME10 | GV2ME10 | GV2ME10 | 9008641107 | AUX CONTACTOR, MPCB NOT WORKING Dear Team, Please log the complaint attached herewith and arrange to re-solve the same on priority. System Invoice No -9008641107, 2)9008622418, 3)9008641427 4) 9008665572 POWERICA LTD (DTA UNIT) NH 4, 31ST KM TUMKUR ROAD NELAMANGALA BANGALORE 562123 MR LOKESH 7795064075 1)CA2KN22M7 =02 (SYSTEM INVOICE NO 9008641427) 2)GV2ME10=01 (SYSTEM INVOICE NO 9008641107 ) 3)GVAD1010 =01 (SYSTEM INVOICE NO 9008622418 ) 04) CA2KN22F7 =06 (SYSTEM INVOICE NO 9008665572) AUX CONTACTOR , ADD ON BLOCK ,MPCB 1)CA2KN22M7 & CA2KN22F7 SUPPLY NOT COMING, 2) GV2ME10 MOUNTING CLAMP NOT PROPER,3 GVAD1010 NOT WORKING SATYAM ENTERPRISES INVOICE NO 1)23240009 2) 232400080 3) 232400113 4)23240009 AMIT RAY Thanks & Regards, ____________________________________________________________________________ AMIT RAY ¦amitray@satyampune.com ¦ www.satyampune.com ¦ Satyam Enterprises Pune Pvt Ltd ¦ 09824564858 ¦ Address: Shop No.19 and 20, Center Point, N.H.No.8, New Mahavir Nagar, Char Rasta, Vapi, Valsad, Gujarat ? 396 195. | 2023-08-16 | 2023-09-08 17:48 | No | Warranty | Powerica Limited DTA Unit | NH-4, 31st K.M., Banglore-Tumkur, Village Bommanahalli, Taluka Nelamangala, | Bangalore | 562123 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Santhosh DP_P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | Inspected and found 1)Ref:no:CA2KN22F7 S/N:8B23041 = 6 No'S contactor NO/NC not working problem, screw threading issue. 2)Ref: CA2KN22M7 S/N:RB2306 = 02 No'S contactor ON/OFF issue, screw threading issue. 3)Ref no: 6U2ME10 S/N:TH2318 = 01 No MPCB ON/OFF not working issue. 4)Ref:GVAD1010 S/N:PK22282 = 01 No NO/NC auxiliary contact NO/NC not working issue. Hence we will give the above mentioned contactor and auxiliary contactor warrany replacement ASAP. | Repair |  | 9- Service Validated | 2023-09-08 17:50 |  |  | 37 | INR | 37 | ENM POWER PRODUCTS
WO-11162237 | 103544916 | 2023-08-25 11:28 | 2023-08-25 |  | 2023-08-25 10:41 | APC SYMMETRA RM 6KVA N+1 FRAME 220-240V EXCLUDING RAIL KIT | SYHF6KI-D | SYHF6KI-D | JD0831011157 | FW: IM02977360 RJ-AJM-01 UPS NOT WORKING Site code: IM02977360 RJ-AJM-01 UPS NOT WORKING Serial# JD0831011157 P: UPS is not working S: AMC | 2023-08-25 | 2023-09-01 14:07 | No | Contract | Central Board of Excise & Customs-CBEC | C R Building Jaipur Road | Ajmer | 144001 | Rajasthan | India FS North1 HBN CSP Legacy Systems Jaipur | Kuldeep Kumawat Legacy Systems Jaipur | Legacy Systems | SURTD3000UXIQ EQ1252003359 RBC44-IN-B22305010711 unit and battery replaced | Repair |  | 10- Closed | 2023-09-01 14:10 |  |  | 140 | INR | 140 | ENM SECURE POWER
WO-11134246 | 103342686 | 2023-08-18 15:08 | 2023-08-18 |  | 2023-08-18 09:55 | GCR_NSX100_630 | GCR_NSX100_630 | GCR_NSX100_630 | TC-2023-W13-4 | Faulty Motor mechanism of MCCB Dear sir, Kindly arrange to rectify/ replace the faulty MCCB motor mechanism purchased recently. LV432641, TC-2023-W13-4 Thanks and Regards, S.B. Mutha Utsav Electrical Pvt. Ltd. H-2/187, MGC, Sangaria Industrial Area, Jodhpur 342013 Mobile No. : 7976123809 utsavpower555@gmail.com www.utsavpower.com | 2023-08-18 | 2023-09-06 12:16 | No | Warranty | Utsav Electrical Pvt. Ltd. | H 2/187 mini growth center, Sangaria, phase first,salawas road, near railway crossing, Phase 1st, Sangriya, Jodhpur, Rajasthan null | Jodhpur | 342013 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Amarjeet Singh Sharma Electric Jaipur | Sharma Electric Works | Checked the mt found not getting charging, Hence faulty replaced. LV432641 - 1 nos Email :id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-06 12:18 |  |  | 338 | INR | 338 | ENM POWER PRODUCTS
WO-11162470 | 103545451 | 2023-08-25 11:54 | 2023-08-25 |  | 2023-08-25 11:13 | APC SYMMETRA RM 6KVA N+1 FRAME 220-240V EXCLUDING RAIL KIT | SYHF6KI-D | SYHF6KI-D | JD0831011100 | FW: TN/ERO/03 UPS NOT WORKING Site code: TN/ERO/03 UPS NOT WORKING Serial# JD0831011100 P: UPS is not working S: AMC | 2023-08-25 | 2023-09-01 13:01 | No | Contract | Central Board of Excise & Customs-CBEC | Office of the superintendent of CGST & Central Excise Dharapuram I & II Ranges , | Dharapuram | 638656 | Tamil Nadu | India FS South2 HBN CSP GRControlSystems Coimbatore | Mani kandan GRControlSystems Coimbatore | GR Control Systems-Coimbatore | Battery Module replacement done unit working fine call closed. STBT2 - 5D2233T07907, 5D2317T34630 | Repair |  | 10- Closed | 2023-09-01 13:09 |  |  | 92 | INR | 92 | ENM SECURE POWER
WO-11162784 | 103544079 | 2023-08-28 13:08 | 2023-08-25 |  | 2023-08-25 13:13 | Rack PDU 2G Metered ZeroU 11kW 230V (36) C13 & (6) C19 | AP8881 | AP8881 | 0A2313G01230 | Faulty PDU P:aulty PDU details S:Warranty | 2023-08-25 | 2023-09-01 13:54 | No | Warranty | Bharti Airtel | Vki msc F-216 , road no. 10 , VKI Industrial area | Jaipur | 302012 | Rajasthan | India FS North1 HBN CSP Legacy Systems Jaipur | Kuldeep Kumawat Legacy Systems Jaipur | Legacy Systems | customer site belong to jodhpur ,defective part in jodhpur office so we re log this case , | Repair |  | 10- Closed | 2023-09-01 13:57 |  |  | 20 | INR | 20 | ENM SECURE POWER
WO-11145406 | 103409239 | 2023-08-22 16:45 | 2023-08-21 |  | 2023-08-21 13:45 | EasyPact MVS-ETA6G-LV equipment - LV Trip Unit | EasyPact MVS-LV equipment - LV Trip Unit |  | 2103142665579 | FW: Regarding MCC and HT Breaker problem, JayKay Cem (Central), Hamirpur (U.P),, Case: 103129585,, Case: 103213461,, Case: 103396637,, Case: 103403299, [ thread::mKhXWU3of_ufMaVR_6HjGD4:: ] 3. CCR MCC Board 1 ? ETA6G- 2103142665579 [Isolator (Door Enclosure Handle) was not working of Feeder No. 8F1, 8R1, 9F4, 9R3, 11F4 & 11R3.] Neeraj Bhatt M- 9151009212 JK Cement Hamirpur | 2023-08-21 | 2023-09-02 17:34 | No | Commercial Action - Service Ops | JK Cement Ltd | A UNIT OF JAYKAYCEM CentralLimited Village Ingohta Tehsil . | Hamirpur | 210341 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Abhishek Patel Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found rotary handle is free so we replaced working fine . | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-02 17:38 |  |  | 174 | INR | 174 | ENM POWER PRODUCTS
WO-11162830 | 103549506 | 2023-08-25 15:34 | 2023-08-25 |  | 2023-08-25 13:34 | APC SYMMETRA RM 6KVA N+1 FRAME 220-240V EXCLUDING RAIL KIT | SYHF6KI-D | SYHF6KI-D | JD0828023502 | FW: IM02978919 PB-KAN-03 UPS Backup Issue Site code: IM02978919 PB-KAN-03 UPS Backup Issue Serial# JD0828023502 P: UPS is not giving backup S: AMC | 2023-08-25 | 2023-09-08 15:53 | No | Contract | Central Board of Excise & Customs-CBEC | CGST Division Khanna, SCO.74-77, 2nd Floor, Khanna city Centre, GT road Khanna, Punjab -141401 | Khanna | 141401 | Punjab | India FS North2 HBN CSP Essar Engineers Chandigarh | Karan Singh Essar Engineers Chandigarh | Essar Engineers | Checked the UPS and found SYBT2 , 5D2234T1357 , 5D2234T21377 is defective . Replaced 2 no. battery module and found SYRIM3Q , JQ0828004198 and SYMIM3Q ,JQ0844007775 is defective .Replaced the defective SYRIM3Q , and SYMIM3 with good one now UPS tested on load its working normal . | Repair |  | 10- Closed | 2023-09-08 15:58 |  |  | 120 | INR | 120 | ENM SECURE POWER
WO-11145417 | 103409718 | 2023-08-22 16:46 | 2023-08-21 |  | 2023-08-21 13:49 | EasyPact MVS-ETA6G-LV equipment - LV Trip Unit | EasyPact MVS-LV equipment - LV Trip Unit |  | 2086013165579 | FW: Regarding MCC and HT Breaker problem, JayKay Cem (Central), Hamirpur (U.P),, Case: 103129585,, Case: 103213461,, Case: 103396637,, Case: 103403299, [ thread::mKhXWU3of_ufMaVR_6HjGD4:: ] [Isolator (Door Enclosure Handle) was not working of Feeder No. 2R2.] 2086013165579 Neeraj Bhatt M- 9151009212 JK Cement Hamirpur | 2023-08-21 | 2023-09-02 17:38 | No | Commercial Action - Service Ops | JK Cement Ltd | A UNIT OF JAYKAYCEM CentralLimited Village Ingohta Tehsil . | Hamirpur | 210341 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Abhishek Patel Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found rotary handle is free so we replaced. | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-02 17:41 |  |  | 180 | INR | 180 | ENM POWER PRODUCTS
WO-11145423 | 103409862 | 2023-08-22 16:48 | 2023-08-21 |  | 2023-08-21 13:55 | EasyPact MVS-ETA6G-LV equipment - LV Trip Unit | EasyPact MVS-LV equipment - LV Trip Unit |  | 1304036765579 | FW: Regarding MCC and HT Breaker problem, JayKay Cem (Central), Hamirpur (U.P),, Case: 103129585,, Case: 103213461,, Case: 103396637,, Case: 103403299, [ thread::mKhXWU3of_ufMaVR_6HjGD4:: ] P:[Isolator (Door Enclosure Handle) was not working of Feeder No. 2F4 & 3F4.] 1304036765579 Neeraj Bhatt M- 9151009212 JK Hamirpur | 2023-08-21 | 2023-09-02 17:43 | No | Commercial Action - Service Ops | JK Cement Ltd | A UNIT OF JAYKAYCEM CentralLimited Village Ingohta Tehsil . | Hamirpur | 210341 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Abhishek Patel Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found rotary handle is free so we replaced. | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-02 17:44 |  |  | 180 | INR | 180 | ENM POWER PRODUCTS
WO-11145511 | 103410287 | 2023-08-22 16:49 | 2023-08-21 |  | 2023-08-21 14:20 | EasyPact MVS-ETA6G-LV equipment - LV Trip Unit | EasyPact MVS-LV equipment - LV Trip Unit |  | 2143030365579 | FW: Regarding MCC and HT Breaker problem, JayKay Cem (Central), Hamirpur (U.P),, Case: 103129585,, Case: 103213461,, Case: 103396637,, Case: 103403299, [ thread::mKhXWU3of_ufMaVR_6HjGD4:: ] 2143030365579 [isolator (Door Enclosure Handle) was not working of Feeder No. 5F2.] 2143030365579 Neeraj Bhatt M- 9151009212 JK Hamirpur | 2023-08-21 | 2023-09-02 17:41 | No | Commercial Action - Service Ops | JK Cement Ltd | A UNIT OF JAYKAYCEM CentralLimited Village Ingohta Tehsil . | Hamirpur | 210341 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Abhishek Patel Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found rotary handle is free so we replaced. | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-02 17:42 |  |  | 180 | INR | 180 | ENM POWER PRODUCTS
WO-11163334 | 103556424 | 2023-08-25 17:56 | 2023-08-25 |  | 2023-08-25 17:40 | APC SMART-UPS RC 1000VA 230V INDIA Harsh Environment | SRC1KI-IN | SRC1KI-IN | 9S1911A12316 | RE: APC UPS suzuki motors9S1911A12316 AMC | 2023-08-25 | 2023-09-03 01:30 | No | Contract | Suzuki Motors Gujarat Ltd. | Block No. 334 and 335, Hansalpur, Near Village Becharaji, Mandal, Hansalpur, 382130 | Ahmedabad | 382130 | Gujarat | India FS West2 HBN CSP_Safal Solutions Mehsana | Falgun Parmar Safal Solutions Mehsana | Safal Solutions | ups has been replaced and after that ups is working ok. new ups: 9S2319A05164 OLD UPS:9S1911A12316 | Repair |  | 10- Closed | 2023-09-02 17:04 |  |  | 110 | INR | 110 | ENM SECURE POWER
WO-11158835 | 103438613 | 2023-08-25 10:19 | 2023-08-24 |  | 2023-08-24 15:37 | LC1K0610M7 | LC1K0610M7 | LC1K0610M7 |  | Defective Item - Schneider Dear Team, Following materials are not working in our office - LC1K0610M7 - 4 PC LR2K0316 - 1 PC 63 AMPS 4P MCB - 1PC 6 AMPS SP MCB - 1PC 10 AMPS 3P MCB - 1PC LRD 22 - 1PC Kindly send your person to look into the same and replace at the earliest. -- photo Nand Kumar Kothari Proprietor, N.K.Trading Company 9830201227 ¦ nktradingkol@gmail.com 7, Pollock Street. Ground Floor. Kolkata-700001 | 2023-08-24 | 2023-09-07 11:56 | No | Warranty | N.K.Trading Company | 7, Pollock Street Ground Floor | Kolkata | 700019 | West Bengal | India FS ED&I CSP East Team SREYAM SERVICES BHATPARA | AMIT BHATTACHARYA_SREYAM SERVICES BHATPARA | Sreyam Services(8513) | AFTER SITE VISIT FOUND MCCB CONTRACTOR AND RELAY REPLACEDBY NEW ONE AND DEFFECTIVE MATERIAL IS COLLECTED. | Repair |  | 9- Service Validated | 2023-09-07 12:15 |  |  | 15 | INR | 15 | ENM POWER PRODUCTS
WO-11164378 | 103559068 | 2023-08-26 10:58 | 2023-08-25 |  | 2023-08-25 19:14 | APC Symmetra LX 16kVA N+1 Tower Frame, 220/230/240V or 380/400/415V | SYAF16KI | SYAF16KI | QD0738280297 | Back up issue IM02978999 MH-PNQ-02 Back up issue Serial# QD0738280297 P: Back up issue S:AMC | 2023-08-25 | 2023-09-01 19:44 | No | Contract | Central Board of Excise & Customs-CBEC | B-1 F-2 Plot No-1 Yeshwant Nagar Telco Road Pimpri-Chirchwad MIDC | Pune | 411018 | Maharashtra | India FS West1 HBN CSP_United Solutions Pune | Prashant Shitole_United Solutions Pune | United Solutions | Replace all pcb. now UPS is working fine on both mode | Repair |  | 8- Service Completed | 2023-09-01 19:47 |  |  | 8 | INR | 8 | ENM SECURE POWER
WO-11038707 |  | 2023-08-07 15:08 | 2023-09-23 |  | 2023-07-27 09:03 | UnisplitR40725UCA0341 indoor 7KW (with PCO1 controller , RS 485 card) | UCA0341CWCAN3 | UCA0341CWCAN3 | C22025003478 | pm | 2023-07-27 | 2023-09-25 07:43 | No | Commercial Action - Service Ops | Ashirvad Pipe Private Limited | Aalanna Polywell India Pvt Ltd,SP-10(A), RIICO INDUSTRIAL AERA,KUSHKHERA null | BHIWADI | 301707 | Rajasthan | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | ANKIT A Freezeotech Airconditioning & Refrigeration GZB | Freezeotech Airconditioning & Refrigeration Corporation | We visited the site and do the wet PM of Unit , check gas pressure , clean ODU and IDU coils and tighten loose points , check unit operation its working ok | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-25 07:46 |  |  | 220 | INR | 220 | ENM SECURE POWER
WO-11038708 |  | 2023-08-07 15:10 | 2023-09-23 |  | 2023-07-27 09:04 | UnisplitR40725UCA0341 indoor 7KW (with PCO1 controller , RS 485 card) | UCA0341CWCAN3 | UCA0341CWCAN3 | C22025003481 | pm | 2023-07-27 | 2023-09-25 07:47 | No | Commercial Action - Service Ops | Ashirvad Pipe Private Limited | Aalanna Polywell India Pvt Ltd,SP-10(A), RIICO INDUSTRIAL AERA,KUSHKHERA null | BHIWADI | 301707 | Rajasthan | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Alauddin Chaudhary Freezeotech Airconditioning & Refrigeration GZB | Freezeotech Airconditioning & Refrigeration Corporation | We visited the site and do the wet PM of Unit , check gas pressure , clean ODU and IDU coils and tighten loose points , check unit operation its working ok | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-25 07:49 |  |  | 220 | INR | 220 | ENM SECURE POWER
WO-11173174 | 103587884 | 2023-09-01 11:25 | 2023-08-28 |  | 2023-08-28 15:40 | LC1G225KUEN | LC1G225KUEN | LC1G225KUEN |  | Complain Contactor 225Amp 3 pole 100-250v AC/DC We have purchased contactor 225 Amp 3 Pole 100-250v AC/DC ? 1Nos from Santosh Electricals Bhiwadi Rajasthan on dated 26/08/2023 bill also attached. But this is faulty and not working we have already complaint to our vendor Santosh Electrical. Kindly arrange to replace it on urgent basis our machine is break down. So please take necessary action on top priority basis. Regard AITA Polymers Pvt Ltd Plot No 139 & 13, Sector ? 3, IMT ? Bawal 123501 Rewari ? Haryana 8607585222 | 2023-08-28 | 2023-08-31 15:29 | No | Warranty | Aita polymers pvt ltd | 139, Sector-3, Phase-1, IMT, Bawal, Sector 3, | Rewari | 123501 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the contactor found working ok. Email : id not provided by customer . | Repair |  | 9- Service Validated | 2023-09-01 16:10 |  |  | 85 | INR | 85 | ENM POWER PRODUCTS
WO-11177025 | 103608117 | 2023-08-29 13:03 | 2023-08-29 |  | 2023-08-29 10:07 | GCR_LV_APFC | GCR_LV_APFC | GCR_LV_APFC | 223891595 | Complaint_AAI_Dibrugarh GCR_LV_APFC Capacitor bank switching is not working prorperly. SO 223891595 Dibrugarh Airport, Mohanbari, Assam- 786012 Vineet Bagri, 9864095108 | 2023-08-29 | 2023-09-01 01:30 | No | Warranty | Airport Authority Of India | Civil Aerodrome, Mohanbari, | Dibrugarh | 786012 | Assam | India FS ED&I CSP East Team SHIV ELECTRICALS Guwahati | Parwez Alam SHIV ELECTRICALS GUWAHATI | SHIV ELECTRICALS | The APFC panel was checked and asked to customer give the proper load. | Repair |  | 9- Service Validated | 2023-09-01 08:20 |  |  | 460 | INR | 460 | ENM POWER PRODUCTS
WO-10958657 | 102269783 | 2023-09-08 14:32 | 2023-09-08 |  | 2023-07-05 22:49 | SURT15KUXIG-INX | SURT15KUXIG-INX | SURT15KUXIG-INX | B22112000202 | Approved by Nitin DOP: In Warranty P: PM S: PM Note: Mail from Ramendra | 2023-07-05 | 2023-09-08 14:36 | No | Commercial Action - Service Ops | Airforce Station | Maude Lines, Delhi Cantonment Palam | Delhi | 110010 | Delhi | India FS North1 HBN CSP Martech Systems & Services New Delhi | Balwant Singh_Martech Systems & Services New Delhi | Martech Systems & Services-Gurgaon | PM DONE | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-08 14:37 |  |  | 0 | INR | 0 | ENM SECURE POWER
WO-11177245 | 103594629 | 2023-08-29 11:22 | 2023-08-29 |  | 2023-08-29 10:38 | MVS10N3NW6L | MVS10N3NW6L | MVS10N3NW6L | 9008645484 | Safety Shutter not getting inserted in ACB (Within Warranty) - Need immediate deputation Dear CCC team, Please register the complaint and arrange to depute service engineer immediately (positively by 30/08/2023 morning). Matter extremely urgent. M/s Switching Circuits S-15 Kasba Industrial Estate, Phase-3, Kolkata-700107. (Landmark: Behind Ruby Hospital - Last Gate). Mr. P.K. Mandal (Mobile no. 9830055007) Hardware Issue MVS10N3NW6L Safety Shutter not getting inserted in ACB Please send soft compies along with this check list. Schneider Invoice No. 9008645484 dated 17.07.2023 Dibakar Ghosh (+919874211481); dibakar.ghosh@se.com Best regards, Dibakar Ghosh DGM-Sales National Sales International Operations Schneider Electric Mobile: +91 9874211481 Telephone: +91 33 4402 7226 Customer Care: 18001030011 / 18004194272 | 2023-08-29 | 2023-09-29 20:51 | No | Warranty | Switching Circuits | S-15, Kasba Industrial Estate, Phase -3 | Kolkata | 700107 | West Bengal | India FS ED&I CSP East Team SREYAM SERVICES BHATPARA | AMIT BHATTACHARYA_SREYAM SERVICES BHATPARA | Sreyam Services(8513) | AS PER DISCUSSION WITH BITHUN SIR, NEW MATERIAL HAVE TO ORDER IN THIS SITE, SO WE CLOSED THE COMPLAIN. | Repair |  | 8- Service Completed | 2023-09-29 20:54 | 226014934 |  | 20 | INR | 20 | ENM POWER PRODUCTS
WO-10958658 | 102269843 | 2023-09-08 14:28 | 2023-09-08 |  | 2023-07-05 22:49 | SURT15KUXIG-INX | SURT15KUXIG-INX | SURT15KUXIG-INX | B22112000200 | Approved by Nitin DOP: In Warranty P: PM S: PM Note: Mail from Ramendra | 2023-07-05 | 2023-09-08 14:31 | No | Commercial Action - Service Ops | Airforce Station | Maude Lines, Delhi Cantonment Palam | Delhi | 110010 | Delhi | India FS North1 HBN CSP Martech Systems & Services New Delhi | Balwant Singh_Martech Systems & Services New Delhi | Martech Systems & Services-Gurgaon | PM DONE | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-08 14:32 |  |  | 0 | INR | 0 | ENM SECURE POWER
WO-11178320 | 103619390 | 2023-08-29 12:29 | 2023-08-29 | NA | 2023-08-29 11:45 | LC1F150 | LC1F150 | LC1F150 | PK2252 | LC1F150 - Phase missing PK2252 LC1F150 - Phase missing PK2252 Arijit Karmakar +917595829590 karmakar.arijit1999@gmail.com Chittaranjan Locomotive Works Dankuni Electric Loco Assembly, Ancilary Unit for CLW Dankuni West Bengal 712311 | 2023-08-29 | 2023-09-01 15:30 | No | Warranty | Chittaranjan Locomotive Works | Dankuni Station Rd, Mrigala, Electric Loco Assembly, Ancillary Unit for CLW , Dankuni null | Hooghly | 712311 | West Bengal | India FS ED&I CSP East Team B.D Electroservices Kolkata | RAHUL RAY_B.D Electroservices Kolkata | B.D Electroservices(500017330) | We close this complain and we will do the physically work tomorrow. | Repair |  | 9- Service Validated | 2023-09-01 17:44 |  |  | 21 | INR | 21 | ENM POWER PRODUCTS
WO-11181330 | 103630303 | 2023-08-30 12:54 | 2023-08-30 |  | 2023-08-30 10:05 | LC1D18BD | LC1D18BD | LC1D18BD | 1022281L103611 | SCHNEDIER ITEM NOT WORKING Kindly find the below items which are not working. Kindly arrange for the same to be replaced as soon as possible. 1. LC1D18BD - 1 nos SL NO. - 1022281L103611 2. LC1D09BD - 1 nos SL NO. - 1023152L101678 3. GV2ME32 - 1 nos SL NO. - TH2243 22:08 B6 2 4. GV2ME07 - 1 nos SL NO. - TH2247 11:45 B3 7 5. GV2ME06 - 1 nos SL NO. - TH2233 14:25 B1 5 6. GV2ME08 - 1 nos SL NO. - TH2237 12:14 B4 1 7. GV2ME16 - 1 nos SL NO. - TH2235 15:44 A55 8. GZ1E32 - 1 nos 9. A9N4P63C - 1 nos 10. LC1D50AM7 - 1 nos SL NO.- 8B23045 11. LC1D25M7 - 1 nos SL NO. - 1022065 12. XCKJ10559H29LC CLAMP IS MISSING Kindly Visit the below Address for Replacement REGENCY ELECTRICALS PVT LTD NO. 125, 2ND MAIN ROAD, CHAMRAJPET, BANGALORE - 560018 Contact Person: Shubham Agrawal Mobile No: 97311 57865 Warm Regards, Shubham | 2023-08-30 | 2023-09-06 13:47 | No | Warranty | Regency Electricals Pvt Ltd | No 125 2nd main rd Chamarajpet | Bangalore | 560018 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Santhosh DP_P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | Inspected and found below mentioned, 1)Ref: LC1D18BD S/N:1022281 = 1 No, continuity issue. 2)Ref: LC1D09BD S/N:1023152 = 1 No, contactor not holding properly. 3)Ref: LC1D50AM7 S/N:8B23045 - 1 No, contactor not holding properly 4)Ref:A9N4P63C S/N:D2308 = 1 No, dolly free issue 5)Ref: GV2ME06 S/N:TH2233 = 1 No, ON/OFF button strucking issue 6)Ref: GV2ME07 S/N:TH2247 = 1 No, MPCB screw theading issue 7)Ref: GV2ME32 S/N:TH2243 = 1 No, MPCB pole continuity issue. 8)Ref: GV2ME08 S/N:TH2237 = 1 No, MPCB pole continuity issue 9)Ref: GV2ME16 S/N:TH2235 = 1 No, MPCB pole continuity issue. Hence will give some new products warranty replacement on good will basis. | Repair |  | 9- Service Validated | 2023-09-06 13:48 |  |  | 8 | INR | 8 | ENM POWER PRODUCTS
WO-11183211 | 103652246 | 2023-08-31 16:30 | 2023-09-01 |  | 2023-08-30 12:44 | GCR_NW_CB | GCR_NW_CB | GCR_NW_CB |  | Re: Issue in ACB NW40H14PED Attached invoice copy On Wed, Aug 30, 2023 at 11:07?AM vmfab panel <vmfab.hyd@gmail.com> wrote: Dear Sir/Madam, Greetings of the day from VM FAB!! We are facing issue in 4000A ACB with Cat no: NW40H14PED. Pl. depute your service engineer to below site address immediately. M/s. Amararaja infra pvt Ltd ARGC, Nunigundlapalli Banglore highway Near PES school Chittoor-517004 Andhra Pradesh Contact: V. Bhaskar rao Mobile no:9441116510 Regards, -- Ashish Gorak Factory & office address: Plot # 87,88 & 89, Phase-5, Navodaya Industrial Park, Cherlapally, Hyderabad-500051 Mobile: +91 9885844955, +91 7416633856. Website: www.vmfab.in Facebook page: www.facebook.com/vmfab | 2023-08-30 | 2023-09-01 15:45 | No | Warranty | Amararaja infra pvt Ltd | ARGC, Nunigundlapalli Banglore highway Near PES school null | Chittoor | 517004 | Andhra Pradesh | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Micrologic Wiring Issue | Repair |  | 9- Service Validated | 2023-09-01 15:59 |  |  | 160 | INR | 160 | ENM POWER PRODUCTS
WO-11183448 | 103631727 | 2023-09-02 13:59 | 2023-09-02 |  | 2023-08-30 14:43 | PCSPHMISTU855WX | PCSPHMISTU855WX | PCSPHMISTU855WX | WXS1B7972722060062 | Re: Requesting Schneider support for AHF panel commissioning MRF arakonam GCR_LV_APFC Problem : during commissioning we are facing some warning in relay setting MRF Arakonam Contact details: Balaram pradan /+91 95832 44166 Sunil / 7502775939 | 2023-08-30 | 2023-09-05 17:30 | No | Warranty | MRF Limited_Arakkonam Chennai | ICHIPUTHUR, TIRUTTANI ROAD, ARAKONAM, DIST- VELLORE, Arakonam , Tamil Nadu | Chennai | 631003 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Site Visit Done | Repair |  | 9- Service Validated | 2023-09-07 11:39 |  |  | 81 | INR | 81 | ENM POWER PRODUCTS
WO-11187617 | 103685446 | 2023-09-01 13:59 | 2023-08-31 |  | 2023-08-31 11:26 | LV563306 | LV563306 | LV563306 | TC-2023-W06-3U2 | LV563306 - Tripping Issue TC-2023-W06-3U2 LV563306 - Tripping Isssue TC-2023-W06-3U2 Mr. Rahul Garg 09050070354 Malakshmi Enterprises Address chajjpur kalan bapoli road Panipat 132103 | 2023-08-31 | 2023-09-01 14:28 | No | Warranty | Malakshmi Enterprises | chajjpur kalan bapoli road | Panipat | 132103 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the mccb found tripping issue and During visit plant is not run and load not available at site. Hence case is closed. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-01 21:02 |  |  | 165 | INR | 165 | ENM POWER PRODUCTS
WO-11188204 | 103690712 | 2023-08-31 18:21 | 2023-08-31 | NA | 2023-08-31 15:50 | GV2ME22 | GV2ME22 | GV2ME22 | 8C2213 | complaint registration form Dear Team, Please visit the site on priority basis. Image also attached for your reference. Please visit the site on priority basis. HOME CREDIT 9TH FLOOR, EMPIRE TOWER, RELIABLE TECH, DIGHA AIROLI-400708 RAJU KADAM 9833914802 GV2ME22- 1 NOS- 8C2213 MPCB PHASE NOT WORKING REQUESTED TO VISIT SIDE ON PRIORITY. INVOICE NUMBER -1481/23-24 21/06/2023 RUPESH ADAWADE -8652119756 -- Regards, Shramica Electricals, Shop No-:- 174, 1st floor, Om Arcade Building, Sec-20, Near Turbhe Station, Turbhe, Navi Mumbai-40705 Tel:- 8652119756/9082013591 Email:-shramicaelectricals@gmail.com/rupesh.adawade7@gmail.com Website:-www.shramicaelectricals.com | 2023-08-31 | 2023-09-01 13:11 | No | Warranty | Home Credit India Finance Pvt Ltd | 9th Floor, Empire Tower, Thane Belapur Road, Airoli null | Navi Mumbai | 400708 | Maharashtra | India FS ED&I CSP West Team East India Power Engineers Mumbai | Sandeep Ingavale East India Power engineers Mumbai | East India Power Engineers (5043) | Visited the site and checked the MPCB Y phase found open in MPCB close/on condition and R and B phase close found in MPCB open /off condition | Repair |  | 8- Service Completed | 2023-09-08 17:03 | =S= Consig Fill up 226011918 |  | 7 | INR | 7 | ENM POWER PRODUCTS
WO-11210675 | 103757536 | 2023-09-06 12:00 | 2023-09-04 |  | 2023-09-04 12:02 | GCR_NW_CB | GCR_NW_CB | GCR_NW_CB | 10230770179 | NW50H1 - Tripping issue 10230770179 NW50H1 - Tripping issue 10230770179 Harish Dubey 9850985429 APL Apollo Tubes Limited IRON & STEEL INDUSTRY, Village :- Rigni, Kasda Si | 2023-09-04 | 2023-09-06 12:00 | No | Warranty | APL Apollo Tubes Limited | IRON & STEEL INDUSTRY, Village :- Rigni, Kasda Simda | Raipur | 493101 | chhattisgarh | India FS ED&I CSP East Team SOMDEV & COMPANY RAIPUR | SOUMYA BEHERA_SOMDEV & COMPANY RAIPUR | Somdev & Company | AFTER VISITED THE SITE AND CHECJED THE ACB, WE FIND THAT THE TRIPPING ISSUE IS CAUSED BY EARTH FAULT RELAY WHICH IS NOT AN SCHNEDER COMPLAINT | Repair |  | 9- Service Validated | 2023-09-06 17:40 |  |  | 75 | INR | 75 | ENM POWER PRODUCTS
WO-11210953 | 103755814 | 2023-09-05 12:12 | 2023-09-04 |  | 2023-09-04 13:16 | METSEEM1220HCL1 | METSEEM1220HCL1 | METSEEM1220HCL1 | 540760008500 | RE: Schneider makes energy meter EM1000H LCD display L1 & L3 light not show refer w/o no. WM23102 Dear Team, Please confirm action. METSEEM1220HCL1 ? 2 qty Contact Person ? Mr. Neeraj Sharma (9760010550) Address - Plot No.1A, Sector-8C, Integrated Industrial Estate, Ranipur-249403, Haridwar, UK Mobile: +91 9760010550. Mail id - neeraj.sharma@cselectric.co.in Material Was billed thru Lalit Electricals Faridabad. For any confusion , call me directly. Ashish Bhatt Deputy General Manager National Sales International Operations Schneider Electric D +91-522-4006010-14 M +91- 8477022777 / 7718881447 E ashish.bhatt@se.com F +91-522 4006015 | 2023-09-04 | 2023-09-05 15:33 | No | Warranty | C&S Electric Ltd | (Bus Trunking Div.) Plot No.1A, | Haridwar | 249403 | Uttarakhand | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the meters found L1 and L3 indication not glowing, screw free problem, & display back light not glowing. Hence faulty replaced. METSEEM1220HCL1 - 5 Nos. email : neeraj.sharma@cselectric.co.in | Repair |  | 9- Service Validated | 2023-09-06 11:33 |  |  | 215 | INR | 215 | ENM POWER PRODUCTS
WO-11211186 | 103763229 | 2023-09-05 13:09 | 2023-09-04 |  | 2023-09-04 14:38 | LC1K0910M7 | LC1K0910M7 | LC1K0910M7 | 8B23202 | LC1K0910M7 - Coil Faulty 8B23202 LC1K0910M7 - Coil Faulty 8B23202 Gautam Kumar +919871513911 store@antarcticaequipment.com Antarctica Equipment pvt ltd Plot No. 352, Sector 8, Imt Manesar, Gurugram, Haryana 122051 | 2023-09-04 | 2023-09-12 12:06 | No | Warranty | Antarctica Equipment pvt ltd | Plot No. 352, Sector 8, Imt Manesar null | Gurugram | 122051 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the contactor found phase missing, Hence faulty replaced. LC1K0910M7 - 1 nos Email : id not provided by customer . | Repair |  | 9- Service Validated | 2023-09-12 12:08 |  |  | 55 | INR | 55 | ENM POWER PRODUCTS
WO-11211232 | 103760196 | 2023-09-04 16:35 | 2023-09-04 | Contactor Chattering Problem | 2023-09-04 14:56 | LC1D32M7 | LC1D32M7 | LC1D32M7 | 1023186l101191 | Contactor & Add on block not operating Pl issue complaint no. Please refer the attached photos for details. 1. Name of Customer: Virtuoso Projects & Engineers PVT. LTD. 2. Site Address: - Gat No.112, At Pimpalgaon, Post. Solu, Tal.Khed, Dist. Pune ? 412105. 3. Name of contact person at site :- Venkat Shinde 4. Contact Phone / Mob. No: - 9373287100 5. Defective product details:- LC1D32, LADN22 6. Product Make:- Schneider Electric 7. Nature of Defect: Contactor not operating, Add on block NC contact not operating 8. Shutdown availability if applicable :nil 9. Serial No: or DOM of ? 10. Dealer Name /OA no. /Invoice Details: - NIL 11. Commissioned / Installed date:- NIL 12. Name & phone No: of person registering the complaint: Mr. Venkat Shinde With Best Regards, Venkat Shinde Virtuoso Projects & Engineers Pvt. Ltd. Office: Office No.108-109,Pride Icon, Mundhwa-Kharadi Rd, Next to Columbia Asia Hospital,Kharadi,Pune,Maharashtra ? 411014. Factory: Gat No.112, At Pimpalgaon, Post. Solu, Tal.Khed, Dist. Pune ? 412105. Mob: +91-9373287100 | 2023-09-04 | 2023-09-05 11:33 | No | Warranty | Virtuoso Projects & Engineers Pvt.Ltd | Gat No.112, At Pimpalgaon,Post. Solu, Tal.Khed | Pune | 412105 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Kunal jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the Contactor Chattering Problem after 3 - 4 operation. so we open it and observed E magnet found some dust so we clean it and assemble again. and then taken on/ off operation found ok. contactor found ok. | Repair |  | 9- Service Validated | 2023-09-05 11:37 |  |  | 40 | INR | 40 | ENM POWER PRODUCTS
WO-11211356 | 103755282 | 2023-09-05 10:25 | 2023-09-04 | MCCB Pole Open | 2023-09-04 15:47 | C16F6TM160 | C16F6TM160 | C16F6TM160 |  | Fw: 15779-Cummins,Kothrud : MCCB Operational Issue Cummins MCCB Tripping C16F6TM160 | 2023-09-04 | 2023-09-09 11:20 | No | Warranty | Cummins India Limited (Cummins, Inc.) | Gandhi Bhavan Road, Dahanukar Colony,Kothrud | Pune | 411038 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Amit Patil_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the MCCB Pole Open. customer observed MCCB was tripped so they checked but MCCB not getting ON. we checked input & output voltage.R phase is not getting. MCCB Pole Open. SO MCCB Needs to be replaced. required Material : C16F6TM160- 01 nos | Repair |  | 9- Service Validated | 2023-09-14 10:47 | 226031635 |  | 40 | INR | 40 | ENM POWER PRODUCTS
WO-11211536 | 103764928 | 2023-09-05 15:29 | 2023-09-05 |  | 2023-09-04 16:26 | C25N3TM250 | C25N3TM250 | C25N3TM250 | 9008354525 | COMPLAINT Please find the below complaint. ITEM CODE : C25N3TM250 ? QTY 1NO (MCCB ONE PHASE NOT WORKING) Invoice No. 9008354525 KINDLY SEND YOUR SERVICE PERSON TO BELOW MENTIONED SITE ADDRESS. Factory address: Southern alloy foundries pvt ltd No.149,G.N.T.Road,ponniammanmedu post, Madhavaram,Chennai - 110. Contact mob: 7305074220 ( Mr.Arunkumar) Thanks & Regards Karan 9884430690 RAHUL CABLES No. 8/4a, Theradi street,(Entrance from No. 136Govindappa naicken street) Chennai - 600 079 | 2023-09-04 | 2023-09-07 19:00 | No | Warranty | Southern alloy foundries pvt ltd | No.149,G.N.T.Road,ponniammanmedu post, Madhavaram null | Chennai | 600110 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | MCCB output voltage not getting. | Repair |  | 9- Service Validated | 2023-09-08 16:30 |  |  | 25 | INR | 25 | ENM POWER PRODUCTS
WO-11215467 | 103765034 | 2023-09-05 12:41 | 2023-09-05 | NA | 2023-09-05 11:46 | LC1D09M7 | LC1D09M7 | LC1D09M7 | 9008616503 Dt.24.06.2023 | COMPLAINT--SPEEDFAM--04.09.2023 Dear Team, Good Afternoon!! Request you to register complaint and arrange service engineer ?SPEEDFAM INDIA PVT LTD "SPEEDFAM INDIA PVT LTD B/87, ADDNL. AMBERNATH MIDC, ANAND NAGAR, JAMBHIVALI, AMBERNATH-421 506. " purchase@speedfam.co.in Mr.PRADEEP MALI / Mr. SAGAR MAHAJAN -8329661981/ 8484859187 LC1D09M7 Not working 9008616503 Dt.24.06.2023 Ms. Amruta Mandave. Tel No- : 022-69691223 E-mail ID - techsupport@elecare.in Thanks & Regards, Amruta Mandave (Sr. Technical Engineer) Email ID: techsupport@elecare.in Telephone No: 022-69691223/ 9594940050 | 2023-09-05 | 2023-09-06 11:37 | No | Warranty | SPEEDFAM INDIA PVT LTD | B/87, ADDNL. AMBERNATH MIDC, ANAND NAGAR, JAMBHIVALI, AMBERNATH | Thane | 421506 | Maharashtra | India FS ED&I CSP West Team East India Power Engineers Mumbai | Akshya Vidhate_East India Power engineers Mumbai | East India Power Engineers (5043) | Visited the site & checked the coil resistance and found ok. Checked the voltage 24V DC and found ok. Checked the pole-to-pole continuity and found ok. The Contactor is working ok. Checked the module 220V AC and found not working | Repair |  | 8- Service Completed | 2023-09-08 16:44 | =S= Consig Fill up 226023546 |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11215482 | 103768334 | 2023-09-06 12:44 | 2023-09-05 |  | 2023-09-05 11:56 | LC1D65AM7 | LC1D65AM7 | LC1D65AM7 | 8B2220200102757 | Short List ( LCD65AM7) Dear Schneider Coil short has been found in the 3 contactors sent by you, please replace them. Model No - LCID65AM7 S/R NO - 8B2220200102757 MODEL NO- LC1D65AM7 S/R NO-8B2220200102766 MODEL NO - LC1D65AM7 S/R NO - 8B2149700102159 COMPANY NAME - KRISHNA ELECTRICAL WORKS ADD. - PLOT NO 196 PHASE-1 HSIIDC BARI SONIPAT HARYANA 131101 CON. PERSON - RAVI MOB: 8684892441 -- Thanks & Regards RASHU TYAGI 97282-47707 KRISHNA ELECTRICAL WORKS PLOT NO. 243, PHASE-1, HSIIDC BARHI, SONEPAT HARYANA - (131101) GST NO- 06AWMPT8496P1Z4 | 2023-09-05 | 2023-09-06 12:46 | No | Warranty | Krishna Electrical Works | 623, Phase-2 , HSIIDC, Barhi, | Sonepat | 131101 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | checked the contactor LC1D65AM7 - 3 Nos. and found that contactor coil was missing. Contactor packing box not available at site. Customer provides invoice M/S Schneider Electric India Pvt Ltd. Contactor : LC1D65AM7 Qty - 3 Nos. Invoice No. : AA3330044501 Invoice Date : 20.3.2023 O.A No. : 225362567 Receiving Date : 28.3.2023 Billing Docket No. : 9008488501 P.O Date : 20.1.2023 | Repair |  | 9- Service Validated | 2023-09-06 13:30 |  |  | 65 | INR | 65 | ENM POWER PRODUCTS
WO-11215620 | 103770093 | 2023-09-06 13:08 | 2023-09-06 |  | 2023-09-05 13:09 | LRD16L | LRD16L | LRD16L |  | LRD16L 1No Not working Dear CC Item : LRD16L - 1no Issue : Tripping issue , not working. Invoice : Delton invoice to customer enclosed. Refer to the above details please depute your service engineer to resolve the issue at below mentioned site. Contact : Mr. Rajendran :: 93846 74128 Site : Performance products and services Survey no 194 to 206, K. S. Road, Thandalancherry, Gummidipoondi, Tamil Nadu 601201 With Regards, Description: Delton New Logo 3 Kokila S ¦ Deltoncontrol & Switchgears LLP ¦ TeleFax :- 080-29743555,26753597,26756527,26756713, 26757190 ¦ Mobile: +91 9620265717 Email: projects@deltoncontrol.com¦ Address: 43-43A,1st main road, New Timberyard Layout, off Mysore road, Bangalore -560026, Landmark-Near Karnataka Bank | 2023-09-05 | 2023-09-06 18:00 | No | Warranty | Performance products and services | Survey no 194 to 206, K. S. Road, Thandalancherry null | Gummidipoondi | 601201 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Site Visit Done | Repair |  | 9- Service Validated | 2023-09-06 18:41 |  |  | 55 | INR | 55 | ENM POWER PRODUCTS
WO-11215671 | 103773363 | 2023-09-05 15:12 | 2023-09-05 |  | 2023-09-05 13:25 | GCR_NW_CB | GCR_NW_CB | GCR_NW_CB | 10221140009 | Service request. We had installed the below mentioned ACB's in the Main LT Panel of our client. Lately the client has been facing the issue with the display unit of the ACB's. ( The ACB's are LSIG with display ). The details of the ACB are provided below. a) Make: Schneider Electric,4000A, ACB, Sl. Nos: 10221140009, 10221140008,10221140010, 10221140026 b) Make: Schneider Electric,1250A,ACB. Sl. No: 10221050082, 10221050085 c) Make: Schneider Electric, 800A, ACB, Sl. No: 10221050092 d) Make: Schneider Electric, 1600A, ACB, Sl. No: 10221050091, 10221050086, 10221050089, 1022105007 Address: Sy No.207NH 4 Motebennur Village Byadgi Taluk Haveri 581198 07259016505 Mane Kancor Ingredients Private Ltd Hence, we request you to depute your service personnel to site and rectify the issue at the earliest and oblige. Thanking you, for S.V.Electricals, Sathya. mob. 07259016505. S.V.ELECTRICALS GOVT LICENCED CLASS I ELECTRICAL CONTRACTORS, CONSULTANTS AND ENGINEERS. Reg.Off. # 123, 2/3rd Main, 8th Cross I Block, RAMAKRISHNAGAR, MYSORE - 570023, KARNATAKA. MOBILE NO. 9886498506, OFFICE NO. 0821-2462010 WEBSITE:http://svelectricals.com email: svelectricals@hotmail.com svelectricals2003@yahoo.com | 2023-09-05 | 2023-09-07 16:01 | No | Warranty | Mane Kancor Ingredients Private Ltd | Sy No.207NH 4 Motebennur Village Byadgi Taluk | Haveri | 581198 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | C Gunasekaran_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported ACB, the problem reported was micrologic display not getting ON, trip unit display will ON when 40% load available or external 24vdc should be given for display On. The same explained to the customer. There is no issue with ACB. | Repair |  | 9- Service Validated | 2023-09-07 19:02 |  |  | 310 | INR | 310 | ENM POWER PRODUCTS
WO-11216017 | 103791051 | 2023-09-07 12:11 | 2023-09-05 |  | 2023-09-05 15:08 | LV510305 | LV510305 | LV510305 | 10-2021-W42-5-3403L1 | LV510305 - Not able to switch off , Stuck issue 10-2021-W42-5-3403L1 LV510305 - Not able to switch off , Stuck issue 10-2021-W42-5-3403L1 Hemant Kumar 9451801098 accounts@sparkcontrol.in Spark Control F 55, Vaisno Dwar, Near Devi Mandir, Rudrapur, Udhham singh Nagar,Uttarakhand 263153 | 2023-09-05 | 2023-09-12 16:22 | No | Warranty | Spark Control | F 55, Vaishno Dwar, Near Devi Mandir, Rudrapur null | Udham Singh Nagar | 263153 | Uttarakhand | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mccb found not able to on/ off, Hence faulty replaced . LV510305 - 1 nos Email : id not provided by customer . | Repair |  | 9- Service Validated | 2023-09-12 17:25 |  |  | 255 | INR | 255 | ENM POWER PRODUCTS
WO-11216345 | 103792420 | 2023-09-06 10:14 | 2023-09-05 | product found in transit damaged. | 2023-09-05 17:52 | LC1F2600MD | LC1F2600MD | LC1F2600MD | PK231640742 | Pl issue complaint no Pl issue complaint no. 1. Name of Customer: GE India Industrial Pvt Ltd 2. Site Address: - Plot no-78/1, Wasuli,Chakan MIDC Phase no-2 MH-410501 3. Name of contact person at site: Ms.Shubhangi Shinde 4. Contact Phone / Mob. No: -9637793760 5. Defective product details:- LC1F2600MD 6. Product Make:-Schneider Electric 7. Nature of Defect: - Contactor not operating properly 8. Shutdown availability if applicable nil 9. Serial No: or DOM of the product- PK231640742 10. Dealer Name /OA no. /Invoice Details: -NIL 11. Commissioned / Installed date: - Nil 12. Name & phone No: of person registering the complaint: Amit Patil (Mob No 8888192174) | 2023-09-05 | 2023-09-06 11:18 | No | Warranty | GE India Industrial Pvt. Ltd. | A-78/1, Chakan Industrial Area Phase-2 Vasuli | Pune | 410501 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Amit Patil_Super electricals Pune | Super Electricals Engineering Services(500017125) | checked contactor front cover left side of contactor was damaged at upper side. inner & outer packing is available on site in good condition. So this problem is not repairable. So Contactor left side cover needs to be replaced. Required Material : Contactor left side cover- 01 nos | Repair |  | 9- Service Validated | 2023-09-06 11:23 |  |  | 60 | INR | 60 | ENM POWER PRODUCTS
WO-11221359 | 103817425 | 2023-09-06 13:03 | 2023-09-06 | FRee replacement of LV525303 | 2023-09-06 12:47 | LV525303 | LV525303 | LV525303 | 10-2023-W06-4-4224L1 | LV525303 - Phase Missing 10-2023-W06-4-4224L1 LV525303 - Phase Missing 10-2023-W06-4-4224L1 Mr. DEVANGBHAI PARIKH 9327963947 Kishor Trading C Address5 Vatva GIDC, Opp. Bombay Conductor Ahmedabad 382445 | 2023-09-06 | 2023-09-08 11:02 | No | Warranty | Kishor Trading Co | 5 Vatva GIDC, Opp. Bombay Conductor | Ahmedabad | 382445 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Mohammad Aasif Anik Engineering Ahmedabad | Anik Engineering (554) | visited site and checked the product, Physically observed ok, , checked the on off operation observed ok. Checked the continuty observed B pole open, checked for any burning at the terminals observed ok, hence free replacement of the mccb recomended | Repair |  | 9- Service Validated | 2023-09-08 11:03 | =S= Consig Fill up 226035392 |  | 15 | INR | 15 | ENM POWER PRODUCTS
WO-11168584 | 103572480 | 2023-08-28 11:33 | 2023-08-26 |  | 2023-08-26 21:15 | EFC Monoblock unit 1.3TER, downflow with start run relay kit | WDF0181BN002 | WDF0181BN002 | JK1342000328 | RE: [External]TT Request_I-KA-YLPR-ILA-0001_High Temperature Issue-critical, Case: 103572044,, Case: 103572290, [ thread::t4k3zGuWf7mtBuy1u1DT1D4:: ] Under AMC P:High Temperature S:AMC | 2023-08-26 | 2023-09-05 17:46 | No | Contract | RELIANCE JIO INFOCOMM LIMITED | No.65A1/A, situated Shri Ramavijaya Building, I B Road, Yallapur null | UTTARA KANNADA | 581359 | Karnataka | India FS South3 Cooling CSP Fresco solutions Bangalore | PAVITHRAN P_Fresco solutions Bangalore | Fresco solutions | Controller replaced | Repair |  | 8- Service Completed | 2023-09-05 17:49 |  |  | 350 | INR | 350 | ENM SECURE POWER
WO-11221688 | 103813867 | 2023-09-06 16:32 | 2023-09-06 |  | 2023-09-06 14:28 | MVS25N3MW6L | MVS25N3MW6L | MVS25N3MW6L | 9008473095 | ACB COMPLAINT PL FIND ATTACHED THE COMPLINT FORM DULY FILLED WITH DETAILS REQUIRED. AS THE PLANT IS DUE FOR INAGURATION , PL ARRANGE TO DO THE NEEDFUL IMMEDIATELY WE ARE KEEPING THE CUSTOMER ALSO IN LOOP FOR BETTER CO ORDINATION ?SISECAM _FLAT Glass , Halol , Vadodoara , Gujarat Bharathkumar J (+91 7305710222) and Mr. Johnson (+91 9841518285 MVS25N3EW6L - 1NO NOT ABLE TO CLOSE EITHER MECAHANICALLY OR ELECTRICALLY SHRIKRISHNA,, CHENNAI -83 9008473095 DATED 13-03-2023 B.VENKATRAMAN 97909-83346 Thanks and Regards, B. VENKATARAMAN 97909-83346 PARTNER SHRI KRISHNA J-49, 1st Floor, Kambar Street, Thiru Nagar, Jafferkhanpet, Chennai - 600 083. PH: 044-2489 3347 Mobile & Whatsapp No: 97909 83347 GST NO: 33AATFS9211N1ZK MSME Registered; UAM No: TN020070304 | 2023-09-06 | 2023-09-07 13:17 | No | Warranty | Sisecam flat glass | Halol G.I.D.C Phase-III Panchmahal, Halol null | Halol | 389360 | Gujarat | India FS ED&I CSP West Team Jay Services Vadodara | Ghanshyam Kachiya_Jay Services Vadodara | Jay Services | We visited at site& checked that ACB charge But not close by manually & electrically. Now we open & observed that XF closing coil position out of space. We rectify & test ACB ON-OFF operation electrically & manually found working satisfactory. We also explain Micrologic ET6G Trip unit all setting & tripping indication. ACB working satisfactory. | Repair |  | 9- Service Validated | 2023-09-07 13:18 |  |  | 53 | INR | 53 | ENM POWER PRODUCTS
WO-11170816 | 103579416 | 2023-08-28 09:04 | 2023-09-02 |  | 2023-08-28 02:37 | DX Leonardo Evolution Model 0511 thru 0611 | UFLEDX0611 | UFLEDX0611 | NUCU3289 | AMC P: PAC - Not Powering On S: AMC | 2023-08-28 | 2023-09-02 19:25 | No | Contract | Delhi Transco | DGM ( IT ), 33 KV,SLDC Building,Minto Road Civic Center | Delhi | 110002 | Delhi | India FS North1 Cooling CSP Hitech solutions New Delhi | Arvind Kumar_Hitech solutions New Delhi | Hitech Solutions-New Delhi-Delhi | CHECK THE UNIT AND FOUND TRANSFORMER BURN change the transformer and unit working ok . | Repair |  | 10- Closed | 2023-09-02 19:32 |  |  | 32 | INR | 32 | ENM SECURE POWER
WO-11221969 | 103814169 | 2023-09-06 18:01 | 2023-09-06 |  | 2023-09-06 16:39 | METSEEM6400NGRSCL1 | METSEEM6400NGRSCL1 | METSEEM6400NGRSCL1 | 540180325382 | Depute Representative Dear Sir, We had Purchased Schneider make MFM meter. during Commissioning 01nos. MFM meter not working properly. So I requested to you kindly Depute your representative at site as soon as possible. we are facing issue with L-N voltage and L-L voltage. In a R phase voltage L-N voltae is ok but in in Y and B voltage in a L-N is shows 421 , And same issue in L-L showing in second row of display 242 . Meter details ,Site Detail ,and Contact Person Name is below. Meter details :- EM 6400 NG class - 1.0 , SR No :- 540180325382 Site Address :- Vodafone Idea Limited Building A , Corporate Road , Off S.G. highway Prahalad Nagar Ahmedabad - Gujarat :- 380015 Contact person :-Mr. Vivek 8866683269 , 9106632502 Regards, Aajay Kumar Mishra 9879966314 | 2023-09-06 | 2023-09-08 15:31 | No | Warranty | Vodafone Idea Limited | Vodafone House, Off S G Highway, Corporate Road,Prahladnagar null | Ahmedabad | 380051 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Mohammad Aasif Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physically observed ok. METSEEM6400NGRSCL1 DOM : 14-04-2023 observed physically ok. we observed on meta l 243.6 l2 421.7 & l3 242.8. we check the meter i/p and observed some voltage show in meter. No any meter problem obsreved. we check busbar voltage observed voltage ok. bute meter s/p side wrong connection found. we connect the wiring and observed meter working satisfactory. | Repair |  | 9- Service Validated | 2023-09-08 15:31 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11171772 | 103573188 | 2023-08-28 10:15 | 2023-08-28 |  | 2023-08-28 10:05 | SUA3000I-IN | SUA3000I-IN | SUA3000I-IN | B21632000049 | Ups not working - Bestech sanskriti Under AMC P:Ups not working s:AMC | 2023-08-28 | 2023-09-02 13:50 | No | Contract | Thyssenkrupp Elevator India Pvt Ltd - Branch Office | Bestech Sanskruti Sector 92 | Gurgaon | 122102 | Haryana | India FS North1 HBN CSP Prokon Hi Tech Systems Gurgaon | Krishna Kumar_Prokon Hi-Tech Systems Gurgaon | Prokon Hi-Tech Systems-Gurgaon | UPS not powering on replaced the new ups, now ups working is okay. Model no SUA3000I-INNBQ Serial no BQ1442001234 | Repair |  | 10- Closed | 2023-09-02 13:54 |  |  | 25 | INR | 25 | ENM SECURE POWER
WO-11234265 | 103890102 | 2023-09-09 15:16 | 2023-09-09 | Part order request validated by Mr Pradeep Patil sir | 2023-09-09 12:04 | LC1E0610M7 | LC1E0610M7 | LC1E0610M7 |  | Reg. Complaint for LC1E0610M7 Please find the attached Complaint form & invoice copy. TPNC Technology Pvt Ltd . Indore "B-8 Suryaansh Deep parisar, indore, Madhya Pradesh, India - 452016" Mr. ChandraShekhar Yaduwanshi 9584525121 LC1E0610M7 Contactor NC not working Devendra Mahajan ¦ 9131575424 Thanks & Regards, Devendra Mahajan ¦ 9131575424 -- WINNERS MARKETING Authorised Partner and System Integrator GST NO. ? 23AAAFW5179L2ZS MSME REGISTERED 309 ¦Raja Ram Mohan Roy Complex¦ MTH Compound¦ INDORE¦ 452007 [M.P.] Ph. No. 0731- 4037930 ¦ E- mail: winnersmarketing309@gmail.com | 2023-09-09 | 2023-09-10 12:44 | No | Warranty | TPNC TECHNOLOGY PRIVATE LIMITED | B-8,Suryaansh Deep Parisar,Bicholi Mardana | Indore | 452016 | Madhya Pradesh | India FS ED&I CSP West Team ABR Technical Service Indore | Lalu Sen_ABR Tecneical Services Indore | ABR Technical Services (9574) | Reached at site and checked contactor and found as per customer its NO terminal not working then we checked all terminals screw tightness properly then we given external 230 VAC supply and checked ON/OFF operation 5-7 times working OK and checked continuity found all power poles continuity showing but it's NO terminal not operate so only for customer satisfaction we replace the contactor | Repair |  | 9- Service Validated | 2023-09-12 12:45 | =S= Consig Fill up 226027069 |  | 26 | INR | 26 | ENM POWER PRODUCTS
WO-11234392 | 103910002 | 2023-09-10 12:47 | 2023-09-09 |  | 2023-09-09 16:07 | C25N3MA220 | C25N3MA220 | C25N3MA220 |  | Complaint Patel Agri Ind. C25N3MA220 A comment has been added to your case: 103890672 ?M/s PATEL AGRI INDUSTRIES PVT LTD VILLAGE ARAWAN, BLOCK BEN, DIST. NALANDA, NALANDA , Bihar - 803114 Himanshu Bajpai 9118553846 MCCB 220A, NSX250- 1NO ( C25N3MA220=04 nos) SCHNEIDER MCCB- 3NOS- SUPPLY NOT COMING FROM 1 PHASE our po no 1263 (2022-23) dt 20.12.22 Jayaram Patil +91 9130035982 Dear Pramod, Greetings from Schneider Electric Customer care!! Kindly share the below details to proceed further, we have not received any attachment with case or details. ? Customer name and contact details ? Email id of customer ? Full site address with pin code ? Product model number , serial number or invoice copy ? Exact issue with product ? Regards, Bijay Kumar Sahoo IN_Primary_Tech_PWR Customer Care Centre customercare.in@schneider-electric.com ¦ Schneider Electric India ¦ Toll Free: 18001030011 / 18004194272 ¦ Email: ¦ Site: www.se.com/IN https://www.se.com/in/en/download/?param=appendQueryParam FAQ Link- https://www.se.com/in/en/faqs/home/ Please review this case by clicking this link With regards, Bijay Kumar Schneider Electric Support Team Thanks & Regards? __________________________________________________________________________ Mr. Pramod Karanjkar ( Customer Support ) ¦ pramod@satyampune.com ¦ office@satyampune.com ¦ Satyam Enterprises ¦ M. +91 9850245733 ¦ Site - www.satyampune.com | 2023-09-09 | 2023-09-16 19:00 | No | Warranty | M/s PATEL AGRI INDUSTRIES PVT LTD | VILLAGE ARAWAN, BLOCK BEN, DIST. NALANDA, | NALANDA | 803114 | Bihar | India FS ED&I CSP East Team Vidya Enterprises Lucknow | Rana Ranjan_Vidya Enterprises Lucknow | Vidya Enterprises | As per customer complaint visited the site and check the MCCB C25N3MA220 found faulty. check the continuity between terminal found not showing. SO, MCCB is faulty. Replaced the MCCB from Schneider Service stock. Replaced the MCCB in panel by customer at the shutdown. handover the new MCCB material to customer. and collected defective. | Repair |  | 9- Service Validated | 2023-09-16 19:00 |  |  | 60 | INR | 60 | ENM POWER PRODUCTS
WO-11234401 | 103901754 | 2023-09-09 16:33 | 2023-09-09 | NA | 2023-09-09 16:23 | GCR_NSX100_630 | GCR_NSX100_630 | GCR_NSX100_630 | WX223475117 | MCCB TRIP FOR ON SITE Dear sir, Please kindly assign SCHNEIDER ELECTRIC's Service Engineer at Customer site to attend this reported issue at the earliest. Take this on priority. Also required a detail cause analysis report for the these issue. Datsons Electronics Pvt Ltd "Electronic Zone, MIDC Industrial Area, Mahape, Navi Mumbai, Maharashtra 400705 NTT mahape, Nav 1B " Prakash Kamble - 8381000728 8381000728 MCCB 630A, TRIPPING OF MCCB WITHOUT LOAD. C6332D630-WX223475117 "Invoice No.- & Invoice Dt.- P.O No. - & P.O. Dt.- " Prakash Kamble - 8381000728 PFA. THANKS & REGARDS PRAKASH KAMBLE | 2023-09-09 | 2023-09-11 11:56 | No | Warranty | Datsons Electronics | Electronic Zone, MIDC Industrial Area, Mahape | Mumbai | 400705 | Maharashtra | India FS ED&I CSP West Team East India Power Engineers Mumbai | Sandeep Ingavale East India Power engineers Mumbai | East India Power Engineers (5043) | Visited the site & checked the MCCB on load found R- 2.85Amp, Y - 2.56Amp & B-2.50Amp Load found & MCCB input voltage R-N 231, Y-N 231 & B-N 231. MCCB working found ok. No issue was found on the MCCB side. The MCCB working found ok. | Repair |  | 8- Service Completed | 2023-09-13 10:55 |  |  | 10 | INR | 10 | ENM POWER PRODUCTS
WO-11234444 | 103781686 | 2023-09-11 07:16 | 2023-09-09 |  | 2023-09-09 18:01 | METSEEM6436HCL10RS | METSEEM6436HCL10RS | METSEEM6436HCL10RS | 540400058150 | Schneider make KWH Meter programming button is not working Please find the enclosed attachment. POWER CONTROL EQUIPMENTS No. 40A, 3rd Road Jigani Industrial Area Bengaluru - 560105 GOWTHAM 9538133147 SCHNEIDER MAKE KWH METER WITH RS 485 PORT CL:1 , EM 6433H PROGRAMING BUTTON IS NOT WORKING UNDER WARRANTY ANUSHA & 9448882105 Regards, Anusha Jr. Executive procurement | 2023-09-09 | 2023-09-11 16:00 | No | Warranty | POWER CONTROL EQUIPMENTS | Road No 4 | Anekal | 560105 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Mohammad Riyaz_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | i had visited the site and checked the customer reported meter found programming button not working; enter and escape button not working. so we had replaced new meter from our stock and closed this complaint. | Repair |  | 9- Service Validated | 2023-09-11 18:40 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11234453 | 103910039 | 2023-09-11 17:24 | 2023-09-09 |  | 2023-09-09 18:32 | GV2P21 | GV2P21 | GV2P21 |  | Request for replacement Faulty GVAD1010 Reference attached Purchase Inv. Item Sr. No. 3, GVAD1010 one No. is not working. We Request you please depute your service engineer to rectify the problem or arrange for replacement. ?? Regards pradeep kumar pal M: +91 7048972716 Kandi Electronic logo PNG Kandi Electrical Solutions Pvt. Ltd. Office & Works: Khasra No 981/330, Block No - 03, Basai Village, Near Basai Flyover, Basai Road, Gurugram-122006-Haryana (INDIA) Regd Off: Pocket G4/23-24, FF, Sector-11, Rohini, Delhi-110085(INDIA) GST NO: 06AAFCK1048L1ZI, PAN NO: AAFCK1048L, CIN NO: U31900DL2013PTC249820 | 2023-09-09 | 2023-09-11 17:45 | No | Warranty | Kandi Electrical Solutions PVT. Ltd. | Khasra No. 981/330 , Block -3 Basai Industrial area village Basai Near Basai Flyover Basai . . | Gurgaon | 122006 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the Add on block found damage/ broken, Hence no replacement given to customer. Email : id not provided by customer. | Repair |  | 9- Service Validated | 2023-09-12 10:57 | As per verbal communication with himani , part order needs to be cancelled now. |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11241413 | 103857775 | 2023-09-11 21:33 | 2023-09-12 |  | 2023-09-11 12:36 | 51209 | 51209 | 51209 | RN-2022-W12-5 | Nalbari Medical College/ 8 STAGE POWER FACTOR Relay malfunctioning Dear Sir/Madam Please refer as per purchased a 8 STAGE POWER FACTOR CORRECTION (51209) MAKE SCHNEIDER for RAJU ENTERPRISES,KOLKATA . INVOICE NO-G16776/23-24, DATED-28-07-2023) for one of our prestigious client SHREE GAUTAM CONSTRUCTION CO.LTD.GUWAHATI, That 8 STAGE POWER FACTOR Relay malfunctioning. So it is our humble request to you that please send your services engineer as early as possible. Site Nalbari Medical College Nalbari, Assam Contact Persone:- Amit Kumar Contact no-+917009605836 Thanks & regards, Tanmoy Halder 9007008129 for, RA INDUSTRIAL SYSTEM PVT.LTD. Boral Main Road, Naboday Pally, Bagharghole, Near Kabi Guru Smriti Sangha Club, P.O.- Bonhooghly, Kolkata - 700103. Ph. No.- 9903226317. Email - raindustrialsystem@gmail.com | 2023-09-11 | 2023-09-13 01:30 | No | Warranty | Nalbari Medical College & Hospital | DakhinGaon, Ghograpar, Dakhingaon, Nonoi | Nalbari | 781350 | Assam | India FS ED&I CSP East Team SHIV ELECTRICALS Guwahati | Partha Basar SHIV ELECTRICALS GUWAHATI | SHIV ELECTRICALS | I checked 6 nos of RT-8 APFC controllers and found a wiring issue. | Repair |  | 9- Service Validated | 2023-09-13 01:30 |  |  | 85 | INR | 85 | ENM POWER PRODUCTS
WO-11241706 | 103925324 | 2023-09-13 15:17 | 2023-09-11 |  | 2023-09-11 14:36 | LC1D80AM7 | LC1D80AM7 | LC1D80AM7 |  | LC1D80A 8B21200101984 Complaint LC1D80A 8B21200101984 Complaint LRD340 Mohit Mittal ?+918950400012 AddressBapoli Road, Nimbri Panipat 132103 Haryana | 2023-09-11 | 2023-09-13 16:33 | No | Warranty | RK Spuntex | Bapoli Road, Nimbri | Panipat | 132103 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the contactor found contact weld but as per serial number contactor found out of warranty, Hence no replacement givent to customer. Email : id not provided by customer. | Repair |  | 9- Service Validated | 2023-09-13 17:04 |  |  | 165 | INR | 165 | ENM POWER PRODUCTS
WO-11241788 | 103918567 | 2023-09-12 20:27 | 2023-09-12 |  | 2023-09-11 15:00 | 30002975 | 30002975 | 30002975 |  | FW: MAXIMUM DEMAND METER NOT WORKING Please find the attachment of the invoice for the maximum demand meter. We are facing the problem that after setting the maximum demand the meter is not given a tripping command after crossing the demand limits. Please depute the service engineer and check the meter. The site address is. CMR ECO ALUMINIUM PVT. LTD. SY.NO 429-434, AIIPC INDUSTRIAL PARK, CHINTHALAPALEM VILLAGE, YERPEDU MANDAL, TIRUPATI DISTRICT TIRUPTI PIN- 517619 With Sincere Regards Arif Khan MV Support (HT Department) Mobile No. : 8448484800 E-mail Id : arifkhanlspc@gmail.com, ashwani@lspowercontrol.com LS Power Control Private Limited C440 - 443 Ansal Pioneer Park Industrial Area, Bilaspur, Gurugram, Haryana 122413. | 2023-09-11 | 2023-09-13 17:00 | No | Warranty | CMR ECO ALUMINIUM PVT LTD | Near Chintalapalem toll plaza, venkatagiri Road, Srikalahasthi | Srikalahasthi | 517619 | Andhra Pradesh | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | EM7200 Demand meter tripping issue. E-mail : ratipal.y@cmr-nikkei.com | Repair |  | 9- Service Validated | 2023-09-13 17:40 |  |  | 138 | INR | 138 | ENM POWER PRODUCTS
WO-11172587 | 103586024 | 2023-08-28 16:43 | 2023-08-28 |  | 2023-08-28 11:22 | SRV6KL-IN | SRV6KL-IN | SRV6KL-IN | 9S2307A00043 | Serial# 9S2307A00043 P:Battery back issue S:Warranty | 2023-08-28 | 2023-09-04 18:06 | No | Warranty | Hardcastle Restaurant Pvt Ltd | Mcdonald Family Restaurant I Eligance Mulgav Anderi East | Mumbai | 400097 | Maharashtra | India FS West1 HBN CSP_Mahavir Sys Power Pvt Ltd Goregoan | Veerappa Neetoor Mahavir Sys Power Pvt Ltd Goregoan | Mahavir Sys Power Pvt Ltd -Goregaon | FSR visited customer site replace battery at customer site ups working fine | Repair |  | 8- Service Completed | 2023-09-04 18:09 |  |  | 20 | INR | 20 | ENM SECURE POWER
WO-11241875 | 103918498 | 2023-09-11 16:05 | 2023-09-11 | ACB Phase missing problem Observed | 2023-09-11 15:38 | GCR_MVS | GCR_MVS | GCR_MVS | 10230110511 | Re: Frequent tripping of Schneider breaker in RMU [ thread::Gt_hbWZ-dKKiSK4zXtJxCT4:: ] Recently we are experiencing frequent tripping of Schneider Breaker in RMU, supplied to and installed by M/s Pratik Systems and Solutions LLP immediately, when heavy loads are taken in circuit We request for rectification of this fault , on emergency basis Our site location is Indiaqo Foods Pvt. Ltd F 215, New MIDC, Supa, Ahmed Nagar Dist. Indiaqo FoodsPrivate Limited F -215, MIDC , Supa Ahmed Nager Dist 414301 Sheriff R M 8056687608 8154808834 maintenance@indiaqofoods.com The Model is MSV25N and serial # is 10230110511 Hardware Issue Loss of contact leading to phase imbalance Regards Sheriff R M Maintenance Manager, IQFPL 8056687608 | 2023-09-11 | 2023-09-12 16:44 | No | Warranty | Indiaqo FoodsPrivate Limited | F -215, MIDC , Supa null | Ahmednagar | 414301 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Amit Patil_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the ACB Phase missing problem Observed. then we off acb rack out & checked when ACB ON. continuity found ok. then we rack in ACB & ON ACB then we ON motor the we on motor then ACB was off because UV supply cut off. observed Mega win relay setting was low then we changed the setting and taken operation found ok. | Repair |  | 9- Service Validated | 2023-09-13 11:25 |  |  | 70 | INR | 70 | ENM POWER PRODUCTS
WO-11242124 | 103930717 | 2023-09-12 12:21 | 2023-09-11 |  | 2023-09-11 17:24 | GCR_NW_CB | GCR_NW_CB | GCR_NW_CB | 10221340269 | we have observed flash issue in WTP main incomer ACB (1250 A).site- MSIL GURGAON we have observed flash issue in WTP main incomer ACB (1250 A).site- MSIL GURGAON P:ACB flash issue ITEM: ACB RATING: 1250A Cat no.: NW12H14PED06.0P MODEL NO.: NW Serial no.: 10221340269 MAKE: SCHNEIDER QTY.: 1 Maruti Suzuki India Limited Sector-18, Old Palam Gurgaon Road Gurgaon, Haryana-122015 Contact person : Mr. Arka Ghosh, Contact no.: 9882134969 Warranty | 2023-09-11 | 2023-09-12 12:24 | No | Warranty | Maruti Suzuki India Limited | Sector-18 Gate no 1 Near Palam mod Gurgaon Road, | Gurgaon | 122015 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the ACB found working ok. Email : id not provided by customer . | Repair |  | 9- Service Validated | 2023-09-12 12:49 |  |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11295496 | 104210216 | 2023-09-22 14:57 | 2023-09-22 |  | 2023-09-22 13:25 | Leonardo EV,DX,R22,TDAR1321A,Downflow With Heater & Humidifier | TDAR1321AN001 | TDAR1321AN001 | NUCS1906 | RE: AAI BF call log - M/s. Fresco AMC UNIT 1/3/2023 to 28/2/2024 P:Issue: Unit issue - Please log a BF call and assign it to M/s. Fresco-NUCS1906 - TDAR1321AN001 S-AMC | 2023-09-22 | 2023-09-16 17:43 | No | Contract | Airport Authority of India | Bangalore International Airport Project Budigere Road | Bangalore | 560300 | Karnataka | India FS South3 Cooling CSP Fresco solutions Bangalore | PRIYESH P_Fresco solutions Bangalore | Fresco solutions | Discharge line leakage re-commissioning the unit with R407 gas 19 kg | Repair |  | 8- Service Completed | 2023-09-22 17:47 |  |  | 45 | INR | 45 | ENM SECURE POWER
WO-11246948 | 103955810 | 2023-09-12 12:34 | 2023-09-12 | Circuit Breaker Part Number is not displayed | 2023-09-12 12:25 | GCR_NW_CB | GCR_NW_CB | GCR_NW_CB | 20219823783 | FW: Circuit Breaker Part no not displayed Hi Samit, Good Evening, As confirmed by you it?s missed from logistics team to put sticker on Product & Box as Cummins requirement. Kindly send the respective sticker to below address and share the docket details here only ? Cummins Technologies India Pvt. Limited, Plot No B-3/1, PHP-SEZ, MIDC industrial area, Surwadi, Phaltan SEZ Industrial Area, Phaltan Taluka, District Satara, Maharashtra, India. Pin Code: 415522 Contact Name & Mob No ? Mr. Vivek kumar & 8789070143 @Sampurna Gupta ? Please log the complaint and assign it Team Super Electricals to visit and paste stickers on our Product and Box accordingly. | 2023-09-12 | 2023-09-14 10:49 | No | Warranty | Cummins India | Cummins India Limited Power Generation Business Unit plot no.:B2,SEZ Industrial area,Village Nandal & Surwadi Taluka - Phaltan, Dist- Satara -415523 | Pune | 415523 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Samadhan S_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the Circuit Breaker Part Number is not displayed on outer packing as well as physically part. So Recognition is possible for cummins. so we Paste the as per requirement cummins india part with invoice. problem resolved after pasting sticker. | Repair |  | 9- Service Validated | 2023-09-14 10:56 | VIP FSR= No 3. FSR Request: Unavailability of the preferred FSR, need to depute Non VIP FSR(dattatray kute). |  | 120 | INR | 120 | ENM POWER PRODUCTS
WO-11295515 | 104210603 | 2023-09-22 15:00 | 2023-09-22 |  | 2023-09-22 13:30 | Leonardo EV,DX,R22,TDAR1321A,Downflow With Heater & Humidifier | TDAR1321AN001 | TDAR1321AN001 | NUCR0013 | P:Issue: Unit issue - Please log a BF call and assign it to M/s. Fresco-NUCR0013 - TDAR1321AN001 AMC UNIT 1/3/2023 to 28/2/2024 P:Issue: Unit issue - Please log a BF call and assign it to M/s. Fresco-NUCR0013 - TDAR1321AN001 S-AMC | 2023-09-22 | 2023-09-16 17:50 | No | Contract | Airport Authority of India | Bangalore International Airport Project Budigere Road | Bangalore | 560300 | Karnataka | India FS South3 Cooling CSP Fresco solutions Bangalore | PRIYESH P_Fresco solutions Bangalore | Fresco solutions | replaced the condenser fan | Repair |  | 8- Service Completed | 2023-09-22 17:52 |  |  | 45 | INR | 45 | ENM SECURE POWER
WO-11037207 | 102688685 | 2023-07-29 18:43 | 2023-07-26 |  | 2023-07-26 22:43 | SRV10KUXI-IN | SRV10KUXI-IN | SRV10KUXI-IN | 9S2313A00758 | DOP:-22-06-2023 P:-Smart UPS-Installation S:-Installation | 2023-07-26 | 2023-09-08 12:58 | No | Commercial Action - Sales | SYDAC SIMULATION TECHNOLOGIES INDIA PVT LTD | Taloja Nagar Mandale null | Navi Mumbai | 410208 | Maharashtra | India FS West1 HBN CSP_Mahavir Sys Power Pvt Ltd Vashi | Sanju Chauthmol_Mahavir Sys Power Pvt Ltd Vashi | Mahavir Sys Power Pvt Ltd -Vashi | Engineer had done the Commissioning of ups at customer site and checked its working fine on both mode, | Commissioning & Installation | Start-up | 10- Closed | 2023-09-08 13:02 |  |  | 23 | INR | 23 | ENM SECURE POWER
WO-11172670 | 103587187 | 2023-08-28 13:54 | 2023-08-28 |  | 2023-08-28 12:02 | SRC2000XLINBQ | SRC2000XLINBQ | SRC2000XLI | bq1723001933 | FW: RR ID : IM15318585 ¦ Store Code : 9173 ¦ Schneider Pending Contract P: UPS not working S:AMC Note: old serial no:B21535001595/SRC2000XLI-CC | 2023-08-28 | 2023-09-02 14:55 | No | Contract | Reliance Retail Ltd | RRL Trends Sibsagar Assam, Baruah Complex A T Road, Ward No 9 PO Sivasagar | Sibsagar | 785640 | Assam | India FS East HBN CSP Comptech Systems Services P Ltd Jorhat | Amarjit Dutta_Comptech Systems Services P Ltd Jorat | Comptech Systems Services P Ltd - Jorhat -Kolkata | Unit replaced along with battery and issue resolved - SRC2000XLINBQ BQ1804012566 | Repair |  | 10- Closed | 2023-09-02 14:56 |  |  | 65 | INR | 65 | ENM SECURE POWER
WO-11249087 | 103969763 | 2023-09-13 14:48 | 2023-09-13 |  | 2023-09-12 19:46 | NSX630N_0059 | NSX630N_0059 | NSX630N_0059 | TC_2022_W38_4 | RE: Complaint - NTT DATA Center, Chennai -Meter issue, Case: 103892125, [ thread::JMo3UHz-c5StGd6ntx1Ypj4:: ] NTT GLOBAL DC & CI INDIA P LTD "Wing A, No 8, South Phase, Sidco Industrial Estate, MTH Road, Sai Nagar, Ambattur Industrial Estate, Chennai TN 600058 India" K.Sathosh Kumar 9940618336 630A motorised MCCB 1st floor not working Any time In warranty Pre commissioning stage | 2023-09-12 | 2023-09-20 15:00 | No | Warranty | NTT GLOBAL DC & CI INDIA P LTD | Wing A, No 8,south phase,Sidco Industrial Estate, MTH Road,Sai Nagar, Ambattur Industrial Estate, | Chennai | 600058 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Visited at site and inspected the 630A Ref: LV432641, DOM: TC-2022-W38-4 MCCB not working customer reported to me. Today visited at site now checked manual mode ON/OFF function found ok. Charged auto mode. Spring charging function counting running no limit switch cutoff. So that issue is escalated to schneider. Replacement motor mechanism DOM: TC-2023-W28-4 | Repair |  | 9- Service Validated | 2023-09-21 12:15 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 15 | INR | 15 | ENM POWER PRODUCTS
WO-11037208 | 102826316 | 2023-07-29 18:42 | 2023-07-26 |  | 2023-07-26 22:43 | SRV15KUXI-IN | SRV15KUXI-IN | SRV15KUXI-IN | 9S2307A01277 | DOP:-22-06-2023 P:-Smart UPS-Installation S:-Installation | 2023-07-26 | 2023-09-08 12:53 | No | Commercial Action - Sales | SYDAC SIMULATION TECHNOLOGIES INDIA PVT LTD | Taloja Nagar Mandale null | Navi Mumbai | 410208 | Maharashtra | India FS West1 HBN CSP_Mahavir Sys Power Pvt Ltd Vashi | Sanju Chauthmol_Mahavir Sys Power Pvt Ltd Vashi | Mahavir Sys Power Pvt Ltd -Vashi | Engineer had done the Commissioning of ups at customer site and checked its working fine on both mode, 16nos battery VDC setting also done | Commissioning & Installation | Start-up | 10- Closed | 2023-09-08 13:01 |  |  | 23 | INR | 23 | ENM SECURE POWER
WO-11253085 | 103993672 | 2023-09-16 08:16 | 2023-09-13 |  | 2023-09-13 12:22 | G7ATSC34000K5X40RM | G7ATSC34000K5X40RM | G7ATSC34000K5X40RM | 2400936-001WE | Warranty Confirmed By Nagabhushan Complaint - Raheja Pallikaranai, Chennai - ATS retransfer issue Sycamore Properties, D&B LS (K.Raheja) "No.2, 200 ft. Radial Road, Opp. To Kamakshi Memorial Hospital, Pallikarnai, Chennai - 600100" R.Ramrajan 9600083570 ASCO ATS 4000A 4P 7000 series (Sl.No.2400936-001WE) Auto Trasfer issue. Position failed issue Night In warranty Commissioned on 13-06-2023 | 2023-09-13 | 2023-09-16 22:31 | No | Warranty | K.Raheja Corp | No.2, 200 ft. Radial Road, Opp. To Kamakshi Memorial Hospital, Pallikarnai | Chennai | 600100 | Tamil Nadu | India FS ED&I CSP South Team Electro Power Systems Chennai | VIJAY KUMAR Electro Power Systems Chennai | Electric Power System | Checked the ATS by giving both EB and DG power supply, Transfer and Re-transfer found normal. But customer suggest that the ATS need to OFF while changing from EB to DG and DG to EB, we explained the Ats is not designed for OFF conditing and transfer time of source is 40ms to 100ms.so the power interruption will not occurs. | Repair |  | 9- Service Validated | 2023-09-19 07:32 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11253159 | 103991930 | 2023-09-14 16:14 | 2023-09-13 |  | 2023-09-13 13:05 | CAD50BD | CAD50BD | CAD50BD | 9008582475 | Complaint Registration 2324-TAI-ECS Dear Sir/Ma?am, Good Morning!! Please find the attached complaint and arrange the service engg ASAP. Taikisha Engineering India Pvt. Ltd. Plot no. 19, sec-3, IMT Manesar GURGAON, HARYANA-122050 Mr. Sanjay Verma 7838111423 CAD50BD=01PCE 1NO contact is not Working Electrical Control Systems Pvt. Ltd. # In no. 9008582475 DT. 31/05/23 ASHISH-9910015705 Thanks & Best Regards Ashish Malik cid:image001.png@01D93716.24E11800 RailTuff Second floor, Plot No-14-15 Sec-33,Opposite Info City 2, Gurgaon-122001 Tel. no:- 0124-2226666, +91-9910015705 | 2023-09-13 | 2023-09-22 14:09 | No | Warranty | Taikisha Engineering india pvt. Ltd. | Plot No-19 ,Sector-3 Imt Manesar | Gurugram | 122051 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the contactor found no/nc point not working , Hence faulty replaced. CAD50BD - 1 nos Email :cpdqa@taikishaindia.com | Repair |  | 8- Service Completed | 2023-09-23 14:13 |  |  | 55 | INR | 55 | ENM POWER PRODUCTS
WO-11295581 | 104211168 | 2023-09-22 17:10 | 2023-09-22 |  | 2023-09-22 14:00 | Big Chillers | BREC | BREC | SRF032711 | Chiller 10 common alarm on BMS console DC8 AMC UNIT 1/5/2023 to 30/4/2024 P:Chiller 10 common alarm on BMS console DC8 - Chiller 10 common alarm (on chiller display-EVO n 1) -XRAC5622 & SRF032711 S-AMC | 2023-09-22 | 2023-09-22 23:18 | No | Contract | Netmagic IT Services Pvt. Ltd. | DC-7,Light hall, C wing, Hirananadani Business Park, Saki Vihar Road, Chandivali, Andheri (E) | Mumbai | 400069 | Maharashtra | India FS West1 Cooling CSP Unique India Mumbai | Deepak Pal Unique India Mumbai | Unique India- Mumbai HBN CSP | Permission not received from customer end. | Repair |  | 10- Closed | 2023-09-22 23:21 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11256812 | 104004954 | 2023-09-18 16:30 | 2023-09-14 |  | 2023-09-14 09:30 | LC1D32M7 | LC1D32M7 | LC1D32M7 | 1023082-1 | LC1D32M7- Stuck Issue 1023082 LC1D32M7- Stuck Issue 1023082 Sarvesh Kumar +919910479400 sbt274@gmail.com Welcare Industries B-274 Service Rd, Mangol Puri Industrial Area Phase I, Phase I, Delhi, New Delhi Delhi 110083 | 2023-09-14 | 2023-09-18 16:33 | No | Warranty | Welcare Industries | B-274 Service Rd, Mangol Puri Industrial Area Phase I, Phase I, Delhi, | New Delhi | 110083 | Delhi | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the contactor found working ok. Email : id not provided by customer . | Repair |  | 8- Service Completed | 2023-09-18 17:09 |  |  | 25 | INR | 25 | ENM POWER PRODUCTS
WO-11259340 | 104034716 | 2023-09-15 10:15 | 2023-09-14 |  | 2023-09-14 16:41 | LV540306 | LV540306 | LV540306 |  | COMPLAIN ? LV540306 - QTY - 01 (SHREEJI ELECTRICAL(PANDESARA).) Please Provide Complain number has per Attached Deta Checklist for Complaint Registration 1 Name of Customer M/S SHREEJI ELECTRICAL(PANDESARA) 2 Site Address ROOM NO.5/6, 1ST FLOOR, SERVICE COMPLEX, GIDC,PANDESARA,SURAT-394221 Contact Phone / Mob. No: 6359381538 3 Name of contact person at site MR. Shreeji Elec. Pandesara Vishal 5 Defective product details LV540306 - QTY - 01 6 Product Make SCHNEIDER-MCCB 7 Nature of Defect NOT WORKING 8 Shutdown availability if applicable 9 Warranty status UNDER WARRANTY 10 Commissioned / Installed date 11 Serial No: or DOM of the product BILL NO - : 5707/23-24 DATE - 08-09-2023 12 Name & phone No: of person registering the complaint JOHNSON- 8780431402 13 NOTE Note : Point Nos: 1 to 9 are compulsory image.png JOHNSON.. Mob No:8780431402 EPABX No: 0261-2432308, 2420774 / 7383732308 / 9737326676 Hi-Tech Marketing NOTE: our new address is Hi-Tech Marketing "HI-TECH House" SHOP NO: 209, SNS INTERIO, E-Block,Bhatar-Althan Road,Surat-395007 | 2023-09-14 | 2023-09-15 12:49 | No | Warranty | SHREEJI ELECTRICAL | ROOM NO.5/6, 1ST FLOOR, SERVICE COMPLEX, GIDC,PANDESARA null | SURAT | 394221 | Gujarat | India FS ED&I CSP West Team SHIV SAI ELECTRICALS Vapi | Hiral Solanki_SHIV SAI ELECTRICALS VAPI | shivsai electricals | AS PER SITE VISIT WE CHECK THE RODUCT AND FOUND OK ON VISUAL INSPECTION.AFTER THAT CHCK THE MCCB POLE CONITNITY AND FOUND THE MCCB POEL IS PEN.WHEN WE CHECK THE PRODUCT WARRNTY STATUS AND FOUND THE PRODUCT IS UNDER WARRNTY NEEDS TO BE REPLACD. | Repair |  | 9- Service Validated | 2023-09-16 12:52 | =S= Consig Fill up 226060660 |  | 138 | INR | 138 | ENM POWER PRODUCTS
WO-11259372 | 104034707 | 2023-09-14 19:24 | 2023-09-14 |  | 2023-09-14 16:51 | GV3P50 | GV3P50 | GV3P50 | 7Q2315 | Complaint - Dynaspede Integrated Systems Pvt Ltd. GV3P50 P {margin-top:0;margin-bottom:0;} Dear Sir/Madam, Kindly find attached checklist for your reference and case no. asap. Dynaspede Integrated Systems Pvt Ltd. No.371 & 372, 10th cross road 4th phase Peenya Indl. Area, Bangalore-560058 Mr. Arun Mob No. : 8884559336 GV3P50 On /Off Switch not working. 7Q2315 Aruna BR Mob: 8884559336 Regards, Aruna BR -------------------------------------------------------------------------------------------------------------------------------------------------------- Pooja Power Products No. 371 & 372, 1st Floor, 10th Cross Road, 4th Phase, Peenya Industrial Area, Bangalore ? 560 058 Mob : +91 8884559336 E-Mail : arunbr@poojapower.com Web : www.poojapower.com | 2023-09-14 | 2023-09-20 16:31 | No | Warranty | PAC systems and solutions (Pooja power controls) | NO : 371 & 372, 1ST Floor, 10th Cross Road, 4th Phase, Peenya Industrial Area, Bangalore | Bangalore | 560058 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | MANOJ GANESAN SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported motor circuit breaker 37-50A, the pro found was intermittent operation, getting stuck up at trip position, due to NTR. So we had booked the zvo directly to the pooja power products. | Repair |  | 9- Service Validated | 2023-09-21 21:49 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11265056 | 104062698 | 2023-09-15 20:09 | 2023-09-15 |  | 2023-09-15 16:10 | MVS32N4NW6A | MVS32N4NW6A | MVS32N4NW6A | 10222671134 | RE: Schneider Electric confirmation on closing Case 103891669 Please find the attached details of the same and do the needful immediately. MVS32N4EW6A 10222671134 M/s. Sobha Projects and Trade Pvt Ltd Godrej Commercial Hub C/o, Godrej Downtown Sahakara Nagar, Batrayanapura Bengaluru - 560092 Mr. Ganesh 9606085427 Easypact MVS32N, ETA 6G, 4P Rack out issue. Sadath: 7760989131 Complaint Date: 08-09-23 Regards S. Mallesh | 2023-09-15 | 2023-09-16 11:15 | No | Warranty | Sobha Projects And Trade Pvt Ltd | Godrej Commercial Hub C/o, Godrej Downtown Sahakara Nagar, Batrayanapura | Bengaluru | 560092 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | C Gunasekaran_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | We had visited the site and checked the customer reported ACB.Found not getting rackout.Due to over rackin. we dismantle and rectified.After that rackin and rackout happening.There is no issues with our product. | Repair |  | 9- Service Validated | 2023-09-17 10:16 |  |  | 25 | INR | 25 | ENM POWER PRODUCTS
WO-11172840 |  | 2023-08-28 16:23 | 2023-09-16 |  | 2023-08-28 13:18 | EFC MONOBLOCK 1.3TR R410A START KIT RS485 SEQ CONTROL | WDF0181BN040-1 | WDF0181BN040-1 | JK2048000831 | PM | 2023-08-28 | 2023-09-11 16:07 | No | Commercial Action - Service Ops | Reliance Jio Infocomm Ltd | Jagmeet Singh, Motor Market, Bhatinda-Malout Road, Giddarbaha | Bathinda | 152101 | Punjab | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Abhishek Sharma Freezeotech Airconditioning & Refrigeration Chandigarh | Freezeotech Refrigeartion & Air Conditioning Corporation | We visited the site and do the wet PM of Unit , check gas pressure , clean ODU and IDU coils and tighten loose points , check unit operation its working ok | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-11 16:09 |  |  | 260 | INR | 260 | ENM SECURE POWER
WO-11265086 | 104056330 | 2023-09-16 08:26 | 2023-09-15 |  | 2023-09-15 16:28 | LRD32 | LRD32 | LRD32 | 9008524325 | COMPLAINT FORM_TARSONS PRODUCTS LTD. Kindly log complaint,detail are below. Company Name & Complete Address with pin code ? TARSONS PRODUCTS LTD. (FOOD AND POLY PARK, DHULAGARH, HOWRAH, 7711302 Where product is installed- Chiller for compressor. Contact Person at Site : Name & Mobile No.- Koushik Dewasi; Mob. No. +919810954314 Contactor Model - LCD38 (200vac coil voltage)-1 No OLR Model- LRD32 -1 No Issue ? Not working. Invoice No- 9008524325/21-04-2023 Thanks & Regards ¦ Raneet kaur ¦ Balaji Switchgears Pvt. Ltd. ¦ Delhi- India ¦ Manager-Operations & Marcom Phone: +91-11-44755186/187/188 /47093969 ¦ Mobile No:- +91-8700189503¦ (In case not-reachable, contact on whatsapp call) ¦ CIN No.: U31300DL1997PTC088005 ¦ | 2023-09-15 | 2023-09-21 11:36 | No | Warranty | Tarsons Products Limited | PPF-1, Poly Park, Dhulagori null | Howrah | 711302 | West Bengal | India FS ED&I CSP East Team SREYAM SERVICES BHATPARA | AMIT BHATTACHARYA_SREYAM SERVICES BHATPARA | Sreyam Services(8513) | AFTER SITE VISIT FOUND DEFFECTIVE CONTRACTOR AND THERMAL OVER LOAD RELAY REPLACE BY NEW ONE AND DEFFECTIVE MATERIAL IS COLLECTED. | Repair |  | 9- Service Validated | 2023-09-21 11:36 | =S= Consig Fill up 226063691 |  | 28 | INR | 28 | ENM POWER PRODUCTS
WO-11265173 | 104063922 | 2023-09-15 17:09 | 2023-09-15 |  | 2023-09-15 16:53 | LV516312 | LV516312 | LV516312 | 10-2023-W06-1-6151L3 | MCCB complain booking required. Pls book complain of MCCB. 125A MCCB- LV516312- 1pc Kush bhai- 9974422612. Office Address- B-206, Ganesh Glory 11, SG highway, Jagatpur Road. Ahmedabad-382470. Regards, Ashish Patel Senior Manager-Sales Retail Division Schneider Electric D +91 79 66826701 M +91 9879594086 E Ashish.patel1@se.com Toll Free: 1800 419 4272, 18001030011 # 1506-1507 Shapath-5, 15th Floor, Opp.Karnavati club, S.G.Highway, Ahmedabad -380 015 Gujarat,India | 2023-09-15 | 2023-09-16 17:38 | No | Warranty | Ganesh Glory 11 | B-206, SG highway, Jagatpur Road. | Ahmedabad | 382470 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | Parthiv Patel JKS Ahmedabad | JKS Engineering Co. | We visit at site check mccb on/off found ok.check mccb tripping found.check mccb terminal and body side not any problem.check mccb 3th pole open.1nos mccb replecement. | Repair |  | 9- Service Validated | 2023-09-27 16:44 | =S= Consig Fill up 226079549 |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11265288 | 104065109 | 2023-09-16 08:30 | 2023-09-15 | NA | 2023-09-15 17:50 | C25F42D250 | C25F42D250 | C25F42D250 | 2300622 | Dear Sir/Madam, Please depute your service engineer for attached complaint on top priority. Regards, Pramod Vertiv Energy Private Limited. Plot G1, Additional Ambernath Industrial Area, Phase2 Ambernath MAHARASHTRA 421506 India Sandip Badgujar / Pratik Rumde 9766900813 / 7400492090 CVS MCCB C25F42D250 NSX25F 36KA AC 4P4D 250A 2.2 Schneider Micrologic Issue Yes Yes No Invoice No. 2300622 dt 12/05/2023 attached invoice Pratik Rumde - Mb.74004 92090 | 2023-09-15 | 2023-09-16 08:48 | No | Warranty | Vertiv Energy Private Limited | G1,Additional Ambernath Industrial Area Phase-2 | Thane | 421506 | Maharashtra | India FS ED&I CSP West Team East India Power Engineers Mumbai | Abhishek Parab_East India Power engineers Mumbai | East India Power Engineers (5043) | Visited the site & observed that 2 days ago NSX250A 4Pole MCCB carried out a secondary injection test. In testing the MCCB trip unit was not communicated with the testing module. In testing whenever connecting the testing software shows a trip unit field. Checked the primary test on the same MCCB and found all primary test was satisfactory. After the primary test was done the secondary injection test & found trip units were properly communicated with the testing module & all LSIG trip tests were found ok. | Repair |  | 8- Service Completed | 2023-09-28 11:56 | =S= Consig Fill up 226060661 |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11269385 | 104076835 | 2023-09-16 14:03 | 2023-09-16 |  | 2023-09-16 12:37 | C12F3TM160B | C12F3TM160B | C12F3TM160B | TC22025 | ComPacT NSXm160F, 160A, TP, 36KA, TM Based MCCComPacT NSXm160F, 160A, TP, 36KA, TM Based MCCB "Y" Phase pole is not working, Voltage is dropping with load. M/s. Texas Instruments No. 66/3, Bagmane Tech Park, C V Raman Nagara Near DRDO, Bangalore - 560 093 Mr. Sibgath 9880162637 ComPacT NSXm160F, 160A, TP, 36KA, TM Based MCCB ("Y" Pahse pole is not working) Schneider ComPacT NSXm160F, 160A, TP, 36KA, TM Based MCCComPacT NSXm160F, 160A, TP, 36KA, TM Based MCCB "Y" Phase pole is not working, Voltage is dropping with load. Yes Yes 10.06.2022 EAV94316, 160A, TC22025, 12-00162-1 Mr.Nagaraja - 9880588618 | 2023-09-16 | 2023-09-22 10:30 | No | Warranty | Texas Instruments India Pvt Ltd | Bagmane Tech Park No. 66/3, Adjacent to LRDE Byrasandra, C.V. Raman Nagar post | bangalore | 560093 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | C Gunasekaran_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported Nsxm160A Mccb, the problem found was mccb y phase continuity not there, when RYB input supply voltage available in the mccb. so we had arranged for the replacement after replacing checked found working ok. | Repair |  | 9- Service Validated | 2023-09-22 19:30 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 15 | INR | 15 | ENM POWER PRODUCTS
WO-11269386 | 104066754 | 2023-09-16 21:10 | 2023-09-16 |  | 2023-09-16 12:37 | MVS20N4MW2L | MVS20N4MW2L | MVS20N4MW2L | 10225004 | Complaint Registration For MVS20N4MW2L We supplied MVS20N4MW2L to RK ENGINEERING AND INFRASTRUCTURE, ERODE (Panel builder) they completed the panel and supply to the Venkateshwaraa Textiles is considered as defective. Please find the attached complaint registration form, invoice for your reference. Kindly clear the problem as soon as possible. Thank you. ?M/S RK ENGINEERING AND INFRASTRUCTURE M/S. Venkateshwaraa Textiles 9/41, Vellakaradu Thappakuttai, Elampillai,Salem.537502. MR. BALAMURUGAN Mob. No: 9345655553 MVS20N4MW2L - 2000A 4P 50KA MDO ET2L ACB ACB CONTINUOUSLY TRIPPING CANT ABLE TO SOLVE THE PROBLEM GS220600, (24/12/2023) S1B69316 10225004 1607 GUNA 99626033328 ERISA ENERGY SOLUTIONS PVT LTD 782 1ST FLOOR,VKK MENON ROAD,NEW SIDDHAPUDUR, COIMBATORE - 641 044 Thanks & Regards M.Gunaseelan | 2023-09-16 | 2023-09-21 15:59 | No | Warranty | Venkateshwaraa Textiles | 9/41, Vellakaradu Thappakuttai, Elampillai, Salem null | Salem | 637502 | Tamil Nadu | India FS ED&I CSP South Team Power Pro Engineering Services Coimbatore | KV ARUNKUMAR_POWER PRO ENGINEERIG SERVICES COIMBATORE | Powerpro Engineering Services | WE HAVE VISITED THE AND INSPECTED WE FOUND ACB NOT ABLE TO ON WE HAVE CHECKED AND FOUND ACB ALL THE OPERATION ARE FOUND OK NO PROBLEM FOUND IN THE ACB | Repair |  | 9- Service Validated | 2023-09-21 16:04 |  |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11269417 | 104076940 | 2023-09-16 16:19 | 2023-09-16 |  | 2023-09-16 13:49 | LV540007 | LV540007 | LV540007 | TC-2022-W23-4_1 | 400A, 4P, MP Based Motorised MCCB is tripping with load & SDE trip status. Dear Sir, Kindly find attached Checklist for complaint registration form and attend this complaint immediately. M/s. Embassy tech village centrel garden varthur outer ring road Dherabishanahalli .Near New horizon collage Bangalore Mr. Anand 9789071314 LV540007E ComPacT, NSX 400 F .36KA 4P 400A MP based motrorised MCCB - 2 Nos. MCCB is tripping with load & SDE trip status LV540007E, TC-2022-W23-4, 8UPW028821, C4 OF 46E, 2URZ0364009, 1022455, LV540630, 1022333 Nagaraja K.G 9880588618 Thanks & Regards, Nagaraja K.G. QA & Service Mobile: +91-9880588618 Pace Switchgears Pvt. Ltd., (Manufacturers of Quality Switch Boards) Sy.No. 2/10, Eeralingaiah Industrial Estate, Srigandhadakaval, Sunkadakatte, Bangalore-560 091. Ph. :+91 8023588338/39, 23582473, | 2023-09-16 | 2023-09-19 12:58 | No | Warranty | Embassy TechVillage | Outer Ring Rd, near New Horizon College, Devarabisanahalli, Kadabeesanahalli null | Bengaluru | 560103 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Mohammad Riyaz_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | We had visited the site and checked the customer reported MCCB.Founded problem was MCCB found water entered inside so they trip randomly.control terminals got rust.And heavy dust accumulated internal MCCB. This is an external cause,so we unable to support for replacement. | Repair |  | 9- Service Validated | 2023-09-19 22:04 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11279317 | 104093438 | 2023-09-19 12:11 | 2023-09-19 |  | 2023-09-19 10:14 | LV525021 | LV525021 | LV525021 | 1023063033 0 | MCCB 250A / TP - 1 Failed MCCB 250A/TP- 1 nos. failed. You are requested to 'kindly, take an immediate action against it. Fault: Phase Failure Site detail; ELAN AUTOMATION # Plot no-2, Ratoli road, Kansapur, Yamuna Nagar Contact No.: 9996523397 Billing detail:- Bill no.: 0389 Bill date:2-05-2023 Billed from: Kohli Electrical Traders THANKS & REGARDS ELAN AUTOMATION SUMAN (Manufacturing & Installation of Electrical Control Panels & Auto Synchronisation Panels.) Office/Factory Address: Ratoli Road, Kansapur,Yamuna Nagar. M: +91 9991633786 'E mail: elanautomationynr@gmail.com | 2023-09-19 | 2023-09-19 12:18 | No | Warranty | Elan Automation | #2 Ratauli Road, Kansapur, | Yamuna Nagar. | 135002 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the MCCB found "Y-B" Phase Missing. Hence faulty replaced. LV525303 - 1 Nos. email : elanautomationynr@gmail.com | Repair |  | 8- Service Completed | 2023-09-19 16:15 |  |  | 105 | INR | 105 | ENM POWER PRODUCTS
WO-11173255 | 103595738 | 2023-08-28 17:53 | 2023-08-28 |  | 2023-08-28 16:26 | Std Exch APC Smart-UPS RT 2000VA 230V No Batteries | SURT2000UXIQ | SURT2000UXI | JQ0750010586 | FW: INC0004270616//S1ANPU95//SYNTEL PUNE CAPTIVE//UPS not working HDFC Bank Pending Contract P: UPS not working S:AMC | 2023-08-28 | 2023-09-04 14:33 | No | Pending Contract | HDFC Bank Ltd | HDFC ATM S1ANPU95 Syntel Pune Captive Plot No B1 Talawada Software Technology Park MIDC Taluka Haveli Talawade Pune Nigdi 411044 | Pune | 411044 | Maharashtra | India FS West1 HBN CSP_United Solutions Pune | Prashant Shitole_United Solutions Pune | United Solutions | Battery replacement pending by customer. Will be physically closed once the batteries and rack is replaced by the customer. | Repair |  | 8- Service Completed | 2023-09-04 14:35 |  |  | 0 | INR | 0 | ENM SECURE POWER
WO-11280319 | 104077524 | 2023-09-19 14:40 | 2023-09-19 |  | 2023-09-19 12:37 | LV525302 | LV525302 | LV525302 | AA2720128906 | faulty material Please replace or repair below faulty material. 01. LV525302-1PCS 02. LV516302-1PCS 03. 47894-1CS Faulty material detail and costumer detail below mentioned. 01. LV525302-1 INVOICE NO.-AA2720128906 DATED-17.12.2023, CUSTOMER ?ESSWIN ELECTRO CONTROL PANTNAGAR 02. LV516302-1 INVOICE NO.AA2730099995 DATED-04.07.2023- CUSTOMER-BRAHMOTECH ENGINEERING 03. 47894-1 INVOICE NO.AA3330045306 DATED-21.03.2023-CUSTOMER-BRAHMOTECH ENGINEERING With Best Regards, Ganesh Kumar Mobile: 91 7351008393. Classic Automation and Control Opp Greenply Industries,Sector-9 Near Centre Point Hotel, SIDCUL,Pantnagar, 263153 U.S.Nagar, Uttrakhand | 2023-09-19 | 2023-09-19 15:18 | No | Warranty | Classic Automation and Control | Opp Greenply Industries, Sector-9 Near Centre Point Hotel, SIDCUL | Pant Nagar | 263153 | Uttarakhand | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Rakesh Kumar Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the MCCB found phase missing. Hence faulty replaced. LV525303 - 1 Nos. email : id not provided by the customer. | Repair |  | 8- Service Completed | 2023-09-19 17:05 |  |  | 435 | INR | 435 | ENM POWER PRODUCTS
WO-11280652 | 104119623 | 2023-09-19 16:27 | 2023-09-19 |  | 2023-09-19 14:23 | 47603 | 47603 | 47603 | W22404 | Complaint - NTT DATA Center, Chennai W22404 S1B16309 24040544 1600A 6E RELEASES NOT WORKING 47603 "Wing A, No 8, South Phase, Sidco Industrial Estate, MTH Road, Sai Nagar, Ambattur Industrial Estate, Chennai TN 600058 India" Santhosh 9940618336 | 2023-09-19 | 2023-09-27 12:30 | No | Warranty | NTT GLOBAL DC & CI INDIA P LTD | Wing A, No 8,south phase,Sidco Industrial Estate, MTH Road,Sai Nagar, Ambattur Industrial Estate, | Chennai | 600058 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Visited Done | Repair |  | 8- Service Completed | 2023-09-27 14:27 |  |  | 15 | INR | 15 | ENM POWER PRODUCTS
WO-11280931 | 104121789 | 2023-09-19 16:47 | 2023-09-19 |  | 2023-09-19 16:21 | Conzerv-EM6400NG-Relay, Control & Measurement - measuring, monitoring device | Conzerv-EM6400NG-Relay, Control & Measurement - measuring, monitoring device |  | 540180269622 | RE: Dr. Reddy's Laboratories Ltd. FTO Unit 3 Faulty Energy Meter, Case: 104116173, [ thread::Q7H3AQrufIyu-cYjPk3-6j4:: ] We are executing EMS in Dr Reddy FTO-3 Hyderabad where 2 EM6400 NG Energy meter found faulty special 1-2 phase voltage is not showing into display where as backside terminal having voltage. Pls Support for replacement urgently Delivery Address : FTO Unit 3 Dr. Reddy's Laboratories Ltd. Medchal Malkajgiri District.-500090,Telangana,India GST NO: 36AAACD7999Q1ZL Suprabath Reddy's DEMS +91 95500 64105 suprabath@drreddys.com EM6400NG-540180269622 EM6400NG-540180268244 | 2023-09-19 | 2023-09-21 12:00 | No | Warranty | Dr. Reddys Laboratories Ltd | FTO-3 Bachupally | Hyderabad | 500090 | Telangana | India FS ED&I CSP South Team Sumanth Electrical Services Hyderabad | Basanth Reddy_SUMANTH ELECTRICAL SERVICES HYDERABAD | Sumanth Electrical Services | Visited the Site and Inspected the Schneider Electric- METSEEM6400NGCL10RS- 02 No's. Here in our observation we found that the meter were not showing the single phase Voltage 240VACin the meter Display. So, we have replaced with New from ASC Stock after the replacement of meter. we have done programming as per Customer requirement and checked the operations which found OK. Complaint is closed. | Repair |  | 9- Service Validated | 2023-09-21 17:13 |  |  | 25 | INR | 25 | ENM POWER PRODUCTS
WO-11295893 | 104215655 | 2023-09-22 17:06 | 2023-09-22 |  | 2023-09-22 15:57 | 4LGU31000000BAA Uniflair LEONARDO DX - Air Cooled -Downflow - EC Radial fans- 40 | TDAV1822A00001 | TDAV1822A00001 | NUCW4448 | AMC P:PAC: Low Pressure alarm S:AMC | 2023-09-22 | 2023-09-25 18:18 | No | Contract | KOTAK (BKC) | Kotak Tower Plot no C-27 G Block BKC | Mumbai | 400051 | Maharashtra | India FS West1 Cooling CSP Unique India Mumbai | Mitesh Nimbayat_Unique India Mumbai | Unique India- Mumbai HBN CSP | Site visit done for low pressure alarm in circuit 1. Checked and found 0 pressure in circuit 1 and suction line depression pin faulty. Also 1nos condenser fan jammed. So we have replaced with new dipressor pin hold N2 pressure for 72hrs vaccuming and gas charging done also replaced 1nos condenser fan motor taken all parameters found normal. Now unit working ok. R407c gas charging 25kg gas supply done. | Repair |  | 8- Service Completed | 2023-09-25 18:29 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11173283 | 103596081 | 2023-08-28 17:00 | 2023-08-28 |  | 2023-08-28 16:43 | SYA12K16IXR | SYA12K16IXR | SYA12K16IXR | AD1713120743 | FW: IM02964587 KA-BNC-32 UPS BACKUP ISSUE Serial# AD1713120743 P:battery replacement S:AMC | 2023-08-28 | 2023-09-01 10:58 | No | Contract | Central Board of Excise & Customs-CBEC | Systems Manager ICES ICD WhiteField Plantation Hoskote Taluk | Bangalore | 562114 | Karnataka | India FS South1 HBN CSP Central Data SystemsPvt.Ltd. Bangalore | Ramesh Central Data SystemsPvt.Ltd. Bangalore | Central Data Systems Pvt Ltd-BLR004 | Checked the ups battery model power models issue but customer is going to purchase new ups hence we are going to use this battery mode l is going to use for other cbec customer | Repair |  | 10- Closed | 2023-09-04 18:12 |  |  | 24 | INR | 24 | ENM SECURE POWER
WO-11295989 | 104216514 | 2023-09-22 20:04 | 2023-09-22 |  | 2023-09-22 16:30 | Leonardo EvDXR407cTDAV0721A Downflow With Heater and Humidifier (SNMP Card) | TDAV0721AN003 | TDAV0721AN003 | C21917020403 | P: PAC- PAC- Water leakage issues S: AMC | 2023-09-22 | 2023-09-22 20:05 | No | Contract | Escorts Ltd. | Escorts Corporate Centre 15/5 Mathura Road | Faridabad | 121003 | Haryana | India FS North1 Cooling CSP Smart Engineering Services Delhi | Sunil Kumar Smart Engineering Services Delhi | Smart Engineering Services | VISIT AND FOUND WATER LEAKAGE AND MAIN DRAIN LINE BLOCKED, WE HAVE CLEANED THE DRAIN LINE AND COOLING COIL TRAY AND PIPE, CHECKED ALL PARAMETERS AND AMPS, NOW UNIT IS WORKING OK | Repair |  | 10- Closed | 2023-09-22 20:12 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two persons is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 48 | INR | 48 | ENM SECURE POWER
WO-11173308 | 103596565 | 2023-08-28 17:13 | 2023-08-28 |  | 2023-08-28 17:02 | APC Symmetra LX 16kVA Scalable to 16kVA N+1 Rack-mount, 220/230/240V or 380/400/ | SYAF16KXR9I | SYAF16KXR9I | QD0827260098 | FW: IM02983674 DL-DEL-01 UPS POWER MODULE ISSUE Site code: IM02983674 DL-DEL-01 UPS POWER MODULE ISSUE Serial# QD0827260098 P: UPS Not working S: AMC | 2023-08-28 | 2023-09-04 14:55 | No | Contract | Central Board of Excise & Customs-CBEC | IP Estate D Block IP Bhawan 5th Floor | New Delhi | 110002 | Delhi | India FS North1 HBN CSP HITEK BUSINESS SYSTEMS PVT LTD Delhi | Mangal M_Hitek Business Systems New Delhi | Hitek Business Systems Pvt Ltd | Engineer this site UPS check found power module fault mim fault so need to replace Engineer this site power module & Mim replaced UPS working ok | Repair |  | 10- Closed | 2023-09-04 15:08 |  |  | 15 | INR | 15 | ENM SECURE POWER
WO-11290675 | 104179512 | 2023-09-23 15:58 | 2023-09-21 |  | 2023-09-21 16:16 | METSEEM6400NGRSCL1 | METSEEM6400NGRSCL1 | METSEEM6400NGRSCL1 | 540180292381 | Re: PLEASE BOOK THE METER COMPLAINT MODEL NO EM6400 1.0 RS DIG.MFM METER SCHNEIDER NOT WORKING., Case: 104004734, [ thread::XNoBgO-DcKSR8EDt7GeQiz4:: ] Dear Sir, we have supply the material to our customer ALLIED PRODUCT Please Book the complaint at customer end. Invoice copy as attached. EM6400NG- Power on issue- 20-10-2022 ALLIED PRODUCT 24B/6 INDUSTRIAL AREA FARIDABAD MOB- 9990992583. Best Regard, ABHISHEK ENTERPRISES 1E/17,B.P.N.I.T.FARIDABAD-121001 PH-NO.0129-4020669,4020928,2423669,2427928 E-mail-abhishekentps@yahoo.co.in Visit our company website at : http://www.abhishekentps.com GST NO. 06AAVPB5647F1ZK Following attachments are linked to this email: 1.ALLIED.pdf | 2023-09-21 | 2023-09-26 18:05 | No | Warranty | ALLIED PRODUCT | 24Industrial Area, Sector 4, Ballabhgarh null | Faridabad | 121001 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the meter found display not showing, Hence faulty replaced. METSEEM6400NGRSCL1 - 1 nos Email : id not provided by customer . | Repair |  | 8- Service Completed | 2023-09-27 10:26 |  |  | 45 | INR | 45 | ENM POWER PRODUCTS
WO-11296099 | 104206795 | 2023-09-22 18:31 | 2023-09-22 |  | 2023-09-22 17:18 | Amico 6 Tr,R407c,DX,Downflow with Heater & Hum | SDA0601AN002 | SDA0601AN002 | ZK1450005333 | PAC cooling issue in server room - SE Digital AMC UNIT 1/4/2023 to 31/3/2024 P:Problem Description- PAC cooling issue in server room - ZK1450005333 & SDA0601AN002 S-AMC | 2023-09-22 | 2023-09-25 18:10 | No | Contract | Schneider Electric India Pvt Ltd | 7,8,9th floors, Elnath Bwing Prestige Tech Park, Kadubeesanahalli | Bangalore | 560103 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Akash MP_UCS Projects and services Bangalore | UCS Projects & Services | Visited site and checked for alarm due to filter drier failure so we have replaced filter drier and pressure holded and re commissioned and gas top up the unit and now the unit working normally | Repair |  | 8- Service Completed | 2023-09-25 18:16 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11295881 | 104210716 | 2023-09-22 17:01 | 2023-09-23 |  | 2023-09-22 15:50 | LC1D18BD | LC1D18BD | LC1D18BD |  | Checklist for Complaint Registration 1 Site Name & Complete Address Shibaura Machine India Private Limited, No.65, Chennai to Bangalore Highway Chembarambakkam Poonamallee Taluk Thiruvallur Distict, Chennai, Tamil Nadu 600123 Site Contact Name & Mob# Sureshkumar, Design Engineer, Ph. 9500105375 3 Site Contact Email Address** 4 Defective Product Model/Part No LC1D18BD Qty 01 No 5 Nature of Defect* SPARKING WHILE LOADING 6 Shutdown availability if applicable N A 7 Distributor Name,Invoice # & Date SHRIKRISHNA,, CHENNAI -83 AA3330050840 & 9008502572 OF 28.03.2023 8 Serial No: or DOM of the product 9 Name & phone No: of person registering the complaint B.VENKATRAMAN 97909-83346 "Points 1,2,4,5 & (7or8) are mandatory. Point 7 not applicable for Industry Business * Kindly share defect symptoms instead of ""Not working"" ** End user will receive a survey asking feedback on service" | 2023-09-22 | 2023-09-23 18:30 | No | Warranty | Shibaura Machine | Chennai | Chennai | 600123 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Visited Done | Repair |  | 9- Service Validated | 2023-09-25 11:51 |  |  | 20 | INR | 20 | ENM POWER PRODUCTS
WO-11296224 | 104166840 | 2023-09-22 18:46 | 2023-09-22 |  | 2023-09-22 18:14 | InRow RC 300mm Chilled Water 100-240V 50/60 Hz - ST | ACRC301S | ACRC301S | JK1530000825 | Fan power fault issue | 2023-09-22 | 2023-09-27 18:14 | No | Contract | Moody?S Analytics Knowledge Services India Private Limited | Elixir Chancery Building, 7th Floor,, Municipal Door No 135\1-2 Residency Road null | Bangalore | 560025 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Akash MP_UCS Projects and services Bangalore | UCS Projects & Services | Checked and found cooling issueand fan power fault alarm issue due to controller failure so we replaced the controller board and software updated and now the unit working in normally | Repair |  | 8- Service Completed | 2023-09-27 18:17 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11299977 | 104215350 | 2023-09-23 11:07 | 2023-09-23 |  | 2023-09-23 10:05 | LC1E1810M7 | LC1E1810M7 | LC1E1810M7 |  | Name of Customer:-ENSOL Site Address:-Odhav Rd, Soni ni chali,G I D C Industrial Area, Odhav, Ahmedabad, Gujarat 382350 Name of contact person at site:-Krunal Rathod Contact Phone / Mob. No:-9737933391.00 Nature of Defect:-Not Working Defective product details:-LC1E1810M7(1 QTY) Invoice no:-PSI/22000620(07/02/2023) | 2023-09-23 | 2023-09-25 14:04 | No | Warranty | ENSOL | Odhav Rd Soni ni chali G I D C Industrial Area Odhav null | Ahmedabad | 382350 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Nijesh Patel_Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the contactor stuck. customer used the contactor for star delta starter this contactor used as a star contactor main and delta contactor observed ok. On star contactor LAEN11 -8C2151 adon block used. adon block not come out from contactor becuase contactor stuck. customer used the starter for 15 kw 20 hp blower fan for customer satisfaction free replacemnet of LC1E1810M7 01 & LAEN11 recommened. problem may be due to motor short ckt or timer problem. request to customer verify motor and wiring before replcing contactor. | Repair |  | 9- Service Validated | 2023-09-25 14:04 | =S= Consig Fill up 226050097 |  | 5 | INR | 5 | ENM POWER PRODUCTS
WO-11296615 | 104220224 | 2023-09-23 13:26 | 2023-09-22 |  | 2023-09-22 18:52 | TUCVQ | TUCVQ | TUCVQ | JK2048001167 | RE: Micron PAHU issue AMC UNIT 1/1/2023 to 31/12/2023 P:Nature of complaint: Loss of air flow - JK2048001167 S-AMC | 2023-09-22 | 2023-09-23 18:20 | No | Contract | Micron Technology Operations India LLP | 4Th & 5Th Floor In Building 9, Cessna Business Park, Kadubesanahalli Village, Varthur Hobli, Outer Ring Road | Bangalore | 560103 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Akash MP_UCS Projects and services Bangalore | UCS Projects & Services | Loos of air flow alarm visited site and observed that alarm due to fuse failure so we have replaced the fuse and kept under observation unit working normally. | Repair |  | 8- Service Completed | 2023-09-23 18:26 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11301151 | 104123737 | 2023-09-25 08:57 | 2023-09-25 |  | 2023-09-23 12:44 | LV510303 | LV510303 | LV510303 |  | Checklist for Complaint Registration 1 Name of Customer Minda Industries 2 Site Address Minda Industries, Chennai 3 Name of contact person at site Mr Hari 4 Contact Phone / Mob. No: 9962149499 Email id: phari@mindainfra.com 5 Product detail 1 Nos MCCB not working at Minda Industries Chennai 6 Product Make Schneider 7 Nature of Defect Malfunctioning R phase missing 8 Shutdown availability if applicable Commissioning going on 9 Warranty status Under Warranty 10 Commissioned / Installed date 11 Serial No: or DOM of the product Picture attached 12 Name & phone No: of person registering the complaint Seema Sharma- 9958998882 Note : Point Nos: 1 to 9 are compulsory | 2023-09-23 | 2023-09-25 17:00 | No | Warranty | Mindarika Pvt Ltd | RNS 22 Sipkat Industrial Growth Center Orakadam Extn Skim Renald Supplier Part | Tiruvallur | 603204 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Visited done | Repair |  | 9- Service Validated | 2023-09-25 17:26 |  |  | 51 | INR | 51 | ENM POWER PRODUCTS
WO-11301166 | 104229443 | 2023-09-23 14:09 | 2023-09-23 |  | 2023-09-23 13:08 | LV540312 | LV540312 | LV540312 |  | Dear team, we have received a complaint for LV429407. This product does not work in "ON" condition with mccb LV540312.Kindly find the following details and arrange a visit pl. check both items . Invoice no- 2324-0731 Date-30/06/2023 Mr. Bharat prajapati Mob : 7567434705 Contact details: 62, Polaris Industrial Hub, Village - Kuha, Ahmedabad - Indore Highway, Dist : Ahmedabad -- THANKS REGARDS ASHOK PATEL POWER CONTROL AGENCY. B/10,SURYAM INDUSTRIAL PARK, NEAR TORRENT POWER SUB STATION (NIKOL), NEAR KATHWADA GIDC,ODHAV TO NIKOL S.P RING ROAD, NIKOL,AHMEDABAD - 382350. [E] powercontrol.agency@gmail.com [M]-9904056868,9624098254 GST NO - 24AAMFP5878R1Z4 VAT TIN-24072603032. CST NO-24572603032. AUTHO.DISTRIBUTOR: Schneider electric | 2023-09-23 | 2023-09-27 16:50 | No | Warranty | BMP ELECTROCRATES - Factory | 62, Polaris Industrial Hub, Kuha, | Ahmedabad | 382433 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Ritesh Prajapati_Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physicallly obsrved ok. when uv coil was installed mccb was reflecting . they replaced with shunt coil but some time the operation at shnt coil not wokring. they have installed new mccb on rite with shunt coil is working ok. check the mccb having issue on rite. observed the metel lever of the mccb mechanical heat heavily. when tried to set the lever the meter lever not broken from mccb. free replacemet of the mccb for customer satisfaction. | Repair |  | 9- Service Validated | 2023-09-28 16:51 | =S= Consig Fill up 226090730 |  | 17 | INR | 17 | ENM POWER PRODUCTS
WO-11301268 | 104216604 | 2023-09-25 11:20 | 2023-09-23 |  | 2023-09-23 16:42 | S_ATV71HU40N4Z | S_ATV71HU40N4Z | S_ATV71HU40N4Z | 8B2218235017 | complaint No. for VFD ATV71HU40N4Z_8B2218235017 (ATV71; 4KW_5HP) at our prime customer M/S Bansal Wire Industries Limited Problem :- Not Power Up | 2023-09-23 | 2023-09-28 16:48 | No | Warranty | Bansal wires | B-3 & 6 Loni Road Industrial Area Mohan Nagar | Ghaziabad | 245101 | Uttar Pradesh | India FS ED&I CSP North Team Saffron Automation Delhi | Yavnish Tyagi Saffron Automation Delhi | Saffron Automation(18001) | Check the drive and found static test is not ok with L2 and L3 phase of input is open with PC- terminal. Dismantle the drive control card and found no sign of any spark on the power board. its input diode become failed due to which drive display is not coming. We replace the faulty drive with new. Mail Id. electrical.66@bansalwire.com | Repair |  | 8- Service Completed | 2023-09-28 16:55 |  |  | 18 | INR | 18 | ENM POWER PRODUCTS
WO-11304704 | 104239307 | 2023-09-26 11:07 | 2023-09-25 |  | 2023-09-25 12:47 | LC1D32M7 | LC1D32M7 | LC1D32M7 | 1022052 | LC1D32M7 1022052 Not powering on at 220V Lochan singh 8273346387 BS Polyfill pvt ltd khasra no 129 mauza lakhanpur sikandra industrial area Agra 282007 Near lifeline school | 2023-09-25 | 2023-09-28 13:26 | No | Warranty | B S Polyfill Pvt Ltd | Khasra Number 129 Mojha Lakhanpur Sikandra Agra 282007 | Agra | 282007 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Monu Pandey_Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found contactor having plunger jam issue so we replaced. | Repair |  | 8- Service Completed | 2023-09-29 13:27 |  |  | 360 | INR | 360 | ENM POWER PRODUCTS
WO-11177633 | 103617936 | 2023-08-29 10:54 | 2023-08-29 |  | 2023-08-29 10:42 | APC Symmetra RM 4kVA Scalable to 6kVA N+1 220-240V | SYH4K6RMI | SYH4K6RMI | JD0831011082 | FW: IM02983918 CT-RPR-06 UPS NOT WORKING Site code: IM02983918 CT-RPR-06 UPS NOT WORKING Serial# JD0831011082 Standby unit: BQ1841016083 P: UPS is not working S: AMC | 2023-08-29 | 2023-09-01 16:26 | No | Contract | Central Board of Excise & Customs-CBEC | DGGSTI,4th floor RIO Lalpur,Dhamtari Road Dhamtari Road Near Fruit Market Rio Mall Building 4th Floor Raipur 492001 (C.G). | Raipur | 493111 | chhattisgarh | India FS East HBN CSP K.G.N.Computers Raipur | Samnan Siddiqui_K.G.N.Computers Raipur | KGN COMPUTERS | Main board & control board and battery replaced, replaced part no. 0J-0P5851AAQ s/n 570708AE23801093, 0J-0P7676AAQ s/n 4476761200006905, RBC44-IN, s/nB22305020128,B22305020123,Fan replace part no.0M-2809B S/N:NA oracle order: 41061197,41062116 | Repair |  | 10- Closed | 2023-09-05 11:37 |  | Main board internal humming and sparking sound so replace main board &bcontrol. | 10 | INR | 10 | ENM SECURE POWER
WO-11301182 | 104229788 | 2023-09-23 13:44 | 2023-09-23 |  | 2023-09-23 13:21 | IDAV0511AN-CPD | IDAV0511AN-CPD | IDAV0511AN-CPD | JK2302002186 | P:High temperature issue S:Onsite | 2023-09-23 | 2023-09-25 17:15 | No | Warranty | NetCracker Technology Solutions (India) Private Limited | Primeco Unioncity, Plot no. 18,19 A & 19 B, Sy.no 76 & 86 , Block B, 10TH Floor, Sadaramangala industrial area, Whitefield Main road | Bangalore | 560067 | Karnataka | India FS South3 Cooling CSP Fresco solutions Bangalore | PRIYESH P_Fresco solutions Bangalore | Fresco solutions | parameter setting changed | Repair |  | 8- Service Completed | 2023-09-25 17:20 |  |  | 20 | INR | 20 | ENM SECURE POWER
WO-11178180 | 103618203 | 2023-08-29 11:03 | 2023-08-29 |  | 2023-08-29 10:57 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | C21707001538 | Controller faulty Serial# C21707001538 P:Controller faulty S:AMC | 2023-08-29 | 2023-08-31 01:00 | No | Contract | Reliance Corporate It Park Limited | Smt.Murta Devi, W/O Late Chhote Lal, Village- Bhadi Nai Aabadi, Post-,-Jaunpur | Shahganj | 223101 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Harinder Yadav Freezeotech Airconditioning & Refrigeration Lucknow | Freezeotech Airconditioning & Refrigeration Corporation | Info Kool controller fault, part Change unit is working ok | Repair |  | 9- Service Validated | 2023-09-01 22:31 |  |  | 217 | INR | 217 | ENM SECURE POWER
WO-10990140 | 102483689 | 2023-07-13 15:13 | 2023-07-13 |  | 2023-07-13 14:58 | LD6000Tx - 6 KVA UPS with Isolation tran | LD6000TXL | LD6000TXL | 83622210100700 | DOP:26/06/2023 P commissioning C NA T NA S commissioning | 2023-07-13 | 2023-09-14 17:25 | No | Commercial Action - Sales | HDFC Bank Ltd | Grd. Floor, Near Puthencruz HP Petrol Station Puthencruz null | Ernakulam | 682308 | Kerala | India FS South2 HBN CSP PrinterPeople Cochin | Vysakht PrinterPeople Cochin | PRINTER PEOPLE-COCHIN | installation done | Commissioning & Installation | Start-up | 10- Closed | 2023-09-15 17:27 |  |  | 0 | INR | 0 | ENM SECURE POWER
WO-11178203 | 103618138 | 2023-08-29 11:52 | 2023-08-29 |  | 2023-08-29 11:04 | APC SYMMETRA RM 6KVA N+1 FRAME 220-240V EXCLUDING RAIL KIT | SYHF6KI-D | SYHF6KI-D | JD0831011130 | FW: IM02977012 UP-BSC-01 UPS BACKUP ISSUE Site code: IM02977012 UP-BSC-01 UPS BACKUP ISSUE Serial# JD0831011130 Standby unit: BQ1507000022 P: UPS battery backup issue S: AMC | 2023-08-29 | 2023-09-02 09:18 | No | Contract | Central Board of Excise & Customs-CBEC | MIG 138 Avas Vokas Avanti Nagar D M Road | Bulandshahr | 203001 | Uttar Pradesh | India FS North2 HBN CSP JDM Technologies Pvt Ltd Gaziabad | Rakesh Rathor JDM Technologies Pvt. Ltd Gaziabad | JDM Power Technologies | battery replaced,ups working ok RBC44-B22307009552 | Repair |  | 10- Closed | 2023-09-01 15:40 |  |  | 90 | INR | 90 | ENM SECURE POWER
WO-11178225 | 103618562 | 2023-08-31 12:13 | 2023-08-29 |  | 2023-08-29 11:15 | WDF0181BN002 | WDF0181BN002 | WDF0181BN002 | C21701003836 | FW: Log Repair Call Shankheshwar Under amc P:Damper Motor issue s:amc | 2023-08-29 | 2023-08-29 23:15 | No | Contract | Reliance Jio Infocomm Ltd | SHANKESHWAR TO BOLERA ROAD, NEAR BECHARAJI ROAD | SHANKESHWAR | 384246 | Gujarat | India FS West2 Cooling CSP Comfort HVAC Solutions Ahd | Rajesh Pramanik_Comfort HVAC Solutions Ahd | Comfort HVAC Solutions | Damper motor replacement done | Repair |  | 10- Closed | 2023-09-01 16:04 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 151 | INR | 151 | ENM SECURE POWER
WO-11178227 | 103618555 | 2023-09-02 09:09 | 2023-08-29 |  | 2023-08-29 11:16 | SRC6KUXIQ | SRC6KUXIQ | SRC6KUXI | BQ1510001827 | FW: UPS not working @4159_C CAMP CENTRE¦¦ Call id : INC0004317333 P:UPS Not Working S:AMC | 2023-08-29 | 2023-09-01 21:11 | No | Contract | HDFC Bank Ltd | D No 87 / 1139, Sai Durga Complex, Nagi Reddy Revenue Colony | Kurnool | 518001 | Andhra Pradesh | India FS South3 HBN CSP Param Technologies Hyderabad | LEELA PRASAD_Param Technologies Hyderabad | Param Technologies | 1st onsite Date:01-09-2023 Checked UPS it is working fine on both modes | Repair |  | 8- Service Completed | 2023-09-02 09:15 |  |  | 222 | INR | 222 | ENM SECURE POWER
WO-10990173 | 102484013 | 2023-07-21 15:55 | 2023-07-13 |  | 2023-07-13 15:09 | LD6000Tx - 6 KVA UPS with Isolation tran | LD6000TXL | LD6000TXL | 83622210100762 | DOP:26/06/2023 P commissioning C NA T NA S commissioning | 2023-07-13 | 2023-09-14 16:43 | No | Commercial Action - Sales | HDFC BANK LTD | Grd. Floor North Street Tirukkoyilur null | Villupuram | 605757 | Tamil Nadu | India FS South2 HBN CSP UpservePowerSystems Pondicherry | Kumaraguru D UpservePowerSystems Pondicherry | Upserve Power Systems-Pondicherry | Installation done ups working fine | Commissioning & Installation | Start-up | 10- Closed | 2023-09-15 16:49 |  |  | 120 | INR | 120 | ENM SECURE POWER
WO-11178730 | 103624797 | 2023-08-30 16:32 | 2023-08-29 |  | 2023-08-29 14:13 | APC Symmetra LX 8kVA Scalable to 16kVA N+1 Rack-mount, 220/230/240V or 380/400/4 | SYA8K16RMI | SYA8K16RMI | QD0738280321 | FW: IM02984919 KA/BLR/05 UPS BATTERY MODULE ISUE Site code: IM02984919 KA/BLR/05 UPS BATTERY MODULE ISUE Serial# QD0738280321 P: UPS battery module faulty S: AMC | 2023-08-29 | 2023-09-05 09:01 | No | Contract | Central Board of Excise & Customs-CBEC | KA BLR 05 CBEC Basaveshwar Building No.29/2 Crescent Road | Bangalore | 560001 | Karnataka | India FS South1 HBN CSP Central Data SystemsPvt.Ltd. Bangalore | Ramesh Central Data SystemsPvt.Ltd. Bangalore | Central Data Systems Pvt Ltd-BLR004 | Checked the ups battery issue so Battery modules or replaced the battery S/N - 5D2307T19017 / 5D2307T19043 | Repair |  | 8- Service Completed | 2023-09-05 16:24 |  |  | 20 | INR | 20 | ENM SECURE POWER
WO-11178622 | 103623163 | 2023-08-29 15:02 | 2023-08-29 |  | 2023-08-29 13:29 | APC Smart-UPS RT 10000VA 230V Harsh Environment | SURT10000XLI-CC | SURT10000XLI-CC | B21504000624 | FW: Ups not working_B21504000624_IM13370908_JC_BSTI_01 Under AMC P: Ups not working S:AMC | 2023-08-29 | 2023-09-04 10:34 | No | Contract | Reliance Jio infocomm | 1st Fl H No 680A Indian Overseas Bank Building Mauza | Basti | 272001 | Uttar Pradesh | India FS North2 HBN CSP Sun Power Systems Gorakhpur | Avinash Trivedi Sun Power Systems Gorakhpur | Sun Power Systems - Gorakhpur - Lucknow | Faulty card replaced, UPS working fine. Old Sr. No.- 5776759906266937 | Repair |  | 8- Service Completed | 2023-09-05 10:37 |  |  | 76 | INR | 76 | ENM SECURE POWER
WO-10990267 | 102485016 | 2023-07-13 16:28 | 2023-07-13 |  | 2023-07-13 15:44 | LD6000Tx - 6 KVA UPS with Isolation tran | LD6000TXL | LD6000TXL | 83622210100685 | DOP:26/06/2023 P commissioning C NA T NA S commissioning | 2023-07-13 | 2023-09-19 10:10 | No | Commercial Action - Sales | HDFC BANK LTD | Grd Floor St.Thomas College Bldg Pallichal Road Thoppumpady null | ERNAKULAM | 682005 | Kerala | India FS South2 HBN CSP PrinterPeople Cochin | Renjith PrinterPeople Cochin | PRINTER PEOPLE-COCHIN | installation done | Commissioning & Installation | Start-up | 10- Closed | 2023-09-20 10:11 |  |  | 0 | INR | 0 | ENM SECURE POWER
WO-11178672 | 103623755 | 2023-08-29 17:57 | 2023-08-29 |  | 2023-08-29 13:45 | APC Symmetra LX 8kVA Scalable to 16kVA N+1 Tower 220/230/240V or 480/400/415V | SYA8K16I | SYA8K16I | AD1626120501 | FW: IM02984599 GJ/KDL/01 UPS BACKUP ISSUE Site code: IM02984599 GJ/KDL/01 UPS BACKUP ISSUE Serial# AD1626120501 P: back up issue S: AMC | 2023-08-29 | 2023-09-04 11:15 | No | Pending Contract | Central Board of Excise & Customs-CBEC | Custom House Near Balaji Temple Commissioner of Customs | Kandla | 370210 | Gujarat | India FS West2 HBN CSP_Active Computers Gandhidham | Milan Patel_Active Computers Gandhidham | Active Computers | The calls is ups are new battery module replacement model number:- SYBT5 SN:- 5D2306T66856. /. 5D2306T66701 UPS working ok | Repair |  | 8- Service Completed | 2023-09-04 11:24 |  |  | 56 | INR | 56 | ENM SECURE POWER
WO-11303993 |  | 2023-09-26 18:15 | 2023-09-25 |  | 2023-09-25 00:02 | LEONARDO MAXDXR410A DOWNFLOW WITH HEATER & HUM ( 4LGD11A100020AA ) | TDAV2842AN40-1 | TDAV2842AN40-1 | C21832010808 | pm | 2023-09-25 | 2023-09-05 18:18 | No | Commercial Action - Sales | Webel Technology Limited | Plot-5, Block-BP, Sector - V, Salt Lake City 2nd floor ,Mani Bhander Building | Kolkata | 700091 | West Bengal | India FS East Cooling CSP Snow Point Kolkata | Jadab Patra_Snow Point Kolkata | Snow Point | DIRTY FILETR AND CONDENSER.FILTER AND CONDENSER CLEAN.ALL TERMINAL ARE TIGHT.ALL PARAMETER ARE CHECKED.MACHINE OK RUNNING. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-26 18:20 |  |  | 30 | INR | 30 | ENM SECURE POWER
WO-11303994 |  | 2023-09-26 18:31 | 2023-09-25 |  | 2023-09-25 00:03 | LEONARDO MAXDXR410A DOWNFLOW WITH HEATER & HUM ( 4LGD11A100020AA ) | TDAV2842AN40-1 | TDAV2842AN40-1 | C21837001904 | pm | 2023-09-25 | 2023-09-04 18:34 | No | Commercial Action - Sales | Webel Technology Limited | Plot-5, Block-BP, Sector - V, Salt Lake City 2nd floor ,Mani Bhander Building | Kolkata | 700091 | West Bengal | India FS East Cooling CSP Snow Point Kolkata | Jadab Patra_Snow Point Kolkata | Snow Point | DIRTY FILETR AND CONDENSER.FILTER AND CONDENSER CLEAN.ALL TERMINAL ARE TIGHT.ALL PARAMETER ARE CHECKED.MACHINE OK RUNNING. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-26 18:35 |  |  | 30 | INR | 30 | ENM SECURE POWER
WO-11303995 |  | 2023-09-26 18:37 | 2023-09-25 |  | 2023-09-25 00:04 | LEONARDO MAXDXR410A DOWNFLOW WITH HEATER & HUM ( 4LGD11A100020AA ) | TDAV2842AN40-1 | TDAV2842AN40-1 | C21836009957 | pm | 2023-09-25 | 2023-09-05 18:38 | No | Commercial Action - Sales | Webel Technology Limited | Plot-5, Block-BP, Sector - V, Salt Lake City 2nd floor ,Mani Bhander Building | Kolkata | 700091 | West Bengal | India FS East Cooling CSP Snow Point Kolkata | Jadab Patra_Snow Point Kolkata | Snow Point | DIRTY FILETR AND CONDENSER.FILTER AND CONDENSER CLEAN.ALL TERMINAL ARE TIGHT.ALL PARAMETER ARE CHECKED.MACHINE OK RUNNING. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-26 18:42 |  |  | 30 | INR | 30 | ENM SECURE POWER
WO-11178777 | 103625350 | 2023-08-29 15:27 | 2023-08-29 |  | 2023-08-29 14:35 | APC SYMMETRA RM 6KVA N+1 FRAME 220-240V EXCLUDING RAIL KIT | SYHF6KI-D | SYHF6KI-D | JD0826000731 | FW: IM02985144 TN/MAA/13 UPS BATTERY MODULE ISSUE Site code: IM02985144 TN/MAA/13 UPS BATTERY MODULE ISSUE Serial# JD0826000731 P: UPS battery module faulty S: AMC | 2023-08-29 | 2023-09-02 11:22 | No | Contract | Central Board of Excise & Customs-CBEC | Besent Nagar Rajaji Bhawan C3 C Wing IInd | Chennai | 600090 | Tamil Nadu | India FS South2 HBN CSP_Soundry Power System Chennai | SaravananMano SoundryPowerSystems Chennai | Soundry Power Systems-Chennai | BATTERY MODULE AND MIM REPLACED DONE. UPS WORKING NORMAL. battery module model-SYBT2 BATTERY MODULE S.NO-5D2313T23362;5D2313T23339 MIM MODEL-SYMIM2Q MIM S.NO-5Q1843T21129 | Repair |  | 10- Closed | 2023-09-02 12:23 |  |  | 20 | INR | 20 | ENM SECURE POWER
WO-11303996 |  | 2023-09-26 18:22 | 2023-09-25 |  | 2023-09-25 00:06 | LEONARDO MAXDXR410A DOWNFLOW WITH HEATER & HUM ( 4LGD11A100020AA ) | TDAV2842AN40-1 | TDAV2842AN40-1 | C21836009958 | pm | 2023-09-25 | 2023-09-04 18:26 | No | Commercial Action - Sales | Webel Technology Limited | Plot-5, Block-BP, Sector - V, Salt Lake City 2nd floor ,Mani Bhander Building | Kolkata | 700091 | West Bengal | India FS East Cooling CSP Snow Point Kolkata | Jadab Patra_Snow Point Kolkata | Snow Point | DIRTY FILETR AND CONDENSER.FILTER AND CONDENSER CLEAN.ALL TERMINAL ARE TIGHT.ALL PARAMETER ARE CHECKED.MACHINE OK RUNNING. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-26 18:28 |  |  | 30 | INR | 30 | ENM SECURE POWER
WO-11178823 | 103621688 | 2023-08-29 15:30 | 2023-08-29 |  | 2023-08-29 14:43 | Leonardo EV,DX,R22,,EC Fan,TDAV1021A,Downflow Without Heater & Humidifier,With M | TDAV1021AN009 | TDAV1021AN009 | ZK1334000821 | RSF found faulty in PAC 2 _ Siliguri OTN Under AMC P:RFS unit issue S:AMC | 2023-08-29 | 2023-09-01 19:26 | No | Contract | Reliance Jio Infocomm Pvt. Ltd. | Jeevan Deep Building, O/P- Bhaktinagr Opp. Salugara Monestry | Siliguri | 734001 | West Bengal | India FS East Cooling CSP Snow Point Kolkata | Jadab Patra_Snow Point Kolkata | Snow Point | WRONG POWER PHASE SEQUENCE.RSF FAULTY.RSF CHANGE.ALL PARAMETER CHECKED.MACHINE OK RUNNING. | Repair |  | 10- Closed | 2023-09-01 23:00 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 570 | INR | 570 | ENM SECURE POWER
WO-11303999 |  | 2023-09-26 17:50 | 2023-09-25 |  | 2023-09-25 00:07 | LEONARDO MAXDXR410A DOWNFLOW WITH HEATER & HUM ( 4LGD11A100020AA ) | TDAV2842AN40-1 | TDAV2842AN40-1 | C21836009926 | pm | 2023-09-25 | 2023-09-05 17:50 | No | Commercial Action - Sales | Webel Technology Limited | Plot-5, Block-BP, Sector - V, Salt Lake City 2nd floor ,Mani Bhander Building | Kolkata | 700091 | West Bengal | India FS East Cooling CSP Snow Point Kolkata | Jadab Patra_Snow Point Kolkata | Snow Point | DIRTY FILETR AND CONDENSER.FILTER AND CONDENSER CLEAN.ALL TERMINAL ARE TIGHT.ALL PARAMETER ARE CHECKED.MACHINE OK RUNNING. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-26 17:56 |  |  | 30 | INR | 30 | ENM SECURE POWER
WO-11304000 |  | 2023-09-26 18:05 | 2023-09-25 |  | 2023-09-25 00:09 | LEONARDO MAXDXR410A DOWNFLOW WITH HEATER & HUM ( 4LGD11A100020AA ) | TDAV2842AN40-1 | TDAV2842AN40-1 | C21837001903 | pm | 2023-09-25 | 2023-09-04 18:09 | No | Commercial Action - Sales | Webel Technology Limited | Plot-5, Block-BP, Sector - V, Salt Lake City 2nd floor ,Mani Bhander Building | Kolkata | 700091 | West Bengal | India FS East Cooling CSP Snow Point Kolkata | Jadab Patra_Snow Point Kolkata | Snow Point | DIRTY FILETR AND CONDENSER.FILTER AND CONDENSER CLEAN.ALL TERMINAL ARE TIGHT.ALL PARAMETER ARE CHECKED.MACHINE OK RUNNING. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-26 18:11 |  |  | 30 | INR | 30 | ENM SECURE POWER
WO-11178937 | 103626695 | 2023-08-29 16:30 | 2023-08-29 |  | 2023-08-29 15:40 | Leonardo EV,DX,R22,EC Fan,TDAV0811A,Downflow Without Heater & Humidifier | TDAV0811AN001 | TDAV0811AN001 | ZK1330006566 | RJIL BF call log - Bannerghatta road - M/s. Fresco Under AMC P:Loss of Air flow. S:AMC | 2023-08-29 | 2023-09-01 10:56 | No | Contract | Reliance Jio Infocomm Ltd. | Reliance Fresh building Bannerghatta road Kalena Agrahara | Bangalore | 560076 | Karnataka | India FS South3 Cooling CSP Fresco solutions Bangalore | PRIYESH P_Fresco solutions Bangalore | Fresco solutions | supported for the previous issue and got rectified | Repair |  | 8- Service Completed | 2023-09-01 11:01 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 22 | INR | 22 | ENM SECURE POWER
WO-11304131 | 104234690 | 2023-09-25 10:20 | 2023-09-25 |  | 2023-09-25 08:34 | Easy UPS 3S 40 kVA 400 V 3:3 UPS for external batteries | E3SUPS40KH | E3SUPS40KH | 9E2220T12613 | P:Easy UPS 3S 40KVA UPS not working S:Onsite | 2023-09-25 | 2023-09-26 15:00 | No | Warranty | Miraj Enterprises Ltd | United Panguim Mall 126/127 Hardoi Road | Sitapura | 302022 | Uttar Pradesh | India FS North2 HBN CSP BK Technologies Kanpur | Chetan Sharma B.K. Technologies Kanpur | BK Technologies | UPS chceked . All parameters are ok and working on both mode. | Repair |  | 10- Closed | 2023-09-26 15:02 |  |  | 180 | INR | 180 | ENM SECURE POWER
WO-11304136 | 104234713 | 2023-09-25 10:42 | 2023-09-25 |  | 2023-09-25 08:42 | Leonardo Ev, Dx,R407c,TDAV1422A (Double Skin),Downflow With Heater & Humidifier | TDAV1422AN005 | TDAV1422AN005 | ZK1550015527 | AMC P: Humidifier Alarm/Loss of Water S:AMC | 2023-09-25 | 2023-09-29 22:33 | No | Contract | Punjab National Bank | 5, Sansad Marg | New Delhi | 110001 | Delhi | India FS North1 Cooling CSP Smart Engineering Services Delhi | Sunil Kumar Smart Engineering Services Delhi | Smart Engineering Services | Visit and found leakage from ODU unit. we have hold N2, leakage repaired and vaccummized the machine properly, recovered gas (7kg), fresh gas refilled R-407 (11.6Kg). Changed the dryer, ODU condennsor unit repaired. We have used warnish for Outdoor unit. Checked all parameters, now unit is working ok. | Repair |  | 10- Closed | 2023-09-29 22:43 |  |  | 22 | INR | 22 | ENM SECURE POWER
WO-11304344 | 104236236 | 2023-09-25 14:19 | 2023-09-25 |  | 2023-09-25 10:58 | Amico 6 Tr,R22,Downflow with Heater & Hum. | SDA0601AN001 | SDA0601AN001 | ZK1439006239 | P:Loss of airflow AMC P:Loss of airflow S-AMC | 2023-09-25 | 2023-09-25 13:13 | No | Contract | Orient Cement Limited | #5-9-22/57/D, 2nd and 3rd Floor, G P Birla Centre, Adarsh Nagar | Hyderabad | 500063 | Telangana | India FS South1 Cooling CSP RK Cooling Enterprises Hyderabad | Kokula SREEDHAR_RK Cooling Enterprises Hyderabad | RK Cooling Enterprises | Attended the call found the unit check the all parameters unit low air flow alarm issue. We have check the FS and all parameters and FS not connecting the unit replaced the New FS controller. Now unit working Ok. | Repair |  | 8- Service Completed | 2023-09-25 13:13 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 0 | INR | 0 | ENM SECURE POWER
WO-11304356 | 104236559 | 2023-09-25 15:52 | 2023-09-25 |  | 2023-09-25 11:08 | IDAV1311AN-CPD |  |  | JK2137003724 | AMC P:Low pressure Alarm S:AMC | 2023-09-25 | 2023-09-25 20:25 | No | Contract | National Institute Of Technology Trichy | National Institute Of Technology Trichy Computer Support Dept | Tiruchirapalli | 620015 | Tamil Nadu | India FS South4 Cooling CSP Unity Air conditioning Engineers Chennai | K Karthick Unity Air-conditioning Engineers Chennai | UNITY AIRCONDITIONING ENGINEERS | Compressor failure : Now we checked and found compressor failure in unit. now we changed the new compressor and dryer, N2 pressure holding, vacuuming and recommissioning the unit observe unit working normal. | Repair |  | 10- Closed | 2023-09-26 16:31 |  |  | 327 | INR | 327 | ENM SECURE POWER
WO-11304355 | 104236514 | 2023-09-25 12:06 | 2023-09-27 |  | 2023-09-25 11:07 | SRC10KUXI | SRC10KUXI | SRC10KUXI | b22011004924 | FW: Orange Blinking. AMC UNIT 26/8/2023 to 25/8/2024 P:UPS in rack three is again started giving Battery alert.Kindly resolve this issue permanently on priority. [b22011003095 & SRC10KUXI] S-AMC | 2023-09-25 | 2023-09-27 15:02 | No | Contract | MUMBAI METRO RAIL CORPORATION | NAMTTRI Building, Plot No. R-13, ?E?- Block, Bandra Kurla Complex, Bandra (East), | Mumbai | 400051 | Maharashtra | India FS West1 HBN CSP_United Solutions Mumbai | Rohan Kamble United Solutions Mumbai | UNITED SOLUTIONS - MUMBAI | Checked the UPS and battery. One battery faulty. Checked the UPS on mains and on battery is working fine. | Repair |  | 10- Closed | 2023-09-27 15:11 |  |  | 10 | INR | 10 | ENM SECURE POWER
WO-11304390 | 104236836 | 2023-09-25 19:14 | 2023-09-25 |  | 2023-09-25 11:24 | Leonardo EVDXR407cEC FanTDAV1321ADownflow With Heater & Humidifier | TDAV1321AN002 | TDAV1321AN002 | C21743000535 | AMC P:Water leak S: AMC | 2023-09-25 | 2023-09-25 22:45 | No | Contract | MENTOR GRAPHICS (INDIA) PRIVATE LIMITED | 6-3-552,Sriram Towers,Salarpuria Sattva, Knowledge city Telangana 500081 | Hyderabad | 500081 | Telangana | India FS South3 Cooling CSP ERIC HVAC SYSTEM Hyderabad | Samir Prasad ERIC HVAC SYSTEM Hyderabad | ERIC HVAC SYSTEM | checked and find out the problem was water leakage so we have cleaned the drain line and humidity tray and now unit is working in normal condition | Repair |  | 8- Service Completed | 2023-09-26 10:58 |  |  | 30 | INR | 30 | ENM SECURE POWER
WO-11179049 | 103629213 | 2023-08-29 16:47 | 2023-08-30 |  | 2023-08-29 16:33 | Leonardo EV,DX,R22,EC Fan,TDAV0811A,Downflow Without Heater & Humidifier | TDAV0811AN001 | TDAV0811AN001 | ZK1331018862 | Create Case ID-Salem RJIL-O ring issue Under AMC P:Fan O ring damaged--ZK1331018862 S:AMC | 2023-08-29 | 2023-09-01 19:00 | No | Contract | Reliance Jio Infocomm Ltd. | Junction Main Road, Five Road Corner, Salem, Tamilnadu | Salem | 636906 | Tamil Nadu | India FS South4 Cooling CSP Unity Air conditioning Engineers Chennai | S. Karthik_ Unity Air conditioning Engineers Chennai | UNITY AIRCONDITIONING ENGINEERS | Fan O ring damaged : Now we checked and found fan O ring got damaged. Now we changed the new O ring and observe unit working normal. | Repair |  | 8- Service Completed | 2023-09-02 11:06 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 360 | INR | 360 | ENM SECURE POWER
WO-11304402 | 104236933 | 2023-09-25 12:01 | 2023-09-25 |  | 2023-09-25 11:28 | EFC MONOBLOCK 1.3TR R410A START KIT RS485 SEQ CONTROL | WDF0181BN040-1 | WDF0181BN040-1 | JK2046001731 | P:Condenser Fan Faulty - JK2046001731 & WDF0181BN040-1 AMC UNIT 1/4/2023 to 31/3/2024 P:Condenser Fan Faulty - JK2046001731 & WDF0181BN040 S-AMC | 2023-09-25 | 2023-09-29 12:00 | No | Contract | Reliance Jio Infocomm Ltd. | Ambedkar nagar | Porbandar | 224132 | Gujarat | India FS West2 Cooling CSP DECENT HVAC SYSTEM Gandhinagar | Narendra Vadhel DECENT HVAC SYSTEM Gandhinagar | DECENT HVAC SYSTEM | Complaint attend, Condenser fan replaced (> 240 Km) | Repair |  | 8- Service Completed | 2023-09-29 12:58 |  |  | 417 | INR | 417 | ENM SECURE POWER
WO-11179102 | 103630139 | 2023-08-29 17:37 | 2023-08-29 |  | 2023-08-29 17:00 | APC Smart-UPS 1000VA USB & Serial 230V | SUA1000I | SUA1000I | B21320002329 | P:Battery fault in the device Customer Request is visible on the customer portal, ensure clarity Under AMC P:Battery fault in the device C:1LIFT T:Customer S:AMC | 2023-08-29 | 2023-09-04 12:50 | No | Contract | Airports Authority of India | Chennai International Airport, next to New Terminal | Chennai | 600016 | Tamil Nadu | India FS South2 HBN CSP_Soundry Power System Chennai | SaravananMano SoundryPowerSystems Chennai | Soundry Power Systems-Chennai | UPS WORKING NORMAL. | Repair |  | 10- Closed | 2023-09-04 12:54 |  |  | 20 | INR | 20 | ENM SECURE POWER
WO-11304453 | 104236889 | 2023-09-25 17:48 | 2023-09-25 |  | 2023-09-25 11:35 | PRODUCT UNIFLAIR LEONARDO CHW TDCV4600A DFLOW WITHOUT H VER WITH DUAL SPLY AND A | TDCVQ | TDCVQ | MB2324002921 | Cooling Issue S-Onsite | 2023-09-25 | 2023-09-26 17:09 | No | Warranty | Ctrsl Datacentres Ltd, | Ctrsl Datacentres Ltd,Plot No:15/A, 2nd Main Road, Electronic City Phase-1,ISBR Law College Lane, Veerasandra Road, | Bangalore | 560100 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Akash MP_UCS Projects and services Bangalore | UCS Projects & Services | Controller board replaced software update | Repair |  | 8- Service Completed | 2023-09-26 17:12 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11179104 | 103630242 | 2023-08-29 17:39 | 2023-08-29 |  | 2023-08-29 17:03 | APC Smart-UPS 1000VA USB & Serial 230V | SUA1000I | SUA1000I | B21321000088 | P:Battery fault in the device Under AMC P:Battery fault in the device C:1LIFT T:Customer S:AMC | 2023-08-29 | 2023-09-04 12:56 | No | Contract | Airports Authority of India | Chennai International Airport, next to New Terminal | Chennai | 600016 | Tamil Nadu | India FS South2 HBN CSP_Soundry Power System Chennai | SaravananMano SoundryPowerSystems Chennai | Soundry Power Systems-Chennai | BATTERY ISSUES. | Repair |  | 10- Closed | 2023-09-04 12:59 |  |  | 20 | INR | 20 | ENM SECURE POWER
WO-11304554 | 104237414 | 2023-09-25 14:02 | 2023-09-25 |  | 2023-09-25 12:08 | PRODUCT UNIFLAIR LEONARDO CHW DOWNFLOW HXCV6200A WITHOUT H VER WITH DUAL SPLY AN | HXCVQ | HXCVQ | JK2243003721 | Abnormal noise observed in PAHU 5, at 2nd floor Server Hall. WARRANTY UNIT 15/2/2023 to 14/2/2024 PAHU-5 -2nd Floor Server Hall - JK2243003721 - Abnormal noise/vibration -JK2243003721 & HXCVQ S-ONSITE | 2023-09-25 | 2023-09-26 02:30 | No | Warranty | Yotta Infrastructure | PLOT NO 7, SECTOR KNOWLEDGE PARK V Tusiana Village, Gautam Buddha Nagar | Greater Noida | 201301 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Mohd. Shadab Freezeotech Airconditioning & Refrigeration GZB | Freezeotech Airconditioning & Refrigeration Corporation | Abnormal sound issue now found the blower bolt broked we have change the bolt unit is working ok | Repair |  | 10- Closed | 2023-09-25 19:53 |  |  | 28 | INR | 28 | ENM SECURE POWER
WO-11304616 | 104238359 | 2023-09-25 13:25 | 2023-09-26 |  | 2023-09-25 12:25 | Leonardo EV,DX,R22,TDAR1021A,Downflow With Heater & Humidifier | TDAR1021AN001 | TDAR1021AN001 | NUCX5501 | AMC P: High Condensing Pressure Alarm Issue S: AMC RDS: Need to check the Contactor, Compressor & Outdoor fan. | 2023-09-25 | 2023-09-25 20:14 | No | Contract | Cifm | Room no 10, ICD Tughlakabad,Admin building | New delhi | 110020 | Delhi | India FS North1 Cooling CSP Hitech solutions New Delhi | Arvind Kumar_Hitech solutions New Delhi | Hitech Solutions-New Delhi-Delhi | Check the unit and found alarm show in alarm history 2 times but no alarm shows when visit check all the parameters Unit working ok | Repair |  | 10- Closed | 2023-09-26 08:18 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two persons is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 39 | INR | 39 | ENM SECURE POWER
WO-11304642 |  | 2023-09-30 19:26 | 2023-09-25 |  | 2023-09-25 12:33 | Easy UPS 3S 30 kVA 400 V 3:3 UPS for external batteries | E3SUPS30KH | E3SUPS30KH | 9E2248T12249 | Start-Up Service 5X8 for (1) Easy UPS 3M 60kVA UPS | 2023-09-25 | 2023-09-28 15:15 | No | Warranty | Unitech CNC Center PVT LTD | IVC Road, Devanahalli | Bangalore | 562110 | Karnataka | India FS South1 HBN CSP UBM Autopower Pvt. Ltd Bangalore | Arun UBM Autopower Pvt. Ltd Bangalore | Autopower systems and solutions | UPS & Battery Installation Done, UPS Working Normal. | Commissioning & Installation | Start-up | 8- Service Completed | 2023-09-30 19:32 |  |  | 30 | INR | 30 | ENM SECURE POWER
WO-11304663 | 104238825 | 2023-09-26 12:53 | 2023-09-25 |  | 2023-09-25 12:37 | APC Easy UPS SRV RM 5000VA 230V with External Battery Pack for INDIA | SRV5KL-IN | SRV5KL-IN | 9S2018A41946 | UPS display backlight not working Warranty P:UPS display backlight not working S:Onsite | 2023-09-25 | 2023-09-30 15:14 | No | Warranty | Amazon sellers services pvt ltd | C/O Snowman logistics Warehouse No.8 Kanera, N.H.8 | Ahmedabad | 387540 | Gujarat | India FS West2 HBN CSP_Nutech Sales & Support Anand | Gopal Thakor Nutech Sales & Support Anand | Nutech Sales & Support | Checked and found ups display not visible and faulty so replaced display after this Ups working fine. replace Model : 0J-31-012338 serial : NA | Repair |  | 8- Service Completed | 2023-09-30 15:20 |  |  | 60 | INR | 60 | ENM SECURE POWER
WO-11304710 | 104239181 | 2023-09-26 12:54 | 2023-09-25 |  | 2023-09-25 12:53 | APC Easy UPS SRV RM 5000VA 230V with External Battery Pack for INDIA | SRV5KL-IN | SRV5KL-IN | 9S2020A52992 | FW: HGJ1 - UPS Display backlight not working, Warranty P:UPS display backlight not working S:Onsite | 2023-09-25 | 2023-09-30 15:17 | No | Warranty | Amazon sellers services pvt ltd | C/O Snowman logistics Warehouse No.8 Kanera, N.H.8 | Ahmedabad | 387540 | Gujarat | India FS West2 HBN CSP_Nutech Sales & Support Anand | Gopal Thakor Nutech Sales & Support Anand | Nutech Sales & Support | Checked and found ups display not visible and faulty so replaced display after this Ups working fine. replace Model : 0J-31-012338 serial : NA | Repair |  | 8- Service Completed | 2023-09-30 15:21 |  |  | 60 | INR | 60 | ENM SECURE POWER
WO-11293871 | 104204834 | 2023-09-22 15:17 | 2023-09-22 | We have inspected the HPFC Panel. Issue: 2P Control MCB Tripping issue. Based on the inspection, MCB is used in the HPFC control circuit. During the visit, we inspected the MCB ON&OFF with 10+ Operations, MCB Mechanical and poles continuity is healthy and MCB is working OK. MCB input present: 415V. We have done the Capacitor Manual ON & OFF Operations. During the visit, no load was present in the APFC panel due to the plant shutdown. In this case, we can suggest, from the control circuit any reverse Voltage, Neutral, Ground or overload has to be checked in the load condition. During the HPFC panel commissioning, please check the above points. | 2023-09-22 09:54 | GCR_LV_APFC | GCR_LV_APFC | GCR_LV_APFC | 224576825-10 | HPFC panel operation issue - Mars HPFC panel operation issue - Mars Mars India Pvt Limited, Wargal, Mr. Deepak Dhanraj/ Mr. Bharat Kumar 9154036033/9486881161 HPFC & AHF Troubleshooting/Communication Issue / Programming, Configuration issue/ Installation SO NO.: 224576825-10 "APFC panel AHF not operational. APFC panel control circuit MCB tripping frequently without fault " | 2023-09-22 | 2023-09-22 15:31 | No | Warranty | Mars International India Pvt. Ltd. | Survey No. 2099 ? 2103, Village Wargal, Siddipet Highway, Distt. Medak ,Telangana , | Hyderabad | 502279 | Telangana | India FS ED&I CSP South Team ENERPRO ENGINEERING SOLUTIONS Vijayawada | ES Chowdary_ENERPRO ENGINEERING SOLUTIONS VIJAYAWADA | Enerpro Engineering Solutions - 500012682 | HPFC NOT WORKING | Repair |  | 8- Service Completed | 2023-09-22 15:33 |  |  | 243 | INR | 243 | ENM POWER PRODUCTS
WO-11293898 | 104181259 | 2023-09-22 10:47 | 2023-09-22 | As per sr no product in warranty raise ZVO | 2023-09-22 10:11 | GCR_NW_CB | GCR_NW_CB | GCR_NW_CB | 10233430075 | Tulsipaper- complain of 3200 amp acb earthfault tripping. Dear sir. We had purchased one 3200 amp acb model NW32H1.Sr no 10233430075. This acb had tripped in eartfault. Pl arrange to check in earlier possible time. Pl confirm the engineer availability. Thanks. D G Thakore Tulsipaper Mills pvt Ltd. Plot 356.57.58.59. Village-kareli. Tal -Palsana Dist - Surat Gujarat Pin 394310 Contact no-8347773596. | 2023-09-22 | 2023-09-25 18:23 | No | Warranty | Tulsi Paper Mills P Ltd. | Block No.359, Kareli-Mota Road, Nr. Gangadhara Bus Stand, Bardoli, | Surat | 396130 | Gujarat | India FS ED&I CSP West Team VARDHAMAN ELECTROSOFT Vadodara | MAHENDRA SINGH VARDHAMAN ELECTROSOFT Vadodara | VARDHAMAN ELECTROSOFT | we visited the site and check the breaker physically ok . i open breaker and check the CT found ok . breaker trip at no load when Ig setting is minimum . so i found that an micrologic internal fault . | Repair |  | 8- Service Completed | 2023-09-30 18:24 | =S= Consig Fill up 226082406 |  | 60 | INR | 60 | ENM POWER PRODUCTS
WO-11295927 | 104212173 | 2023-09-22 16:54 | 2023-09-22 | MCCB output not getting | 2023-09-22 16:10 | LV563640 | LV563640 | LV563640 | 4KNO0397067 | complaint for MCCB LV563640 9970930015 Issue: Y PHASE OPEN 4KNO0397067 B 1 MIDC RANJANAGAONTALUKA SHIRUR PUNE, Maharashtra 412209, IN BEKAERT INDUSTRIES PVT LTD Yogesh 99709 30015 | 2023-09-22 | 2023-09-25 10:41 | No | Warranty | Bekaert Industries Pvt. Ltd. | B-1MIDC Ranjangaon, Tal Shirur | Pune | 412209 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Amit Patil_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the MCCB output not getting. checked output is low. the we off the MCCB & observed incoming side Y phase was loose at MCCB terminal & spreader due to loose termination. so it is not a product related issue. product found ok. | Repair |  | 9- Service Validated | 2023-09-25 10:48 | VIP FSR= No 3. FSR Request: Unavailability of the preferred FSR, need to depute Non VIP FSR(dattatray kute). |  | 55 | INR | 55 | ENM POWER PRODUCTS
WO-11301097 | 104217444 | 2023-09-23 11:37 | 2023-09-23 |  | 2023-09-23 11:22 | LC1D18M7 | LC1D18M7 | LC1D18M7 |  | Sub : COMPLAIN FOR CONTACTOR Complain for Contactor Lc1d12M7- QTY 1 NOs. & LC1D18M7 QTY 1 NOS. Lc1d18M7 - SR NO.1022086 Lc1d12M7- SR.NO.1022346 CONTACTOR COIL IS NOT OPERATE. CLIENT NAME : MAHA SHAKTI ENGINEERING CO 159/9 NARAYAN ESTATE NEAR DEEP CINEMA, CHHANI JAKATNAKA,VADODARA MOB.NO. 81419134 37 INVOICE NO:1156 DT.04.02.23 SAWANT K G Office Mobile : 9924946140 WhatsApp - 9099793665 Land Line - Tel: 0265 2361025 Thanking you Yours truly Industrial Marketing Inc. 55-Paradise Complex, Sayajigunj, Baroda - 390020 GST NO : 24AADFI0578C1ZS | 2023-09-23 | 2023-09-23 14:56 | No | Warranty | MAHA SHAKTI ENGINEERING CO | 156/9 NARAYAN ESTATE, NEAR DEEP CIMEMA CHHANI JAKAT NAKA BARODA. | Baroda | 390002 | Gujarat | India FS ED&I CSP West Team Jay Services Vadodara | Ghanshyam Kachiya_Jay Services Vadodara | Jay Services | We visited at site & chacked both contactor are physically ok. Lc1D12M7- found that plnnger jam. Now We open & rectify found test working ok. LC1D18M7- found coil. termination loose. Now We rectify & test contactor working ok. Both contactor are working ok return to contactor. | Repair |  | 9- Service Validated | 2023-09-23 14:56 |  |  | 8 | INR | 8 | ENM POWER PRODUCTS
WO-11301149 | 104219448 | 2023-09-23 14:05 | 2023-09-23 | NA | 2023-09-23 12:44 | INA_NWDOU4 | INA_NWDOU4 | INA_NWDOU4 | 213140047 | COMPLAINT NO. 405 ARROW Please refer attached excel and register the complaint. ARROW ELECTRICALS INDIA PVT. LTD LBS Marg, Oberoi Enigma, Near Jonson Company Mulund West. Nitin Ingle (9028232073) 9028232073 arrowsales@arrowelectricals.in INA_NWDOU4 FOUND FOULTY INVOICE NO.9008226607 (DATE- 24 Aug 2023) PRANOTI KASTURE Warm Regards, Nikita Pednekar __________________________________________________________________________________________ NOVATEK ELECTROENGINEERS PRIVATE LIMITED I National Distributors For Schneider Electric I ISO 9001:2008 Certified I Address (HO): 306, Prathmesh Tower, B-Wing, Senapati Bapat Marg, Lower Parel, Mumbai - 400 013. Phone: (+91-22) 2494 2080 / 2491 2634/35 I Telefax: (+91-22) 2494 2080 I | 2023-09-23 | 2023-09-26 11:36 | No | Warranty | ARROW ELECTRICALS INDIA PVT. LTD | LBS Marg, Oberoi Enigma, Near Jonson Company Mulund West. | Mumbai | 400080 | Maharashtra | India FS ED&I CSP West Team East India Power Engineers Mumbai | Sandeep Ingavale East India Power engineers Mumbai | East India Power Engineers (5043) | Visited the site & checked the UA Controller and found a normal source indication not showing on the controller & showing faulty. Replace the UA Controller & ACP plate from another running panel which is healthy working. After replacing the same problem showing on the controller. | Repair |  | 8- Service Completed | 2023-09-26 11:36 |  |  | 12 | INR | 12 | ENM POWER PRODUCTS
WO-11181314 | 103650840 | 2023-08-31 11:13 | 2023-08-30 |  | 2023-08-30 09:51 | APC Symmetra LX 16kVA N+1 Tower Frame, 220/230/240V or 380/400/415V | SYHF6KI-D | SYHF6KI-D | QD0848260656 | FW: IM02986228 RJ-JDH-14 UPS BATTERY ISSUE Site code: IM02986228 RJ-JDH-14 UPS BATTERY ISSUE Serial# QD0848260656 P: UPS battery module issue. S: AMC | 2023-08-30 | 2023-09-20 16:34 | No | Contract | CBEC | G-105, New Jodhpur Industrial Area, Jodhpur | Jodhpur | 342311 | Rajasthan | India FS North1 HBN CSP EL-TRONICS Jodhpur | Sukhdev Bhati EL-TRONICS Jodhpur | EL-TRONIC | Power module,Intelligence module and battery module replaced successfully.(SYMIM5Q-1 nos,SYPM4KIQ-2 nos,SYBT5-IN-2 nos) UPS is working ok. Stamp is not available at site. | Repair |  | 10- Closed | 2023-09-20 16:40 |  |  | 25 | INR | 25 | ENM SECURE POWER
WO-11301189 | 104229668 | 2023-09-25 18:20 | 2023-09-23 |  | 2023-09-23 13:34 | LV563319 | LV563319 | LV563319 |  | VINTECH MCCB COMPLAINT REGISTRATION - 23.09.2023 - REG., Kindly find the attached Complaint registration form. M/s.VINTECH CONTROLS & DEVICES PVT LTD., 519/2, ATHIPALAYAM ROAD, CHINNAVEDAMPATTI, COIMBATORE - 641049 MS.LATHA 9994943480 LV563319-1 NO MCCB NOT WORKING 9008617069/25.06.2023 Premanand PK - 9043006683 | 2023-09-23 | 2023-09-26 17:38 | No | Warranty | Vintech Controls & Devices Pvt. Ltd. | 519/2, Athipalayam Road, Chinnavedampatti, | Coimbatore | 641006 | Tamil Nadu | India FS ED&I CSP South Team Power Pro Engineering Services Coimbatore | KV ARUNKUMAR_POWER PRO ENGINEERIG SERVICES COIMBATORE | Powerpro Engineering Services | we have visited the site and inspected we found mccb not working due to mccb trip lever not holding we have rectified the same tesetd and found ok tested electricalay ok | Repair |  | 8- Service Completed | 2023-09-26 17:40 |  |  | 21 | INR | 21 | ENM POWER PRODUCTS
WO-11181377 | 103651323 | 2023-08-30 15:33 | 2023-08-30 |  | 2023-08-30 10:37 | SRV6KRIL-IN | SRV6KRIL-IN | SRV6KRIL-IN | 9S2319A00517 | Re: Require installation for JONES LANG LASALLE PROPERTY CONSULTANTS INDIA PVT LTD, Case: 103450574, [ thread::p7ljtN-Gf0mnEdYjp-x5RT4:: ] P:Installation S:Onsite | 2023-08-30 | 2023-09-08 12:00 | No | Commercial Action - Sales | Jones Lang LaSalle Property Consultants (India) Private Limited | Level 13, 14, Prestige Khoday Towers, No.5, Raj Bhavan Road | Bangalore | 560001 | Karnataka | India FS South1 HBN CSP EssgiInfotechPVTLTD Bangalore | Anand G EssgiInfotechPVTLTD Bangalore | Essgi Infotech-Bangalore-BLR007 | SRV6KRIL-IN With Battery Pack Installed As Per parameter UPS Is Working Normal On Both Mode AC & DC | Commissioning & Installation | Start-up | 10- Closed | 2023-09-12 12:01 |  |  | 18 | INR | 18 | ENM SECURE POWER
WO-11301230 | 104229730 | 2023-09-23 17:00 | 2023-09-23 |  | 2023-09-23 15:18 | GCR_NW_CB | GCR_NW_CB | GCR_NW_CB |  | Complaint : 2nos 24V DC shunt problem This is to inform you that, we have purchased 2nos 24V DC shunt (33659) from Novatek Electro Engineers. Both are not working. Please depute your service person to check the same and arrange for the replacement immediately. Address :- M/s. Imperial Electro Controls Pvt. Ltd. (Unit-2) Survey no. 36/1, Gollahalli extension, BDA layout Anjanapura post Bangalore 560 083 Contact person : Mr.Ashok 8310943848 Note : Video & invoice photo attached for your reference. Thanks & Regards Achutha 9902062510 | 2023-09-23 | 2023-09-28 13:22 | No | Warranty | Imperial Electro Controls Pvt. Ltd. | Survey no. 36/1, Gollahalli extension, BDA layout Anjanapura post null | Bangalore | 560083 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | C Gunasekaran_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | i had visited the site and checked the customer reported shunt coil and uv coil the problem found was 24 v ac/dc 2 nos found not actuating when input given we opened and checked found pcb burunt - checked the uv coil 200-250 ac/dc the problem found was pcb board got brunt .so we zvo booked the replacement .the new material handed over the customer checked found working ok . | Repair |  | 8- Service Completed | 2023-09-28 18:22 |  |  | 40 | INR | 40 | ENM POWER PRODUCTS
WO-11182988 | 103651061 | 2023-08-30 11:11 | 2023-08-30 |  | 2023-08-30 11:05 | LEONARDO EV,DX,R22,EC FAN,( HCM109-DANFOSS ), DOWNFLOW WITHOUT HEATER & HUMIDIFI | TDAV0811AN005 | TDAV0811AN005 | C21611010359 | Outdoor fan faulty Under AMC P: Outdoor fan faulty C: NA T: Need visit S: AMC | 2023-08-30 | 2023-08-31 03:00 | No | Contract | Reliance Jio Infocomm Ltd. | 4th Floor Vinayak Tower Commercial Property No 28-B Situated at Civil Station Mahathma Gandhi Marg | Allahabad | 211001 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Harinder Yadav Freezeotech Airconditioning & Refrigeration Lucknow | Freezeotech Airconditioning & Refrigeration Corporation | SITE VISIT FOND THE CONDENSORE FAN FAULTY NOW CHANGE THE PART UNIT WORKING OK | Repair |  | 8- Service Completed | 2023-09-03 14:26 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 200 | INR | 200 | ENM SECURE POWER
WO-11305376 | 104241064 | 2023-09-27 07:57 | 2023-09-25 |  | 2023-09-25 15:44 | MVS20N4MW2L | MVS20N4MW2L | MVS20N4MW2L |  | 1 Name of Customer M/S RK ENGINEERING AND INFRASTRUCTURE 2 Site Address 176,METTUKKADU,CHINNAMEDU, THINDAL,ERODE - 638 012. 3 Name of contact person at site GUNASEELAN.M 4 Contact Phone / Mob. No: 9626033328 5 Defective product details MVS20N4MW2L - 2000A 4P 50KA MDO ET2L ACB 6 Product Make SCHNEIDER ELECTRIC 7 Nature of Defect UV COIL NOT WORKING 8 Shutdown availability if applicable N/A 9 Warranty status UNDER WARRANTY 10 Commissioned / Installed date INVOICE NO: GS220600, (24/12/2023) 11 Serial No: or DOM of the product S1B69316 10225004 1607 PRASANNA SUBRAMANIAN (9095967603) ERISA ENERGY SOLUTIONS PVT LTD 782 1ST FLOOR,VKK MENON ROAD,NEW SIDDHAPUDUR, COIMBATORE - 641 044 Checklist for Complaint Registration Note : Point Nos: 1 to 9 are compulsory Name & phone No: of person registering the complaint 12 | 2023-09-25 | 2023-09-30 21:54 | No | Warranty | RK Engineering and Infrastructure | D.No.176, Mettukadu, Chinnamedu, Thindal, | Perundurai | 638 012 | Tamil Nadu | India FS ED&I CSP South Team Power Pro Engineering Services Coimbatore | KV ARUNKUMAR_POWER PRO ENGINEERIG SERVICES COIMBATORE | Powerpro Engineering Services | WE HAVE VISITED THE SITE AND INSPECTED WE FOUND COIL NOT WORKING DUE TO COIL MALL-FUNCTIOING WE HAVE COLLECTED THE DETAILS FOR FURTHER ACTION AND ARRAGING FOR FREE REPLACEMENT FOR THIS AND COLLECTED THE DETAILS | Repair |  | 8- Service Completed | 2023-09-30 21:55 |  |  | 135 | INR | 135 | ENM POWER PRODUCTS
WO-11305428 | 104207390 | 2023-09-25 16:30 | 2023-09-25 |  | 2023-09-25 16:02 | METSEEM6400NGPOCL1 | METSEEM6400NGPOCL1 | METSEEM6400NGPOCL1 |  | Dear Sir/Madam, We purchased a Schneider digital energy meter on 06.07.2023. For your reference invoice copy and meter pics attached please check. Present that meter not working please do needful immediately. Location Address: Retail Infra Projects Paradise Mall,Main Road, Nacharam,Hyderabad, Telangana-500076 Mobile No:8309017476,9490304050 Thanks & Regards, Retail Infra Projects Paradise Mall (SPAR Hyper Market), Nacharam Main Road, Opp. Nacharam Police Station, Nacharam, Hyderabad - 500076. Office: +919490304050 Hand: +919963444362 Mail: retailinfraprojects@gmail.com | 2023-09-25 | 2023-09-27 12:00 | No | Warranty | SPAR Hyper Market | 1-91/175/A, Bhavani Nagar, Nacharam | Hyderabad | 500076 | Telangana | India FS ED&I CSP South Team Sumanth Electrical Services Hyderabad | Venkata Prasad_SUMANTH ELECTRICAL SERVICES HYDERABAD | Sumanth Electrical Services | Visited the Site and Inspected the Schneider Electric-METSEEM6400NGPOCL1- 01 No's. Here in our observation we found that the Meter is not getting On after the proper Auxiliary Supply of 239 VAC and 415 VAC. We have replaced with New Meter and we have Checked the ON/OFF Operations which found OK. Complaint is closed. | Repair |  | 8- Service Completed | 2023-09-27 16:08 |  |  | 10 | INR | 10 | ENM POWER PRODUCTS
WO-11183053 | 103651610 | 2023-09-08 10:32 | 2023-08-30 |  | 2023-08-30 11:40 | SRV6KRIL-IN | SRV6KRIL-IN | SRV6KRIL-IN | 9S2319A00379 | Re: Require installation for JONES LANG LASALLE PROPERTY CONSULTANTS INDIA PVT LTD, Case: 103450643, [ thread::4faJqOSScNGOecocs_mfxT4:: ] P:Installation S:Onsite | 2023-08-30 | 2023-09-09 12:00 | No | Commercial Action - Sales | Jones Lang Lasalle | UB city, Vital mallaya Road, 113, Concord Block, | Bangalore | 560001 | Karnataka | India FS South1 HBN CSP EssgiInfotechPVTLTD Bangalore | Anand G EssgiInfotechPVTLTD Bangalore | Essgi Infotech-Bangalore-BLR007 | With 3 nos of batteries pack has been Installed As per Parameter UPS is Working Fine And Both AC& DC mode | Commissioning & Installation | Start-up | 10- Closed | 2023-09-12 12:10 |  |  | 18 | INR | 18 | ENM SECURE POWER
WO-11308434 | 104245849 | 2023-09-26 10:39 | 2023-09-26 |  | 2023-09-26 09:37 | C63N42D630 | C63N42D630 | C63N42D630 |  | Checklist for Complaint Registration 1 Name of Customer TECH PI SOLUTIONS 2 Site Address Plot No. 989 & 990, Syno: 302, Ram Reddy Nagar,Jeedimetla, Hyderabad - 55 3 Name of contact person at site RAJA T 4 Contact Phone / Mob. No: Mobile No.+91 9502242106 5 Defective product details 630A MCCB BREAKER, NSX MODEL 6 Nature of Defect MCCB NOT WORKING IN ON POSITION. 7 Shutdown availability if applicable Morning 08=00AM to Evening 18=00Hrs 8 Warranty status YES 9 Commissioned / Installed date Sep-23 10 Serial No: or DOM of the product TC-2023-W17-5-U2 11 Name & phone No: of person registering the complaint RAJA T , 9502242106 Note : Point Nos: 1 to 9 are compulsory | 2023-09-26 | 2023-09-26 12:00 | No | Warranty | TECH PI SOLUTIONS | Plot No 989 & 990 Syno 302 Ram Reddy Nagar Jeedimetla null | Hyderabad | 500055 | Telangana | India FS ED&I CSP South Team Sumanth Electrical Services Hyderabad | Venkata Prasad_SUMANTH ELECTRICAL SERVICES HYDERABAD | Sumanth Electrical Services | Visited Site and Inspected Schneider Electric Energy Meters and Explained About Energy KWH Kilowatt Hours and Basic Program Made As Per Site Conditions and we have not found any Quality Related Problems with Energy Meters and work order is closed | Repair |  | 8- Service Completed | 2023-09-26 18:53 |  |  | 10 | INR | 10 | ENM POWER PRODUCTS
WO-11308475 | 104267295 | 2023-09-27 15:01 | 2023-09-26 |  | 2023-09-26 10:12 | LC1D18M7 | LC1D18M7 | LC1D18M7 |  | LC1D18M7 2 nos 1023074 1023082 NO NC issue 09350675862 Surendra Singh Lokpal Industries, A6, Sector 3 noida | 2023-09-26 | 2023-09-29 16:59 | No | Warranty | Lokpal Industries | A6 Sector3 opposite Sector 16 Metro Station | Noida | 201301 | Uttar Pradesh | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the contactor found not getting on due to coil open, Hence faulty replaced LXD1N7 - 1 nos Email : id not provided by customer . | Repair |  | 8- Service Completed | 2023-09-29 17:02 |  |  | 52 | INR | 52 | ENM POWER PRODUCTS
WO-11310407 | 104267708 | 2023-09-26 17:57 | 2023-09-26 |  | 2023-09-26 12:38 | METSEEM1220HCL1 | METSEEM1220HCL1 | METSEEM1220HCL1 | 540760009002 | Dear sir , Model - METSEEM1220HCL1 Serial no. - 540760009002 , Problem- display issue We are facing a problem. Also we checked the supply on input side found 231VAC , but the problem was same , it was not showing display note - if no not reachable or anything please send some person to this address our company is on main road , there was a network problem Mr Shivam always there at site , Jaiswal granite every person knows Coustmer name - Jaiswal granite Contact person - Shivam Mishra Contact no. - 9554313632 Address - Goramachiya, Jhansi, Digara, Uttar Pradesh Pin code - 284128 Thanks & Regards Shivam Mishra | 2023-09-26 | 2023-09-27 12:51 | No | Warranty | JASWAL GRANITE | GORAMACHYA JHANSI | JHANSI | 284001 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Aman Khare_Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found meter having lose termination issue customer face the problem. now working fine. | Repair |  | 8- Service Completed | 2023-09-27 12:55 |  |  | 425 | INR | 425 | ENM POWER PRODUCTS
WO-11310974 | 104273228 | 2023-09-26 17:47 | 2023-09-27 |  | 2023-09-26 15:55 | METSEEM6436HCL10RS | METSEEM6436HCL10RS | METSEEM6436HCL10RS |  | Dear Team We have received a customer complaint in recently supplied EM6433H CL 1.0 RS485 Energy Meter - 1 No not working due to no display issue, please refer the given below details and meter image., image.png Model: EM6433H CL 1.0 RS485 Part Reference: METSEEM6433HCL10RS Qty: 1 No SL.NO: 540400047011 (Under Warranty) DOM: 03.10.22 Nature of Defect: No Display Site Address: SYMTEC ENGINEERS PVT LTD 1/36F, MGR NAGAR MAIN STREET, KOLAPAKKAM, CHENNAI- 600128. Contact Person: Deepak - 90805 10195 Your immediate action on this case will be highly appreciated. Thanks & Regards, Madhan Pandian M Mobile: 9790972275 E Power Engineering EPE Tower, Plot No. 51 & 60, Balakrishna Nagar 3rd Street, Annai Indira Nagar, Velachery, Chennai - 600 042. India. Tel : + 91 44 22432543 / 43213630 / 43213516 Fax : + 91 44 22432544 GSTIN: 33AEAPP4512Q1ZD Email : epowerengg2013@gmail.com sales@epowerengineering.in Website: www.epowerengineering.in | 2023-09-26 | 2023-09-27 17:30 | No | Warranty | Symtec Engineers (P) Ltd. | 1/36F, MGR Nagar, Kolappakkam | Chennai | 600128 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Site Visit Done | Repair |  | 8- Service Completed | 2023-09-27 18:54 |  |  | 7 | INR | 7 | ENM POWER PRODUCTS
WO-11311046 | 104278851 | 2023-09-27 16:52 | 2023-09-26 |  | 2023-09-26 16:23 | LC1E1210M7 | LC1E1210M7 | LC1E1210M7 |  | lc1d09m7 1021492 lc1e1210m7 1021216 check invoice at site for E series No output Supriya 09818036619 DP Electricals Plot no 145 146 ecotech 3rd udyog kendra 2 near watertank 201306 | 2023-09-26 | 2023-09-29 17:03 | No | Warranty | DP Electricals | Plot no 145 146 ecotech 3rd udyog kendra 2 Greater noida null | GAUTAM BUDDHA NAGAR | 201306 | Uttar Pradesh | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the contactor found phase missing, Hence faulty replaced. LC1E1210M7 - 1 nos Email : id not provided by customer. | Repair |  | 8- Service Completed | 2023-09-29 17:05 |  |  | 70 | INR | 70 | ENM POWER PRODUCTS
WO-11311062 | 104274469 | 2023-09-26 16:56 | 2023-09-26 |  | 2023-09-26 16:29 | LRE16 | LRE16 | LRE16 |  | Name of Customer:-GAYATRI ELECTRICALS Site Address:-1810/1, PADA POLE GANDHI ROAD Ahmedabad, 380001 Name of contact person at site:-Bhavin Bhai Contact Phone / Mob. No:-9898331268.00 Defective product details:-LRE16(1 QTY) Invoice no.:-PSI/23001945(17/05/2023) | 2023-09-26 | 2023-09-28 16:52 | No | Warranty | Gayatri Electricals | 4, Milancomplex, Cross Road, Chattral | Ahmedabad | 380025 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Ritesh Prajapati_Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physically osberved ok. A9KF71463 SR NO : D2318 D2318 D2938 observed dolly free ( 3 Nos ) so free replacement. LC1D09F7 SR NO : 1023236 LC1D09F7 SR NO : 102328 observed contact pole open. the contactor and checked free replacment. LC1D18F7 SR NO : 1022272 observed pole open so free replacment. | Repair |  | 9- Service Validated | 2023-09-28 16:52 | =S= Consig Fill up 226084506 |  | 15 | INR | 15 | ENM POWER PRODUCTS
WO-11183151 | 103653863 | 2023-08-30 12:37 | 2023-08-30 |  | 2023-08-30 12:19 | APC Symmetra LX 16kVA N+1 Ext. Run Tower Frame, 220/230/240V or 380/400/415V | SYAF16KXR9I | SYAF16KXR9I | QD0826360022 | FW: IM02986881 DL-DEL-33 UPS POWER MODULE ISSUE Under AMC P: Ups Power Module issue S:AMC | 2023-08-30 | 2023-09-04 12:00 | No | Contract | Central Board of Excise & Customs-CBEC | IP Estate D Block IP Bhawan 5th Floor | New Delhi | 110002 | Delhi | India FS North1 HBN CSP HITEK BUSINESS SYSTEMS PVT LTD Delhi | Mangal M_Hitek Business Systems New Delhi | Hitek Business Systems Pvt Ltd | Engineer this site UPS check found UPS power module and battery module faulty so need to replace Engineer this site power module replaced & battery calibration done UPS working ok | Repair |  | 10- Closed | 2023-09-05 10:15 |  |  | 15 | INR | 15 | ENM SECURE POWER
WO-11183162 | 103651494 | 2023-08-30 15:40 | 2023-08-30 |  | 2023-08-30 12:23 | SRV10KRIL -IN | SRV10KRIL-IN | SRV10KRIL-IN | 9S2305A00026 | Re: Require installation for JONES LANG LASALLE PROPERTY CONSULTANTS INDIA PVT LTD, Case: 103450626, [ thread::LrR8Bp5beGqpR30AnYEAQz4:: ] P:Installation S:Onsite | 2023-08-30 | 2023-09-10 12:00 | No | Commercial Action - Sales | Jones Lang LaSalle Property Consult India Private Limited | PRESTIGE TRADE TOWER, LEVEL 4, #46, PALACE ROAD, HIGH GROUNDS, SAMPANGI RAMA NAGAR, BENGALURU | Bangalore | 560001 | Karnataka | India FS South1 HBN CSP EssgiInfotechPVTLTD Bangalore | Anand G EssgiInfotechPVTLTD Bangalore | Essgi Infotech-Bangalore-BLR007 | Instalation Done Working Fine And Both AC & DC Mode | Commissioning & Installation | Start-up | 10- Closed | 2023-09-12 12:20 |  |  | 18 | INR | 18 | ENM SECURE POWER
WO-11316543 | 104279539 | 2023-09-28 11:09 | 2023-09-27 |  | 2023-09-27 13:18 | EM7230 | EM7230 | EM7230 |  | Complaint No. A/c 7230 | 2023-09-27 | 2023-09-28 11:12 | No | Warranty | Inder Metals | Jesico Colony Jagadhri | YAMUNA NAGAR | 135001 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | checked the meter found display issue. hence faulty, replaced. 30002055 -1 Nos. Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-28 14:59 |  |  | 105 | INR | 105 | ENM POWER PRODUCTS
WO-11318446 | 104249572 | 2023-09-28 16:59 | 2023-09-27 |  | 2023-09-27 21:14 | LC1E1810M7 | LC1E1810M7 | LC1E1810M7 |  | Checklist for Complaint Registration 1 Name of Customer M/s. SRG POWER CONTROL SYSTEM, 2 Site Address D/NO : 4/72B PETHANAICKEN PALAYAM, THE INDIAN PUBLIC SCHOOL, KALLIPALAYAM ANNA NAGAR, COIMBATORE - 641107 3 Name of contact person at site Mr. PURCHASE DEPARTMENT 4 Contact Phone / Mob. No: 8056815111 5 Customer's email I'd purchase@srgpower.in 6 Defective product details( Complete Product ref) LC1E1810M7 - 1NO LC1E3210M7 - 1NO 7 Product Make SCHNEIDER 8 Nature of Defect NOT WORKING 9 Shutdown availability if applicable YES 10 Commissioned / Installed date 11 Serial No: or DOM of the product/OA no./Invoice Details S.NO : 1023364, 1023173 12 Name & phone No: of person registering the complaint CHITHRA N 0422 - 4379941 Note : Point Nos: 1 to 9 are compulsory Serial no. / invoice details(Bill no, date and Supplier name) of our Distributor, a mandatory information and needs to be provided for warranty assessment. In case product is found out of warranty after visit, charges may be taken from customer. | 2023-09-27 | 2023-09-30 21:58 | No | Warranty | THE INDIAN PUBLIC SCHOOL | D/NO 4/72B PETHANAICKEN PALAYAM KALLIPALAYAM ANNA NAGAR | COIMBATORE | 641107 | Tamil Nadu | India FS ED&I CSP South Team Power Pro Engineering Services Coimbatore | KV ARUNKUMAR_POWER PRO ENGINEERIG SERVICES COIMBATORE | Powerpro Engineering Services | WE HAVE VISITED THE SITE AND INSPETED WE FOUND CONTACTOR COIL ISSUE AND NO+ NC BLOCK TERMINAL ISSUE WE HAVE COLLECTED THE DETAILS FOR FURTHER ACTION AND ARRAGING FOR FREE REPALCEMENT THIS AND COLLECETD THE DEFECTIVE | Repair |  | 8- Service Completed | 2023-09-30 21:59 |  |  | 31 | INR | 31 | ENM POWER PRODUCTS
WO-11183326 | 103651620 | 2023-08-31 09:59 | 2023-08-30 |  | 2023-08-30 13:31 | SRV10KRIL-IN | SRV10KRIL-IN | SRV10KRIL-IN | S9S2305A00055 | Re: Require installation for JONES LANG LASALLE PROPERTY CONSULTANTS INDIA PVT LTD, Case: 103633425, [ thread::0bnY6ZvZe06e7Ttu9DKDUj4:: ] P:Installation S:Onsite | 2023-08-30 | 2023-09-11 12:56 | No | Commercial Action - Sales | Jones Lang Lasalle Property Consultants India Pvt Ltd | 8th Floor Block B-2 World Tech Park DLF IT SEZ Silokhera Sector 30 | Gurgaon | 122003 | Haryana | India FS North1 HBN CSP Prokon Hi Tech Systems Gurgaon | Krishna Kumar_Prokon Hi-Tech Systems Gurgaon | Prokon Hi-Tech Systems-Gurgaon | Saturday our engineer visit at site and input / output not ready so our engineer 4 battery bank installed in rack and connected to up, but us not on . | Commissioning & Installation | Start-up | 10- Closed | 2023-09-11 13:03 | customer conformation pending |  | 0 | INR | 0 | ENM SECURE POWER
WO-11321212 | 104329942 | 2023-09-30 10:24 | 2023-09-28 |  | 2023-09-28 10:52 | LC1D12M7 | LC1D12M7 | LC1D12M7 |  | ComplaintLC1D12M7 1022123 Coil stuck Aventis elevators B114/A street no 3 mohanbaba nagar rajpur extension badarpur 110044 Shashikant +919990007676 aventiselevator@gmail.com | 2023-09-28 | 2023-09-29 18:29 | No | Warranty | AVENTIS ELEVATOR | HNO B-114/A, FIRST FLOOR, GALI NO 3 MOHAN BABA NAGAR TAJPUR EXTN BADARPUR null | New Delhi | 110044 | Delhi | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the contactor found coil burnt due abnormal voltage, Hence no replacement given to customer . Email : id not provided by customer . | Repair |  | 8- Service Completed | 2023-09-30 12:30 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11183345 | 103656880 | 2023-08-31 09:58 | 2023-09-01 |  | 2023-08-30 13:42 | SRV10KRIL-IN | SRV10KRIL-IN | SRV10KRIL-IN | S9S2305A00065 | Re: Require installation for JONES LANG LASALLE PROPERTY CONSULTANTS INDIA PVT LTD, Case: 103633425, [ thread::0bnY6ZvZe06e7Ttu9DKDUj4:: ] P:Installation S:Onsite | 2023-08-30 | 2023-09-11 12:58 | No | Commercial Action - Sales | Jones Lang Lasalle Property Consultants India Pvt Ltd | 8th Floor Block B-2 World Tech Park DLF IT SEZ Silokhera Sector 30 | Gurgaon | 122003 | Haryana | India FS North1 HBN CSP Prokon Hi Tech Systems Gurgaon | Krishna Kumar_Prokon Hi-Tech Systems Gurgaon | Prokon Hi-Tech Systems-Gurgaon | Saturday our engineer visit at site and input / output not ready so our engineer 4 battery bank installed in rack and connected to up, but us not on . | Commissioning & Installation | Start-up | 10- Closed | 2023-09-11 13:04 | customer conformation pending |  | 25 | INR | 25 | ENM SECURE POWER
WO-11322127 | 104330122 | 2023-09-28 15:10 | 2023-09-28 |  | 2023-09-28 13:27 | LC1E1210M7 | LC1E1210M7 | LC1E1210M7 |  | COMPANY NAME - Ahmedabad Electric Corporation ADDRESS- 25,37,38, Adarsh Gold Estate, B/H.Abhishree Estate, Opp.CISF Camp Odhav Ring Road,Odhav,Ahmedabad-382430 CON NUM- +91 91736 89721 CATALOG NUM SERIAL NUM PROBLEM LC1E1210M7 1022341 POLE PROBLEM | 2023-09-28 | 2023-09-29 15:30 | No | Warranty | Ahmedabad Electric Corporation | SHED NO 25 AND 38, ADARSH INDUSTRIAL PARK, B/H G.V.M.M NR, ABHI SHREE ESTATE, NAVA ODHAV | Ahmedabad | 382415 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Nijesh Patel_Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physially observed ok LC1D32M7 SR NO : 1023261 physically ok but l3 pole open observed. underwarranty status so free replacement for customer satisfaction. LC1E1210M7 SR NO : 1022063 physcially ok but give a 230 v ac supply but contactor not pick up so only coil to be replaced. GZ1E21 SR NO : 8C21194 physcially ok but on off mechsnism problem but as per sr no product out of warranty but customer give a invoice so free replacemnet for customer satisfaction. | Repair |  | 8- Service Completed | 2023-09-29 15:31 | =S= Consig Fill up 226086486 |  | 10 | INR | 10 | ENM POWER PRODUCTS
WO-11327412 | 104330568 | 2023-09-30 13:33 | 2023-09-29 |  | 2023-09-29 14:32 | EM7230 | EM7230 | EM7230 |  | Please find the attached videos of controller . We have set all parameters acc. To instruction menu but controller is not working. We purchase this controller 3 days ago from VS electricals kundli. Please provide us the solution ASAP. Our contact no. 9991334296 Address: plot no. 10 Decotech electrical pvt. Ltd. Sec. 53 phase 1 kundli Hsiidc kundli 131028 -- Thanks !! Regards Sachin kumar Maintenance Engineer 9991334296/8168142242 Office Address M/s M B Deco International. Plot No.- 38 & 39, Sec- 53, Phase- V, HSIIDC, Kundli, Sonipat- 131028. Haryana. | 2023-09-29 | 2023-09-30 13:35 | No | Warranty | MB Deco International | Plot No 118D, Sec. 56, Hsiidc Kundli | Sonipat | 131028 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Pradeep Sharma_Sharma Electric Delhi | Sharma Electric Works (16295) | checked the meter found wiring issue. set right the same, now working ok. Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-30 13:39 |  |  | 65 | INR | 65 | ENM POWER PRODUCTS
WO-11183381 | 103657767 | 2023-08-30 14:52 | 2023-08-30 |  | 2023-08-30 14:01 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | C21716001244 | PAC cooling issue Serial# C21716001244 P: PAC cooling issue S:AMC | 2023-08-30 | 2023-08-31 18:05 | No | Contract | RELIANCE JIO INFOCOMM LIMITED | Mr. Gajanan Rambhau Yene, Gat No. 239/2B/5/2B, Plot No. 4, Acharya Shri Tulsi Nagar, A/P. & Tal : Jamner, Dist : Jalgaon | Jamner | 424206 | Maharashtra | India FS West2 Cooling CSP Gale HVAC Pune | Umar Sheikh_Gale HVAC Pune | GALE HVAC | We have done R22 gas topup to the unit upto 1 kg then unit working normally | Repair |  | 10- Closed | 2023-09-02 01:07 |  |  | 432 | INR | 432 | ENM SECURE POWER
WO-11304932 | 104242559 | 2023-09-26 15:38 | 2023-09-25 |  | 2023-09-25 14:19 | LC1E65M7 | LC1E65M7 | LC1E65M7 | WH2318 | LC1E65M7 - Coil faulty WH2318 LC1E65M7 - Coil faulty WH2318 Naveen Kumar +919711730547 skaexports@gmail.com SKA Export Plot No 84, Sec 4, Manesar Gurgaon 122050 | 2023-09-25 | 2023-09-30 15:58 | No | Warranty | SKA Export | PLOT NO 84, SEC-4, IMT MANESAR null | Gurgaon | 122050 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the contactor found coil burnt , Hence faulty replaced. LC1E65M7 - 1 nos Email : id not provided by customer . | Repair |  | 8- Service Completed | 2023-09-30 16:22 |  |  | 55 | INR | 55 | ENM POWER PRODUCTS
WO-11308453 | 104230019 | 2023-09-26 13:11 | 2023-09-26 |  | 2023-09-26 09:55 | LV540021 | LV540021 | LV540021 | 102242400100092 | Re: Fwd: Complaint against MCCB Shunt contact. 103554601 [ thread::B3QPUonKcVqQDH72pS7m8z4:: ] Dear Team, Here we received a complaint against MCCB Shunt coil, its not working properly. LV540021 102242400100092 Please look into the matter, Site Address- LMR OILS LTD. LMR OILS PRIVATE LIMITED Plot No. 155-A, Industrial Area, Baikampady, Mangalore-575 011 Karnataka, India Phone: 0824-2973050 Mobile: +91 8217827482 Email: info@lmroils.com. Thanks & Regards......... Sales Department +91 8291849593/90 ARISTO ELECTROPOWER Shop No-10 & 11 , Om Sai Building, Near Pipe Line No-227, Osiya mata Complex, Reti bander Road, Kahler, Bhiwandi-421302. | 2023-09-26 | 2023-09-28 10:30 | No | Warranty | LMR OILS PRIVATE LIMITED | Plot No. 155-A, Industrial Area, Baikampady | Mangalore | 575011 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | C Gunasekaran_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported cvs 400 3p mccb and shunt coil found working ok, checked input and output voltages, there is no issue with our product. | Repair |  | 8- Service Completed | 2023-09-28 13:40 |  |  | 350 | INR | 350 | ENM POWER PRODUCTS
WO-11310377 | 104270396 | 2023-09-26 12:46 | 2023-09-26 |  | 2023-09-26 12:30 | LC1E65M7 | LC1E65M7 | LC1E65M7 | WH2307-2 | LC1E65M7 - Stuck Issue WH2307 LC1E65M7 - Stuck Issue WH2307 Mr. Ritesh +919824538679 Vidhyut sales Edit Account Name Address111,Bharvi tower,Nr.CTM,Amraiwadi,Ahmedabad Ahmedabad 380026 Gujarat | 2023-09-26 | 2023-09-29 12:54 | No | Warranty | Vidhyut sales | 111,Bharvi tower,Nr.CTM,Amraiwadi,Ahmedabad | Ahmedabad | 380026 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Mistri Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physically observed ok. LC1E65M7 SR NO : WH2306 obsrved nvc coil open so we open the coil contactore and check nvc coil but no any flashing obsreved. so for customer satisfaction only coil. | Repair |  | 8- Service Completed | 2023-09-29 12:54 | =S= Consig Fill up 226097220 |  | 17 | INR | 17 | ENM POWER PRODUCTS
WO-11310965 | 104277438 | 2023-09-27 17:04 | 2023-09-26 |  | 2023-09-26 15:52 | EM7230 | EM7230 | EM7230 | 54512190 | Reading issues in schneider electric meter (EM7200) As discussed, we assign service engineer on urgent basis. Meter images also attached for your reference. My contact details as follows We had recently installed one EM 7200 in our panel for load mentoring but meter giving contnue false reading. Actually meter is updated Vadm parameters date frequently whereas that is no change in max power. Snap of this problem attached herewith. Since it is in warranty so you are requested to send your service engineer on top priority. EM7230 54512190 29 oct 2022 Name- Satyaprakash yadav Department - Maintenance Mobile no- 6388451694 Company Name- BCH ELECTRIC LIMITED. Add.- 20/4 MATHURA ROAD FARIDABAD (121006),(HARYANA), INDIA. Website- www.bchindia.com Meter Images.- Regards Satyaprakash yadav | 2023-09-26 | 2023-09-27 17:07 | No | Warranty | BCH India | 20, NH-19Pocket B, Sector 27 null | FARIDABAD | 121006 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Pradeep Sharma_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the meter found working ok. Email : id not provided by customer . | Repair |  | 8- Service Completed | 2023-09-27 17:10 |  |  | 45 | INR | 45 | ENM POWER PRODUCTS
WO-11314577 | 104276527 | 2023-09-27 17:26 | 2023-09-28 |  | 2023-09-27 10:20 | METSEEM6436HCL10RS | METSEEM6436HCL10RS | METSEEM6436HCL10RS | 540420195169 | METSEEM6436HCL10RS-- Compliant Registration --- MAGNUM ELECTRO TECH Kindly note part reference METSEEM6436HCL10RS? 1no is not working. Complaint Form attached, please request to depute your Service Engineer to resolve the case immediately. Soft copy of the invoice materials supplied attached for your reference. Kindly need your immediate action on the case. "Salcomp Manufacturing India Pvt Ltd. Nokia Telecom SEZ,SIPCOT Industrial Park Chennai Bangalore Highway, Sriperumbudur, Tamilnadu. 602105 " 9865054061 METSEEM6436HCL10RS Uma 09972869984 Warm regards, Uma G ________________________________________________________________ Purchase & Logistics NOVATEK ELECTRO ENGINEERS PRIVATE LIMITED I National Distributors For Schneider Electric I ISO 9001:2008 Certified I Phone: (+91-80) 2321 6471/09972869984 Address: #3440, Ground & 1st floor, Service Road, R P C Layout, Vijayanagar, Bangalore - 560 040. | 2023-09-27 | 2023-09-28 17:00 | No | Warranty | Salcomp Manufacturing India Pvt Ltd | Nokia Telecom SEZ,SIPCOT Industrial Park Chennai Bangalore Highway null | Sriperumbudur | 602105 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | EM6436 meter display blinking - Replacement | Repair |  | 8- Service Completed | 2023-09-29 13:00 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11183491 | 103658239 | 2023-09-01 10:29 | 2023-08-30 |  | 2023-08-30 15:09 | SUA3000I-IND | SUA3000I-IND | SUA3000I-IND | B22025030106 | RE: APC UPS Complaint at IBS Software Repair job , Trivandrum, Case: 103511676, [ thread::DBKM-l6_dL6p5EybFamFoz4:: ] INV# CA05220001575 / SO# 50076284 / DN# 134407965 Date ? 24-Jun-2022. P:Battery change indication S:Onsite | 2023-08-30 | 2023-09-02 14:59 | No | Warranty | Thyssenkrupp Elevator India Pvt Ltd - Service Location | IBS SOFTWARE PRIVATE LIMITED, TECHNOPARK, KAZHAKOOTAM null | Trivandrum | 695581 | Kerala | India FS South2 HBN CSP YEMYEMEnterprises Trivandrum | Mahesh.B YEMYEMEnterprises Trivandrum | Yemyem Enterprises | Battery Voltage Low,Now Battery charged and Now UPS Working Fine. | Repair |  | 10- Closed | 2023-09-02 15:14 |  |  | 20 | INR | 20 | ENM SECURE POWER
WO-11317082 | 104310201 | 2023-09-28 15:02 | 2023-09-27 |  | 2023-09-27 16:18 | LC1D25M7 | LC1D25M7 | LC1D25M7 | 1022065-2 | LC1D25M7 - Phase Missing 1022065 LC1D25M7 - Phase Missing 1022065 Mantu Kumar +919958558931 Unis Footware G987, GSIDC Narela Industrial Area, Delhi 110040 | 2023-09-27 | 2023-09-28 15:04 | No | Warranty | younis footwear | G987, GSIDC Narela Industrial Area null | Delhi | 110040 | Delhi | India FS ED&I CSP North Team Sharma Electric Works Delhi | Pradeep Sharma_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mcb found phase missing due to no overload and short circuit protection used and no follow type 2 cordination, Hence no replacement given to customer . Email : id not provided by customer. | Repair |  | 8- Service Completed | 2023-09-28 15:34 |  |  | 40 | INR | 40 | ENM POWER PRODUCTS
WO-11183496 | 103660386 | 2023-09-01 10:31 | 2023-08-30 |  | 2023-08-30 15:13 | SUA3000I-IND | SUA3000I-IND | SUA3000I-IND | B22025030117 | RE: APC UPS Complaint at IBS Software Repair job , Trivandrum, Case: 103511676, [ thread::DBKM-l6_dL6p5EybFamFoz4:: ] INV# CA05220001575 / SO# 50076284 / DN# 134407965 Date ? 24-Jun-2022. P:Battery change indication S:Onsite | 2023-08-30 | 2023-09-02 15:20 | No | Warranty | Thyssenkrupp Elevator India Pvt Ltd - Service Location | IBS SOFTWARE PRIVATE LIMITED, TECHNOPARK, KAZHAKOOTAM null | Trivandrum | 695581 | Kerala | India FS South2 HBN CSP YEMYEMEnterprises Trivandrum | Mahesh.B YEMYEMEnterprises Trivandrum | Yemyem Enterprises | Battery Voltage Low,Now Battery charged and Now UPS Working Fine. | Repair |  | 10- Closed | 2023-09-02 15:24 |  |  | 20 | INR | 20 | ENM SECURE POWER
WO-11183517 | 103660827 | 2023-08-30 16:08 | 2023-08-30 |  | 2023-08-30 15:25 | WDF0181BN003 | WDF0181BN002 | WDF0181BN002 | C21752000085 | P:Cooling issue---c21752000085 Under AMC P:Cooling issue---c21752000085 S:AMC | 2023-08-30 | 2023-09-02 23:47 | No | Contract | Reliance Jio | Bhaskar Gurung-9002776398,6 Rock Ville,Dr Jakir Hossain Rd,Dist-Darjeeling | Darjeeling | 734101 | West Bengal | India FS East Cooling CSP Snow Point Kolkata | Jadab Patra_Snow Point Kolkata | Snow Point | OL/UL ALARM.RELAY KIT FAULTY AND DUMPER BROKEN.RELAY KIT AND DUMPER CHARGE.ALL PARAMETER CHECKED.MACHINE OK RUNNING. | Repair |  | 10- Closed | 2023-09-03 23:52 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 600 | INR | 600 | ENM SECURE POWER
WO-11183725 | 103664031 | 2023-08-31 17:30 | 2023-09-01 |  | 2023-08-30 17:13 | SYAF16KI | SYAF16KI | SYAF16KI | AD1649120313 | FW: IM02987319 DL-DEL-02 UPS INTELLIGENCE MODULE ISSUE Under AMC P: Ups Intelligence module issue S:AMC | 2023-08-30 | 2023-09-01 16:32 | No | Contract | Central Board of Excise & Customs-CBEC | 1st & 2nd floor, Hotel Samrat, Kautilya Marg, Chanakyapuri | Delhi | 110003 | Delhi | India FS North1 HBN CSP Martech Systems & Services New Delhi | Balwant Singh_Martech Systems & Services New Delhi | Martech Systems & Services-Gurgaon | Eng. visited at site check the ups found MIM was faulty then replaced now ups is working fine so call closed 5Q1704T71840 SYMIM5Q | Repair |  | 10- Closed | 2023-09-01 16:36 |  |  | 25 | INR | 25 | ENM SECURE POWER
WO-11183769 | 103664891 | 2023-08-30 19:22 | 2023-09-02 |  | 2023-08-30 17:38 | SRC3KUXI | SRC3KUXI | SRC3KUXI | B22242013631 | Under warranty P:NO OUTPUt C:PC T:Customer request S:Onsite | 2023-08-30 | 2023-09-02 18:49 | No | Warranty | Renew Power Pvt Ltd | 220/33KV Higrid Kakkuppi Village Vijaynagar Dist null | Bellary | 583128 | Karnataka | India FS South1 HBN CSP ABPowerSystems Gulbarga | Pradeep Pawar ABPowerSystems Gulbarga | AB Power Systems-Gulbarga-BLR020 | BDC error showing display check the ups ups is working fine battery problem inform the customer replace the battery as soon as possible battery is customer scoop | Repair |  | 10- Closed | 2023-09-02 19:11 |  |  | 400 | INR | 400 | ENM SECURE POWER
WO-11184830 | 103668163 | 2023-08-31 14:30 | 2023-08-30 |  | 2023-08-30 19:40 | EFC MONOBLOCK UNIT 1.3TR ( START RUN RELAY KIT, SEQUENCING , RS485 ) | WDF0181BN003 | WDF0181BN003 | C21902002397 | RE: [External]RE: Urgent PAC servicing required _ I-AS-MAOI-ENB-6016 / I-AS-TZPR-ILA-6027, Case: 100474154, [ Under AMC P:Abnormal Noise S:AMC | 2023-08-30 | 2023-09-01 08:21 | No | Contract | Reliance Jio Infocomm Ltd | BHABEN BORO. S/O LATE KATI RAM BORO, VILL. HATIGARH,PO. ROWTA | ODALGURI | 784508 | Assam | India FS East Cooling CSP SYSCOMP POWERSOL Guwahati | SHUBHAM PATHAK SYSCOMP POWERSOL Guwahati | SYSCOMP POWERSOL - GUWAHATI | Found supply air grill sound, supply air grill and return air grill all tightness and check all parameters, now working properly. | Repair |  | 10- Closed | 2023-09-01 23:23 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 130 | INR | 130 | ENM SECURE POWER
WO-11185917 | 103683435 | 2023-08-31 10:14 | 2023-08-31 |  | 2023-08-31 09:22 | Big Chillers | BREC | BREC | SRF032713 | Chiller-11 Source-1 & Source-2 Off DC8 Chiller-11 Source-1 & Source-2 Off DC8 P:Chiller-11 Source-1 & Source-2 Off S:AMC | 2023-08-31 | 2023-08-31 17:46 | No | Contract | Netmagic IT Services Pvt. Ltd. | DC-08, Lighthall, C Wing, Hiranandani Business Park, Saki Vihar Road, Chandivali, | MUMBAI | 400072 | Maharashtra | India FS West1 Cooling CSP Unique India Mumbai | Shameem Akhter_Unique India Mumbai | Unique India- Mumbai HBN CSP | Site visit done for noise issue. Checked and found making abnormal noise. So we have replace new fan check unit operation. Now unit working ok. | Repair |  | 10- Closed | 2023-09-01 09:53 |  |  | 51 | INR | 51 | ENM SECURE POWER
WO-11186382 | 103684497 | 2023-08-31 18:09 | 2023-08-31 |  | 2023-08-31 10:36 | WDF0181BN002 | WDF0181BN002 | WDF0181BN002 | ZK1538007298 | FW: RJIL Saswad Call Log Request Under AMC P: Damper Motor Faulty S:AMC | 2023-08-31 | 2023-09-01 18:08 | No | Contract | Reliance Jio Infocomm Ltd. | Aacharya Atre Pratisthan, Pargaon Road,Saswad null | PUNE | 411043 | Maharashtra | India FS West2 Cooling CSP Gale HVAC Pune | Gaurav More_Gale HVAC Pune | GALE HVAC | We have replaced the damper motor of the unit then unit working normally | Repair |  | 10- Closed | 2023-09-02 01:01 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 70 | INR | 70 | ENM SECURE POWER
WO-11187683 | 103686669 | 2023-08-31 16:31 | 2023-09-20 |  | 2023-08-31 12:07 | APC Symmetra LX 8kVA Scalable to 16kVA N+1 Rack-mount, 220/230/240V or 380/400/4 | SYA8K16RMI | SYA8K16RMI | QD0814180431 | FW: IM02988495 AP-HYB-29 UPS INTELLIGENCE MODULE AND BACKUP ISSUE Under AMC P: INTELLIGENCE MODULE AND BACKUP ISSUE S:AMC | 2023-08-31 | 2023-09-20 21:44 | No | Contract | Central Board of Excise & Customs-CBEC | ASSISTANT COMMISSIONER OF CENTRAL TAXES 2ND FLOOR CO-OPERATIVE BANKCOLONY,NAGOLE BANDLAGUDA ROAD NAGOLE HYDERABAD,TELANGANA | Hyderabad | 500068 | Telangana | India FS South3 HBN CSP LaserSystemsPvtLtd Secunderabad | Vasanth kumar LaserSystemsPvtLtd Secunderabad | LASER SYSTEMS LIMITED. - SECUNDERABAD - HYDERABAD | Battery Module Power Module and MIM Replaced UPS Working fine Fine | Repair |  | 8- Service Completed | 2023-09-20 21:52 | Battery Module Power Module and MIM Replaced UPS Working fine Fine |  | 20 | INR | 20 | ENM SECURE POWER
WO-11187727 | 103687496 | 2023-09-01 14:16 | 2023-08-31 |  | 2023-08-31 12:25 | APC Easy UPS Online 6000VA Indian Outlet Rackmount 230V India | SRV6KL-IN | SRV6KL-IN | 9S2147A00193 | DOP-5 JUNE 2023 P:No Bcak up 15 min C:1server T:Customer has checked with input site and bypass mode not activated and load is normal connected and no fault logs found S:Onsite | 2023-08-31 | 2023-09-01 14:18 | No | Warranty | Mac Donalds Family Restaurant | Shop no 8 , 9 Ground floor , Green memories near Vodafone tower | Ahmedabad | 382481 | Gujarat | India FS West2 HBN CSP_Mahavir Sys Power Pvt Ltd Ahmedabad | Dhaval Chauhan_Mahavir Sys Power Pvt Ltd Ahmedabad | Mahavir Sys Power Pvt Ltd | Engineer visited the site and check ups, there was problem in input side and so engineer fix it and now ups working fine | Repair |  | 8- Service Completed | 2023-09-01 14:25 |  |  | 10 | INR | 10 | ENM SECURE POWER
WO-11187755 | 103687905 | 2023-08-31 14:31 | 2023-08-31 |  | 2023-08-31 12:39 | APC Symmetra LX 16kVA N+1 Tower Frame, 220/230/240V or 380/400/415V | SYAF16KI | SYAF16KI | QD0813180005 | FW: IM02988604 TN-CBE-03 UPS ONE BATTERY MODULE ISSUE Site code: IM02988604 TN-CBE-03 UPS ONE BATTERY MODULE ISSUE Serial# QD0813180005 P: Battery module issue in ups S: AMC | 2023-08-31 | 2023-09-11 13:30 | No | Contract | Central Board of Excise & Customs-CBEC | Office of the Assistant Commissioner of customes Inland container Depot RACECOURSE ROAD 6/7, ATD Street, Coimbatore | Coimbatore | 641018 | Tamil Nadu | India FS South2 HBN CSP GRControlSystems Coimbatore | Edison V GRControlSystems Coimbatore | GR Control Systems-Coimbatore | Battery replacement done unit working fine call closed SYBT5 - 5D2306T66761 | Repair |  | 10- Closed | 2023-09-11 13:34 |  |  | 24 | INR | 24 | ENM SECURE POWER
WO-11187770 | 103688319 | 2023-08-31 17:20 | 2023-08-31 | OLD :AQ1917110160 / AD1921210274 | 2023-08-31 12:52 | APC Symmetra RM 4kVA Scalable to 6kVA N+1 220-240V | SYH4K6RMI | SYH4K6RMI | JD0826014331 | FW: IM02988424 MH-PLG-01 UPS BATTERY CHARGING ISSUE Site code: IM02988424 MH-PLG-01 UPS BATTERY CHARGING ISSUE Serial# JD0826014331 P: UPS Battery not charging S: AMC | 2023-08-31 | 2023-09-06 13:10 | No | Contract | Central Board of Excise & Customs-CBEC | Mahavir Chambers Kacheri Road Palghar HO | Palgarh | 401404 | Maharashtra | India FS West1 HBN CSP_Mahavir Sys Power Pvt Ltd Goregoan | SAGAR PANDHARE_Mahavir Sys Power Pvt Ltd Goregoan | Mahavir Sys Power Pvt Ltd -Goregaon | FSR visited customer site replace power module at customer site ups working fine . new: AQ211311010103 / AQ1751110906 | Repair |  | 8- Service Completed | 2023-09-06 13:17 |  |  | 86 | INR | 86 | ENM SECURE POWER
WO-11187917 | 103690071 | 2023-08-31 14:08 | 2023-08-31 |  | 2023-08-31 13:49 | PRODUCT UNIFLAIR TWIN COOL EV R407C EC TDTV1822A DOWNFLOW WITH H VER AND DAMP WI | TDTVQ | TDTVQ | JK2148002887 | PAC Cooling issue DOP:AMC P: PAC Cooling issue S: AMC | 2023-08-31 | 2023-09-07 17:15 | No | Contract | SAP Labs India Pvt Ltd | BLR-4, No 138, Export Promotion Industrial Park Whitefield null | Bengaluru | 560066 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Akash MP_UCS Projects and services Bangalore | UCS Projects & Services | Checked and found PAC cooling issue due to condenser fan failure so we replaced the condenser fan motor and now the unit working in normally | Repair |  | 10- Closed | 2023-09-07 17:24 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 50 | INR | 50 | ENM SECURE POWER
WO-11187930 | 103690855 | 2023-09-01 16:28 | 2023-08-31 |  | 2023-08-31 13:59 | PRODUCT UNIFLAIR LEONARDO DX IDAV0811 DOWNFLOW R410A DBL SKN WITHOUT HTR AND HUM | TDAVQ | TDAVQ | JK2105002186 | P:Water Leakage--jk2105002186 Under Warranty P:Water Leakage--jk2105002186 S:Onsite | 2023-08-31 | 2023-08-31 23:45 | No | Warranty | Reliance Jio Infocomm Ltd. | Vadodra Express Hw Tt Vadodra Express Hw Tt | Ahmedabad | 380026 | Gujarat | India FS West2 Cooling CSP Comfort HVAC Solutions Ahd | Rajesh Pramanik_Comfort HVAC Solutions Ahd | Comfort HVAC Solutions | Leakage Repairing/EEV replacement done & gas supply done | Repair |  | 10- Closed | 2023-09-01 16:34 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 36 | INR | 36 | ENM SECURE POWER
WO-11188056 | 103692150 | 2023-08-31 15:31 | 2023-08-31 |  | 2023-08-31 14:37 | APC Smart-UPS 2200VA USB & Serial 230V | SUA2200I | SUA2200I | AS1105143091 | UPS light blinking Serial# AS1105143091 P:UPS light blinking S:Pending contract | 2023-08-31 | 2023-09-01 13:48 | No | Contract | ESIC MODEL HOSPITAL | Lakshmi Nagar Sodala Hatwara Road | JAIPUR | 302006 | Rajasthan | India FS North1 HBN CSP Legacy Systems Jaipur | Kuldeep Kumawat Legacy Systems Jaipur | Legacy Systems | up sok two battery faulty found advise to replace it | Repair |  | 10- Closed | 2023-09-01 13:49 |  |  | 5 | INR | 5 | ENM SECURE POWER
WO-11188072 | 103692384 | 2023-09-04 19:28 | 2023-08-31 |  | 2023-08-31 14:40 | EFC MONOBLOCK 1.3TR R410A START KIT RS485 SEQ CONTROL | WDF0181BN040-1 | WDF0181BN040-1 | JK2050001692 | Compressor Faulty P:Compressor Faulty S:AMC | 2023-08-31 | 2023-09-06 18:00 | No | Contract | Reliance JIO Infocomm Ltd | Ram hari Daas R/o Ramjanki Sthal Ucha Mohalla Freedpur | Freedpur | 243503 | Uttar Pradesh | India FS North2 Cooling CSP DTC System Uttrakhand | Tahir DTC System Uttrakhand | DTC System | Visited and find compressor faulty, compressor replaced, leak tested, vacuumed and charged with R-410 gas. unit is working ok | Repair |  | 10- Closed | 2023-09-06 19:00 |  |  | 270 | INR | 270 | ENM SECURE POWER
WO-11188084 | 103692050 | 2023-08-31 15:34 | 2023-08-31 |  | 2023-08-31 14:44 | SUA2200I-IN | SUA2200I-IN | SUA2200I-IN | B21542001746 | UPS not working Serial# B21542001746 P:UPS not working S:AMC | 2023-08-31 | 2023-09-01 13:34 | No | Contract | ESIC MODEL HOSPITAL | Lakshmi Nagar Sodala Hatwara Road | JAIPUR | 302006 | Rajasthan | India FS North1 HBN CSP Legacy Systems Jaipur | Dilip Singh Legacy Systems Jaipur | Legacy Systems | calibration done unit working fine . | Repair |  | 10- Closed | 2023-09-01 15:03 |  |  | 5 | INR | 5 | ENM SECURE POWER
WO-11188097 | 103632636 | 2023-09-01 15:34 | 2023-08-31 |  | 2023-08-31 14:53 | MISCELLANEOUS ANCILLARY EQUIPMENT | ANC-MISC | ANC-MISC | IK-RAC-35A-SS-LE-5417 | Serial Number:B21444000922(ACSerial Number-IK-RAC-35A-5S-LE-5417) Model Number:APC / APC 6 KVA UPS Customer Site Address along with Pin Code: HDFC BANK LTD, Golei Chhak, Rairangpur, Dist. - Mayurbhanj, Odisha - 757043. Name of the contact person at site: Under AMC P:All in One Rack Ac not Power on. S:AMC | 2023-08-31 | 2023-09-02 12:09 | No | Pending Contract | HDFC Bank Ltd | HDFC Bank Branch 4067-Rairangpur Golei Chhak, Rairangpur | Mayurbhanj | 757043 | Odisha | India FS East Cooling CSP Cool Care Refrigerant Bhubaneshwar | Debasis Sahoo_Cool Care Refrigerant Bhubaneshwar | Cool Care Refrigerant | we attend the site found gas leakage from condensor unit suction flair nut crack ,leak repairing psi testing & gas charging ,now ac running ok . | Repair |  | 8- Service Completed | 2023-09-02 12:12 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 300 | INR | 300 | ENM SECURE POWER
WO-11188112 | 103691973 | 2023-09-01 17:39 | 2023-08-31 |  | 2023-08-31 14:58 | MISCELLANEOUS ANCILLARY EQUIPMENT | ANC-MISC | ANC-MISC | IK-RAC-35A-SS-LE-5423 | FW: AC cooling issue¦¦¦4032_Tubrahalli>>INC0004348144 AC Cooling Issue S:AMC | 2023-08-31 | 2023-09-01 16:30 | No | Commercial Action - Sales | HDFC Bank Ltd | HDFC Bank Ltd Tubrahalli (Varthur Road) Branch No 7 Tubrahalli Varthur Main Road PO-Whitefield Bangalore Karnataka 560066 | Bangalore | 560066 | Karnataka | India FS South3 Cooling CSP Fresco solutions Bangalore | PRIYESH P_Fresco solutions Bangalore | Fresco solutions | Discharge line leakage Leakage arrested and re-commissioning the unit with R22 Gas 4 Kg. Now the unit is working normally | Repair |  | 8- Service Completed | 2023-09-01 17:49 |  |  | 21 | INR | 21 | ENM SECURE POWER
WO-11188118 | 103657797 | 2023-09-01 15:35 | 2023-08-31 |  | 2023-08-31 15:02 | MISCELLANEOUS ANCILLARY EQUIPMENT | ANC-MISC | ANC-MISC | IK-RAC-35A-SS-BF-6006 | Serial Number:B21508000106(AC serial number- IK-RAC-35A-SS-BF-6006) Model Number:APC/APC 6 KVA UPS Customer Site Address along with Pin Code:HDFC BANK LTD,Plot Number -385, 1st Floor,Patia, Bhubaneswar, Odisha - 751024. Name of the contact person at site Under AMC P:AC cooling issue S:AMC | 2023-08-31 | 2023-09-01 19:28 | No | Pending Contract | HDFC Bank Limited | Infocity, Chandoka Industrial, | Bhubaneswar | 751024 | Odisha | India FS East Cooling CSP Cool Care Refrigerant Bhubaneshwar | Satyaranjan Rout_Cool Care Refrigerant Bhubaneshwar | Cool Care Refrigerant | we attend the site found gas leakage from discharge line near condensor ,leak repairing psi testing vaccuming & gas charging ,now ac running ok . | Repair |  | 8- Service Completed | 2023-09-01 19:30 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 16 | INR | 16 | ENM SECURE POWER
WO-11188143 | 103693463 | 2023-09-02 16:46 | 2023-08-31 |  | 2023-08-31 15:13 | MISCELLANEOUS ANCILLARY EQUIPMENT | ANC-MISC | ANC-MISC | IK-RAC-35A-SS-BF-5868 | Server room AC cooling issue Serial# IK-RAC-35A-SS-BF-5868 P: Server room AC cooling issue S: AMC | 2023-08-31 | 2023-08-31 23:00 | No | Contract | HDFC Bank Ltd | Shop No 3/4/5/6/7, First Floor, KD Plaza, Near Balaji Complex | Mehsana | 384210 | Gujarat | India FS West2 Cooling CSP Comfort HVAC Solutions Ahd | Rajesh Pramanik_Comfort HVAC Solutions Ahd | Comfort HVAC Solutions | Leakage Repairing/EEV replacement done & gas supply done | Repair |  | 10- Closed | 2023-09-02 16:51 |  |  | 114 | INR | 114 | ENM SECURE POWER
WO-11188237 | 103695171 | 2023-09-01 10:40 | 2023-09-01 |  | 2023-08-31 16:09 | LEONARDO EV,DX,R22,EC FAN,( HCM109-DANFOSS ), DOWNFLOW WITHOUT HEATER & HUMIDIFI | TDAV0811AN005 | TDAV0811AN005 | ZK1603004401 | P:ZK1603004401---Outdoor fan fault Under AMC P:ZK1603004401---Outdoor fan fault S:AMC | 2023-08-31 | 2023-09-02 23:45 | No | Contract | RELIANCE JIO INFOCOMM LIMITED | Pratapganj Sashtri nagar null | Kanpur | 208012 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Karuna Tripathi Freezeotech Airconditioning & Refrigeration Lucknow | Freezeotech Airconditioning & Refrigeration Corporation | Site visit found the condenser fan faulty now change the part unit is working ok | Repair |  | 10- Closed | 2023-09-05 10:34 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 92 | INR | 92 | ENM SECURE POWER
WO-11188404 | 103686175 | 2023-08-31 17:15 | 2023-08-31 |  | 2023-08-31 17:09 | SRV5KL-IN | SRV5KL-IN | SRV5KL-IN | 9S20202A53109 | RE: PLEASE FIND THE BELOW SERVICE CALL AND ASSIGN IT TO AHD-016 POWER SOLUTIONS . MODEL :- SRV 5KL-IN , SERIAL NUMBER :- 9S2020A53109 , TOYODA GOSEI MINDA INDIA PVT LTD . Under Warranty P:UPS DISPLAY NOT SHOWING OUTPUT . S:Onsite NOTE;INVOICE ATTACHED IN CASE | 2023-08-31 | 2023-08-31 15:53 | No | Warranty | Toyoda Gosei Minda India Pvt.Ltd | TOYODA GOSEI MINDA INDIA PVT.LTD VILLAGE DEKAWADA, TEHSIL- DETROJ, KADI - VITHALAPUR ROAD , AHMEDABAD - 382130, GUJRAT INDIA | Ahmedabad | 382130 | Gujarat | India FS West2 HBN CSP_Power Solutions Ahmedabad | Shailendra H Koshthi_Power Solutions Ahmedabad | Power Solutions | Our Engineer has visited at customer site , After checking the UPS , We have found that UPS No Problem Found and All Parameters are working okay . Now UPS is working fine okay . | Repair |  | 8- Service Completed | 2023-09-01 15:59 |  |  | 66 | INR | 66 | ENM SECURE POWER
WO-11189768 | 103705814 | 2023-09-01 10:17 | 2023-08-31 |  | 2023-08-31 21:20 | APC Easy UPS Online 6000VA Indian Outlet Rackmount 230V India | SRV6KL-IN | SRV6KL-IN | 9S2013A25345 | FW: RR : IM15378847 ¦ Store Code : TJV1 ¦ SCHNEIDER ¦ WEST BENGAL -TRENDS IN-WARRANTY P: UPS Display Issue S:Onsite | 2023-08-31 | 2023-09-02 12:20 | No | Contract | Reliance Retail Limited | RRL TST Chakdaha, Lalpur Ranjan Pally, Chakdaha, Nadia Dist | CHAKDAHA | 741222 | West Bengal | India FS East HBN CSP SYSCOMP POWERSOL Sodepur | Amit Raha SYSCOMP POWERSOL Sodepur | Syscomp Infotech Pvt Ltd - KOLKATA | Found Display faulty, Replaced display. 0J-31-012338 Now UPS is working properly. | Repair |  | 10- Closed | 2023-09-02 17:25 |  |  | 120 | INR | 120 | ENM SECURE POWER
WO-11191890 | 103717722 | 2023-09-02 10:38 | 2023-09-01 |  | 2023-09-01 10:46 | APC Smart-UPS RC 2000VA 230V Harsh Environment | SRC2000XLI-CC | SRC2000XLI-CC | B21645001330 | FW: RR : IM15427147 ¦ Store Code : TP31 ¦ SCHNEIDER ¦ KARNATAKA -DIGITAL EXPRESS MINI Under AMC P: UPS BACKUP Issue S:AMC | 2023-09-01 | 2023-09-04 14:39 | No | Contract | Reliance DX MINI | Ground Floor ,16-1-26-16/A-0-1,Court Road null | Puttur | 574201 | Karnataka | India FS South1 HBN CSP MeghaAssociates Mangalore | Prashanth Anchan MeghaAssociates Mangalore | Megha Associates-Mangalore-BLR008 | Battery needs to be replaced. | Repair |  | 10- Closed | 2023-09-04 14:43 |  |  | 65 | INR | 65 | ENM SECURE POWER
WO-11017253 | 102676183 | 2023-07-22 12:00 | 2023-07-21 |  | 2023-07-21 09:59 | SRV10KUXI-IN | SRV10KUXI-IN | SRV10KUXI-IN | 9S2313A00364 | DOP:14th July .2023 P:Installation S:Installation | 2023-07-21 | 2023-09-06 13:49 | No | Commercial Action - Sales | Director Medical Education and Training | Heads of Department Building Unit-V Khorda null | Bhubaneswar | 751015 | Odisha | India FS East HBN CSP Disha Computers Bhubneshwar | SUJIT SENAPATI Disha Computers Bhubneshwar | Disha Computers-Bhubaneshwar | INSTALLATION DONE NOW UPS OK & WORKING | Commissioning & Installation | Start-up | 10- Closed | 2023-09-06 13:51 |  |  | 10 | INR | 10 | ENM SECURE POWER
WO-11192064 | 103717876 | 2023-09-01 18:00 | 2023-09-01 |  | 2023-09-01 10:57 | APC Smart-UPS RT 10000VA 230V Harsh Environment | SURT10000XLI-CC | SURT10000XLI-CC | B21450000320 | FW: Ups not working_B21450000320_IM13373210_JC_JLUN_01 Under AMC P: Ups not working S:AMC | 2023-09-01 | 2023-09-02 15:04 | No | Contract | Reliance Jio infocomm | Prabha Utsav Palace, Mohalla Fardnavis, Churkhi Road | Jalaun | 285123 | Uttar Pradesh | India FS North2 HBN CSP BK Technologies Kanpur | Shakti kumar_B.K. Technologies Kanpur | BK Technologies | UPS OK but battery modules 4nos.. RBC44 faulty.Need to replace. | Repair |  | 10- Closed | 2023-09-02 15:09 |  |  | 132 | INR | 132 | ENM SECURE POWER
WO-11193551 | 103719768 | 2023-09-01 17:55 | 2023-09-01 |  | 2023-09-01 12:26 | EFC Monoblock unit 0.8TR, downflow with start run relay kit | WDF0101BN002 | WDF0101BN002 | ZK1520003835 | RJIL Gadchiroli Call log Request Under AMC P:Condenser Fan Faulty S:AMC | 2023-09-01 | 2023-09-05 17:09 | No | Contract | RELIANCE JIO INFOCOMM LIMITED | Reliance Jio Infocom Plot Kabra Open Plot | Gadchiroli | 442605 | Maharashtra | India FS West2 Cooling CSP Gale HVAC Pune | Yesudas Sing Gale HVAC Pune | GALE HVAC | We have replaced the condenser fan with new one then unit working normally | Repair |  | 8- Service Completed | 2023-09-05 23:17 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 900 | INR | 900 | ENM SECURE POWER
WO-11193918 | 103720841 | 2023-09-01 19:35 | 2023-09-01 |  | 2023-09-01 12:57 | Leonardo EV,DX,R22,EC Fan,TDAV0511A,Downflow Without Heater & Humidifier | TDAV0511AN001 | TDAV0511AN001 | ZK1335026329 | P:Cooling issue--zk1335026329 Under AMC P:Cooling issue--zk1335026329 S:AMC | 2023-09-01 | 2023-09-01 19:39 | No | Contract | Reliance Jio Infocomm Ltd. | Asharam Nag Tikarpada Muniguda | Rayagada | 765020 | Odisha | India FS East Cooling CSP Cool Care Refrigerant Bhubaneshwar | Debasis Sahoo_Cool Care Refrigerant Bhubaneshwar | Cool Care Refrigerant | we attend the site found gas leakage condenser coil row ,leak repairing psi testing vaccuming & gas charging ,now pac running ok . | Repair |  | 10- Closed | 2023-09-01 19:41 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 320 | INR | 320 | ENM SECURE POWER
WO-11194624 | 103723381 | 2023-09-01 16:12 | 2023-09-01 |  | 2023-09-01 14:21 | SYA8K16I | SYA8K16I | SYA8K16I | AD1649120315 | FW: IM02990458 PB-RAJ-01 UPS BATTERY ISSUE Site code: IM02990458 PB-RAJ-01 UPS BATTERY ISSUE Serial# AD1649120315 P: Battery module issue in ups S: AMC | 2023-09-01 | 2023-09-05 12:46 | No | Contract | Central Board of Excise & Customs-CBEC | Tandon Complex, Above SBI Main Branch, Calibre Market | Rajpura | 140401 | Punjab | India FS North2 HBN CSP Essar Engineers Chandigarh | Vishal Chauhan Essar Engineers Chandigarh | Essar Engineers | Checked the UPS and found SYBT5-IN , 5D2113T89004 .is defective , Replaced the defective SYBT5 with good one sr. 5D2241T81810 .Now UPS tested on load its working normal . | Repair |  | 10- Closed | 2023-09-05 12:48 |  |  | 80 | INR | 80 | ENM SECURE POWER
WO-11194765 | 103724105 | 2023-09-01 16:22 | 2023-09-06 |  | 2023-09-01 14:45 | APC Symmetra LX 16kVA N+1 Ext. Run Tower Frame 220/230/240V or 380/400/415V | SYAF16KXR9I | SYAF16KXR9I | QD1431160132 | FW: IM02990962 MH-BCT-94 UPS POWER MODULE ISSUE Site code: IM02990962 MH-BCT-94 UPS POWER MODULE ISSUE Serial# QD1431160132 P: Two power module faulty S: AMC | 2023-09-01 | 2023-09-06 17:58 | No | Contract | CBEC | Central Board of Excise and Customs, Centre 1 building, 30th Floor World Trade Centre | Mumbai | 400072 | Maharashtra | India FS West1 HBN CSP_United Solutions Mumbai | Rohan Kamble United Solutions Mumbai | UNITED SOLUTIONS - MUMBAI | 4.9- Check the UPS found power module and battery module faulty. Please need to be replaced. 6.9- Material received. 6.9- So replaced power module and battery module. Now UPS is working fine. SYPM4KIQ- AQ2008110467, AQ1803310215 SYBT5- 5D2306T66819 | Repair |  | 8- Service Completed | 2023-09-06 18:07 |  |  | 30 | INR | 30 | ENM SECURE POWER
WO-11195123 | 103726473 | 2023-09-01 16:35 | 2023-09-01 |  | 2023-09-01 16:14 | ANC-MISC | ACCH | ACCH | SRF032298 | Chiller no 11 showing fan thermal alarm Ckt no -02 Serial# SRF032298 P:Chiller no 11 showing fan thermal alarm Ckt no -02 S:warranty | 2023-09-01 | 2023-09-01 22:06 | No | Warranty | BRIDGE DATA CENTERS LLP | TTC ,Industrial Area,MIDC,Plot No-13, Digha | Mumbai | 400708 | Maharashtra | India FS West1 Cooling CSP Unique India Mumbai | Shameem Akhter_Unique India Mumbai | Unique India- Mumbai HBN CSP | Site visit done for chiller no 11, CKT 2, Fan thermal alarm, Checked and found there is Chiller fan jam and also TP Open , So we have replaced the Chiller fan with a new one, also chimney installed Run the chiller for 1 hour, taken all parameters found normal operation, Now chiller working fine. | Repair |  | 10- Closed | 2023-09-01 22:16 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11195138 | 103726884 | 2023-09-02 11:13 | 2023-09-01 |  | 2023-09-01 16:31 | SRV10KUXI-IN | SRV10KUXI-IN | SRV10KUXI-IN | 9S2310A01896 | battery volatage not displaying and no backup Serial# 9S2310A01896 P:battery volatage not displaying and no backup S:warranty | 2023-09-01 | 2023-09-04 17:20 | No | Warranty | TCSL - Siruseri Special Economic Zone, | Plot No. 1/G1, SIPCOT IT Partk, Kancheepuram Dist, | Kanchipuram | 631501 | Tamil Nadu | India FS South2 HBN CSP_Soundry Power System Chennai | SaravananMano SoundryPowerSystems Chennai | Soundry Power Systems-Chennai | UPS WORKING NORMAL. | Repair |  | 10- Closed | 2023-09-04 17:33 |  |  | 55 | INR | 55 | ENM SECURE POWER
WO-11195242 | 103727344 | 2023-09-01 18:07 | 2023-09-01 |  | 2023-09-01 17:18 | APC Symmetra LX 16kVA N,1 Ext. Run Tower Frame 220/230/240V or 380/400/415V | SYAF16KXR9I | SYAF16KXR9I | QD1531260516 | FW: KL-CLT-09 UPS POWER MODULE ISSUE Site code: KL-CLT-09 UPS POWER MODULE ISSUE Serial# QD1531260516 P: UPS power module faulty S: AMC | 2023-09-01 | 2023-09-04 16:19 | No | Contract | Central Board of Excise & Customs-CBEC | Mahe House, Panicker Road, Nadakkavu, Po Kozhikode | Kozhikode | 673011 | Kerala | India FS South2 HBN CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | ups power module faulty faulty power module replaced ups working fine SYPM4KIQ AQ2114110586 | Repair |  | 10- Closed | 2023-09-05 16:22 |  |  | 30 | INR | 30 | ENM SECURE POWER
WO-11195254 | 103728189 | 2023-09-01 19:52 | 2023-09-01 |  | 2023-09-01 17:30 | WDF0181BN001 | WDF0181BN001 | WDF0181BN001 | C21711001904 | P:Compressor is getting tripped---c21711001904 Under AMC P:Compressor is getting tripped---c21711001904 S:AMC | 2023-09-01 | 2023-09-03 22:09 | No | Contract | RELIANCE JIO INFOCOMM LIMITED | Kashi Nath Shah S/o Aditya Kumar Shah AtPost+Ps- Phulparas Distt- Madhubani | Phulparas | 847409 | Bihar | India FS East Cooling CSP Cool Care Refrigerant Bhubaneshwar | Satyaranjan Rout_Cool Care Refrigerant Bhubaneshwar | Cool Care Refrigerant | we attend the site found compresor faulty ,replaced compresor psi testing vaccuming & gas charging ,now efc running ok . | Repair |  | 10- Closed | 2023-09-04 08:36 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 311 | INR | 311 | ENM SECURE POWER
WO-11195343 | 103728833 | 2023-09-01 21:07 | 2023-09-01 |  | 2023-09-01 18:18 | Leonardo EV,DX,R22,EC Fan,TDAV0511A,Downflow Without Heater & Humidifier | TDAV0511AN001 | TDAV0511AN001 | ZK1331002720 | Create Case id-cooling issue-Coimbattore Serial# ZK1331002720 P: No Cooling issue S: AMC | 2023-09-01 | 2023-09-02 11:15 | No | Contract | Reliance Jio Infocomm Ltd. | AG2 OTN Race course Low Gudy Chamber | Coimbatore | 641001 | Tamil Nadu | India FS South4 Cooling CSP Unity Air conditioning Engineers Chennai | Raja_Unity Air-conditioning Engineers Chennai | UNITY AIRCONDITIONING ENGINEERS | L.P alarm : Now we checked and found Low suction pressure, now we observed no leakage in coil, we top up refrigerant gas and observe unit working normal. | Repair |  | 10- Closed | 2023-09-04 09:16 |  |  | 505 | INR | 505 | ENM SECURE POWER
WO-11196180 | 103730430 | 2023-09-01 21:52 | 2023-09-01 |  | 2023-09-01 18:51 | APC Easy UPS SRV RM 6000VA 230V with External Battery Pack for INDIA | SRV6KRIL-IN | SRV6KRIL-IN | 9S2149A03590 | FW: RR : IM15428346 ¦ Store Code : F1AD ¦ SCHNEIDER ¦ MAHARASHTRA -CENTRO In-warranty P: Beep sound coming in UPS S:Onsite | 2023-09-01 | 2023-09-02 15:46 | No | Warranty | Reliance Retail Limited | Bearing CTS NO 27, Final Plot No 24,Pune Municipal Corporation | Pune | 411004 | Maharashtra | India FS West1 HBN CSP_United Solutions Pune | Prashant Shitole_United Solutions Pune | United Solutions | Visited to the site checked ups on site found battery final negative cable disconnect from connecter. correct the cable tempery. checked the ups on mains and battery is working fine. | Repair |  | 8- Service Completed | 2023-09-02 15:50 |  |  | 9 | INR | 9 | ENM SECURE POWER
WO-11035443 | 102805652 | 2023-07-28 15:23 | 2023-07-26 |  | 2023-07-26 14:59 | LC1D80AM7 | LC1D80AM7 | LC1D80AM7 | 2312072500047 | Compland Dear Sir Attachment the tax invoice and Sr. No. 80 Amp. 48 voltage ac contactor not working LC1D80AM7 07032312072500047 Site address- Tulip Orange, Block B-1, Sector 70, Gurugram, Haryana 122101 Contact no. Ashok Ji 9971785987 Khalid Beg 9818137680 | 2023-07-26 | 2023-08-31 18:20 | No | Warranty | Tulip Orange | Block B-1, Sector 70 | Gurugram | 122101 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the contactor found not working Hence faulty replaced. LC1D80AE7 - 1 nos Email : id not provided by customer . | Repair |  | 9- Service Validated | 2023-09-01 16:26 |  |  | 40 | INR | 40 | ENM POWER PRODUCTS
WO-11295756 | 104190539 | 2023-09-23 16:51 | 2023-09-22 |  | 2023-09-22 14:52 | LV540630 | LV540630 | LV540630 | 44927 | Re: 400A MCC NOT WORKING Dear Schneider Team, The following materials are not working, which we have received from M/S Lalit Electricals & Electronics vide Invoice No E/22-23/5475 Dt 03-01-2023. 1) MCCB 400A 4P 36KA (LV540630) 01Nos (Not working). Kindly arrange your engineer visit to resolve the issue immediately at site:- M/S Mist Cold Sales & Services Pvt. Ltd. C/O Jubilant Biosys Ltd. Plot No.15 Knowledge Park - 2 Greater Noida Contact No. Mr Tavamani- 9944424734 Mr Ranjitji 7204387784 Thanks & Regards, Rajendra EAP Electro Projects Pvt. Ltd. Plot No.-173-174, Sector-37, Udyog Vihar, Phase-VI Gurgaon (Haryana) 122001 | 2023-09-22 | 2023-09-23 16:57 | No | Warranty | Jubilant Biosys Limited | plot no-15 knowledge park 2,Greater Noida | Noida | 201306 | Uttar Pradesh | India FS ED&I CSP North Team Sharma Electric Works Delhi | Pradeep Sharma_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mccb found working ok. Email : id not provided by customer | Repair |  | 8- Service Completed | 2023-09-23 17:02 |  |  | 65 | INR | 65 | ENM POWER PRODUCTS
WO-11296092 | 104186237 | 2023-09-25 08:48 | 2023-09-25 |  | 2023-09-22 17:14 | LC1E160M5 | LC1E160M5 | LC1E160M5 | 8C2229350122 | Power Contactor Service support LC1E160M5 - 8C2229350122 operation issue Site Address: OLYMPIA CYBERSPACE PRIVATE LIMITED Block-2, Door No. 21/22 Alandur Road, Adyar Village Guindy, Chennai-600032 Contact Person Name - KARTHIK Number - 81445 59369 | 2023-09-22 | 2023-09-25 17:00 | No | Warranty | OLYMPIA CYBERSPACE PRIVATE LIMITED | 21/22, Arulayammanpet 2nd Street, Arulayammanpet Guindy null | Chennai | 600032 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Visited Done | Repair |  | 8- Service Completed | 2023-09-26 17:42 |  |  | 15 | INR | 15 | ENM POWER PRODUCTS
WO-11296134 | 104190254 | 2023-09-25 15:20 | 2023-09-22 |  | 2023-09-22 17:34 | LC1D40AF7 | LC1D40AF7 | LC1D40AF7 |  | complaint Case No. 104099617 LC1D40AF7 - operation issue Site Address: Shree Ganga Engineers plot no-5, khasra no-38-16/2, 17-25/1, harfla road seekri, ballabgarh, faridabad-121004 Mr. Sunil Dutt Parasher M-9953147160 | 2023-09-22 | 2023-09-25 15:23 | No | Warranty | SHREE GANGA ENGINEERS | KHASRA NO-38-16/2 17-25/1, PLOT NO-5, HARFLA ROAD, SEEKRI, BALLABGARH null | Faridabad | 121004 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | checked two nos. contactor found working oK. and one contactor found PCM damaged/ broken. hence no replacement given to customer. Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-25 17:03 |  |  | 52 | INR | 52 | ENM POWER PRODUCTS
WO-11297938 | 104210479 | 2023-09-23 15:52 | 2023-09-22 |  | 2023-09-22 20:36 | C40F42D400 | C40F42D400 | C40F42D400 |  | C40F42D400? 1no Tripping Issue -- Compliant Registration --- Bhaskara Power C40F42D400 operating mechanism issue Site Address: BHASKARA power controls & services Address NO 138/1, Kadabagere Magadi Main Road, Machohalli Village, Dasanapura Hobli Bangalore Karnataka 560091 Mr. Ravishankar B S - 7619217527 | 2023-09-22 | 2023-09-25 16:24 | No | Warranty | Bhaskara Power Controls and services | No.138/1, Kadabagere Cross, Magadi Main Road, Machohalli Village, Dasanapura Hobli, | Bangalore | 560091 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Nagaraja G_P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | Visited the site and inspected the below mentioned. 1)Ref:C40F42D400 S/N:1022063 = 01 No, MCCB shunt trip operation was not operating properly, because of MCCB inside coil reset lever was bended from the customer side and coil supporter was also missing. So we rejected the warranty replacement | Repair |  | 8- Service Completed | 2023-09-25 16:26 |  |  | 52 | INR | 52 | ENM POWER PRODUCTS
WO-11199061 |  | 2023-09-02 10:35 | 2023-09-02 |  | 2023-09-02 09:45 | LEONARDO EVDXR410A DOWNFLOW WITH HEATER & HUM ( 4LGD11A100020AA ) | TDAV1021AN40-1 | TDAV1021AN40-1 | JK2302003591 | pm | 2023-09-02 | 2023-09-02 18:25 | No | Commercial Action - Service Ops | Concor | ICD Road, Near Tughlakabad Railway Station, Lal Kuan, Tughlakabad null | Delhi | 110044 | Delhi | India FS North1 Cooling CSP Smart Engineering Services Delhi | Taranjeet Singh_Smart Engineering Services Delhi | Smart Engineering Services | REGUL AR PM | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-02 18:27 |  |  | 28 | INR | 28 | ENM SECURE POWER
WO-11297976 | 104212495 | 2023-09-25 15:42 | 2023-09-22 |  | 2023-09-22 20:52 | MVS08N4MW6A | MVS08N4MW6A | MVS08N4MW6A | 1022143 | Complaint of Air Circuit Breaker at Bundi MVS08N4MW6A 1022143 UV coil operation issue Site Address: R B ASSOCIATES NEAR SILOR CHORAHA FLYOVER, KOTA JAIPUR N.H. 52, CHHATARPURA BUNDI-323001 CONTACT PERSON ? Mr. Vinay Kumar (90452-89781) | 2023-09-22 | 2023-09-30 15:27 | No | Warranty | R B ASSOCIATES | NEAR SILOR CHORAHA FLYOVER, KOTA JAIPUR N.H. 52, CHHATARPURA | Bundi | 323001 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | Checked the UV coil found not operating , Hence faulty replaced. 33671 - 1 nos Email : id not provided by customer . | Repair |  | 8- Service Completed | 2023-09-30 15:29 |  |  | 250 | INR | 250 | ENM POWER PRODUCTS
WO-11299968 | 104214879 | 2023-09-23 11:06 | 2023-09-23 |  | 2023-09-23 09:47 | LC1D18 | LC1D18 | LC1D18 | 102318 | Name of Customer:-INDUCTOTHERM INDIA PVT LTD Site Address:-PLOT NO SM 6, SANAND GIDC,PHASE-II, B/H. COLGATE PALMOLIVE,BOL-VILLAGE Ahmedabad, 382170 Name of contact person at site:-Yagnik Contact Phone / Mob. No:-7227899615.00 Defective product details:-L | 2023-09-23 | 2023-09-25 14:05 | No | Warranty | Inductotherm India Pvt. Ltd. | PLOT NO SM 6, SANAND GIDC, PHASE-II, B/H. COLGATE PALMOLIVE,, BOL-VILLAGE | Ahmedabad | 382170 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Sitpuriya_Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physically observed ok. LC1D18BD SR NO : 1023152 observed ok. For customer satisfaction free replacement. | Repair |  | 9- Service Validated | 2023-09-25 14:06 | =S= Consig Fill up 226078866 |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11199063 |  | 2023-09-02 10:36 | 2023-09-02 |  | 2023-09-02 09:47 | LEONARDO EVDXR410A DOWNFLOW WITH HEATER & HUM ( 4LGD11A100020AA ) | TDAV1021AN40-1 | TDAV1021AN40-1 | JK2248004556 | pm | 2023-09-02 | 2023-09-02 18:28 | No | Commercial Action - Service Ops | Concor | ICD Road, Near Tughlakabad Railway Station, Lal Kuan, Tughlakabad null | Delhi | 110044 | Delhi | India FS North1 Cooling CSP Smart Engineering Services Delhi | Taranjeet Singh_Smart Engineering Services Delhi | Smart Engineering Services | REGULAR PM | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-02 18:31 |  |  | 28 | INR | 28 | ENM SECURE POWER
WO-11300972 | 104188218 | 2023-09-23 11:58 | 2023-09-23 |  | 2023-09-23 10:52 | EZEROTE | GCR_EZC_KR | GCR_EZC_KR |  | EZC RHOM PROBLEM. EZEROTE locking issue Site Address: G.K CONTROLS, Sy. No.16/8,Gulakamale Village, T.K. Falls Road, Kaggalipura Off Kanakapura Road, Bengaluru-560 116. Office Ph: 81053 18845 Mr. Ashvath Bhat M-9900280965 | 2023-09-23 | 2023-09-23 15:05 | No | Warranty | G.KCONTROLS | Sy. No.16/8,Gulakamale Village,T.K. Falls Road,Kaggalipura,Off Kanakapura Road | Bangalore | 560116 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Nagaraja G_P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | Inspected and found 1)Ref:EZEROTE S/N:2023 = 2 No's, MCCB with extended rotary handle ON/OFF tested and some as explained to customer and after tested working found ok. | Repair |  | 8- Service Completed | 2023-09-23 15:06 |  |  | 32 | INR | 32 | ENM POWER PRODUCTS
WO-11301079 | 104206964 | 2023-09-25 10:10 | 2023-09-23 | MCCB Hardware Problem | 2023-09-23 11:02 | LV438372 | LV438372 | LV438372 | NN-2022-W41-2 | Complaint for failure of BREAKER NSX630F DC 4P LV438372 NN-2022-W41-2 operation issue Site Address: Tata Communication Ltd., Dighi Alandi road, Dighi Pune. Mr. Shriniwas Solanke 9730591691 Mr. Ashish Gaikwad 7276473727. | 2023-09-23 | 2023-09-25 15:51 | No | Warranty | Tata Communication Ltd | TTDC, Alandi Road, Dighi, Pune | Pune | 411015 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Swamesh S_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the MCCB Hardware Problem . hardware socket found threading issue on both MCCB. then we arranged hardware from our stock and installed it. we checked cable connection on this terminal found tight properly found ok. we checked installing condition of cables found ok. | Repair |  | 9- Service Validated | 2023-09-25 15:57 |  |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11301095 | 104125628 | 2023-09-23 12:33 | 2023-09-23 |  | 2023-09-23 11:16 | GV2P20 | GV2P20 | GV2P20 |  | FW: DEFECTIVE MATERIAL @ V D ELECTRICAL AND ENGINEERING CO. GV2P20 pole continuity issue Site Address: V D Electrical & Engineering Co. B001, Ground Floor, Shalin Height-4, OPP: Lambha Turning, Lambha Vatva Canal Road, Nr, Divine Life International School Narol Ahmadabad 382405 Gujarat MR. MAYUR DAVE Contact Person No. 9427302722 | 2023-09-23 | 2023-09-25 10:00 | No | Warranty | V D Electrical & Engineering Co. | B001, Ground Floor, Shalin Height-4, OPP: Lambha Turning, Lambha Vatva Canal Road, Nr, Divine Life International School Narol | Ahmadabad | 382405 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Ritesh Prajapati_Anik Engineering Ahmedabad | Anik Engineering (554) | visited the site and checked the product found physically observed ok. checked mcb observed dolly free so free replacement. | Repair |  | 9- Service Validated | 2023-09-25 10:01 | 226076559 |  | 17 | INR | 17 | ENM POWER PRODUCTS
WO-11199077 | 103740723 | 2023-09-02 10:30 | 2023-09-02 |  | 2023-09-02 10:12 | TUAVQ | TUAVQ | TUAVQ | JK2215010281 | Call Log & Assign to CSS - SKS Mumbai in-warranty P:Loss of Air Flow Alarm S:warranty | 2023-09-02 | 2023-09-02 12:30 | No | Warranty | Webwerks India Pvt Ltd. | unit No. 901, Sigma IT Park, Plot No 203/204, Rabale | Mumbai | 400701 | Maharashtra | India FS West1 Cooling CSP Shree Krishma Services Mumbai | Chimmili Trimurthulu Shree Krishma Services Mumbai | Shree Krishna Services | P:Loss of Air Flow Alarm Site visit done for Loss of air flow alarm. As per site visit we have checked all Electrical parameter's then check blower fan motor not work. Checked and found blower fan motor Jammed and not working so replaced the same blower fan motor and started the unit working fine normal. Now PAC unit working ok. | Repair |  | 10- Closed | 2023-09-02 15:40 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 50 | INR | 50 | ENM SECURE POWER
WO-11301221 | 104220212 | 2023-09-25 10:13 | 2023-09-23 | MCCB not working properly | 2023-09-23 15:06 | LV510037 | LV510037 | LV510037 | 102247 | Regarding 1 nos MCCB y phase not working at Minda Supa Site Please refer the attached CFR, & Picture and arrange to depute your service engineer for 1 nos MCCB B Phase output supply is not coming at Minda Supa Site. For more information please refer to the attached pictures or you can speak to Mr Himanshu Das @ 8950066031. Please arrange to visit site, urgently. Contact Person- Mr Himanshu Das Contact No 8950066031 Site Address Uno Minda Ltd Alloy Wheel Division 2W, Plot no E-1, Additional Supa, Parner Indl Area, MIDC Apdhup, Ahmednagar, Maharashtra 414301 Your immediate support will be highly appreciable. | 2023-09-23 | 2023-09-25 15:43 | No | Warranty | Uno Minda Limited | Minda-MIL2W-Expansion Supa, Alloy Wheel Division 2W, Plot No.- E-1, Add. MIDC Vill, Apdhup Road, supa | Ahmed Nagar | 414301 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Kunal jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the MCCB not working properly. MCCB B phase not showing. we checked continuity pole found open. observed MCCB Y & B pole is open due to loose termination. so we make it proper tightening.and checked continuity found ok. there is no problem found in out product. MCCB found ok. | Repair |  | 9- Service Validated | 2023-09-25 15:50 |  |  | 135 | INR | 135 | ENM POWER PRODUCTS
WO-11199087 | 103728893 | 2023-09-02 12:06 | 2023-09-02 |  | 2023-09-02 10:23 | APC Smart-UPS RC 6000VA 230V for India - No Batteries | SRC6KUXI | SRC6KUXI | B21449050607 | Serial Number:B21449050607 Model Number:APC 6 KVA UPS Customer Site Address along with Pin Code:HDFC BANK LTD, SULAKASHANA COMPLEX, HATWA MARKET, KATCHERY ROAD, CHAPRA 841301 Name of the contact person at site:Arun Kumar Singh Contact person mobile and e Under AMC P:UPS Unit Issue / Down / due to short circuit ups not powering on S:AMC | 2023-09-02 | 2023-09-16 10:21 | No | Contract | HDFC Bank Ltd | Sulakshana Complex Hatwa Market Katchery Road Chhapra | Saran | 841301 | Bihar | India FS East HBN CSP Ascent Technology Patna | Md Kalam_Ascent Technology Patna | Ascent Technology - PATNA-KOLKATA | All 7 cards replaced ups is working fine 0J-0P6617AC/0J-0P7225AA/0J-0P7226AA/0J-0P5705AA/0J-0P5704AB/0J-0P7228AA/0J-0P5718 576617AC07049104/577225AJ23683059/577226AC20768940/575705AF23717800/57570AJ22469098/577228AC21165534/5757189916916350 | Repair |  | 8- Service Completed | 2023-09-16 10:22 |  |  | 115 | INR | 115 | ENM SECURE POWER
WO-11301222 | 104230032 | 2023-09-23 15:28 | 2023-09-23 |  | 2023-09-23 15:11 | GCR_ASCO_S7000 | GCR_ASCO_S7000 | GCR_ASCO_S7000 | 2400618-001WE | ATS Ref:- A7ACTM031200V5XC; Or pls use GCR_ASCO_S7000 SL no:- 2400618-002WE Under warranty:- Yes Problem:- ATS not operating in AUTO and in Manual(TNC). Customer details:- Elins Switchboards Pvt Ltd; HP Site 65A-1, 3rd Cross, Bommasandra Industrial Area, Aneka Taluk, Bangalore-560099 Mr. Vishwanath/Mr. Abhinandan +91-8431525091 abhinandan@elinsswitchboards.com | 2023-09-23 | 2023-09-28 18:28 | No | Warranty | Elins Switchboards Pvt Ltd | 65/1A Bommansandra industrial area | Bengaluru | 560099 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Swamy HJ_P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | Checked the above mentioned ATS, customer informed that it is not working in AUTO and Manual, we have found issues in TNC switch, it was not operated correctly earlier, re checked with correct operation and found It is is working in Manual, but to test in Auto, both the sources not available.. informed arrange both sources, check in auto and give is feedback | Repair |  | 8- Service Completed | 2023-09-28 18:29 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11199511 | 103740984 | 2023-09-04 10:22 | 2023-09-02 |  | 2023-09-02 10:50 | APC Smart-UPS RT 10000VA 230V Harsh Environment | SURT10000XLI-CC | SURT10000XLI-CC | B21432001182 | FW: Ups Not Working ¦¦ B21432001182 ¦¦ IM13375185 ¦¦ JC_DLHI_03. Under AMC P: UPS Not Working S:AMC | 2023-09-02 | 2023-09-04 15:00 | No | Contract | Reliance Corporate It Park Limited | Reliance Jio Center, C-34/4, Lawrence Road null | New Delhi | 110035 | Delhi | India FS North1 HBN CSP ARCHIT POWER SERVICES Delhi | Vinay Patel_Archit Power Services New Delhi | ARCHIT POWER SERVICES | site visit is done, found no problem, battery good, ups is ok & working fine. | Repair |  | 9- Service Validated | 2023-09-04 15:00 |  |  | 8 | INR | 8 | ENM SECURE POWER
WO-11301263 | 104229541 | 2023-09-25 10:29 | 2023-09-23 |  | 2023-09-23 16:30 | GCR_NSX100_630 | GCR_NSX100_630 | GCR_NSX100_630 |  | Mccb Not Work, Dear sir, We have received MCCB- NSX630N 50kA AC 3P3D 630A 6.3E Against invoice no-9008644453 Date-15-7-2023. This Mccb is not working. Kindly depute your service engineer to resolve the issue on high priority basis. Thanks & Regards Sumit Incoming Quality 9056656638 Email: quality2@cmkl.co.in | 2023-09-23 | 2023-09-25 12:24 | No | Warranty | Core Metal Krafts Ltd.(105184) | Dera Bassi,Vill:Saidpura | Mohali | 140507 | Punjab | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Vinod Kumar_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the mccb found not getting on due to mechanism dislocated. Set right the same now working ok. Email : quality2@cmkl.co.in | Repair |  | 8- Service Completed | 2023-09-25 12:30 |  |  | 25 | INR | 25 | ENM POWER PRODUCTS
WO-11200082 | 103741028 | 2023-09-02 11:38 | 2023-09-02 |  | 2023-09-02 11:01 | APC Easy UPS Online 6000VA Indian Outlet Rackmount 230V India | SRV6KL-IN | SRV6KL-IN | 9S1948A98752 | FW: RR : IM15430228 ¦ Store Code : TDZ0 ¦ SCHNEIDER ¦ WEST BENGAL -TST JANGIPUR Under AMC P: UPS not Powering on S:AMC | 2023-09-02 | 2023-09-03 12:20 | No | Contract | Reliance Retail Limited | RRL TST Jangipur, Beside Hotel Indigo, Raghunathganj P O, Murshidabad Dist | JANGIPUR | 742213 | West Bengal | India FS East HBN CSP SYSCOMP POWERSOL Sodepur | Prasenjit Mondal_SYSCOMP POWERSOL Sodepur | Syscomp Infotech Pvt Ltd - KOLKATA | Found Display Faulty. Replaced Display . 0J-31-012338 Now UPS is working properly. | Repair |  | 10- Closed | 2023-09-04 07:33 |  |  | 200 | INR | 200 | ENM SECURE POWER
WO-11304209 | 104230676 | 2023-09-25 11:23 | 2023-09-25 |  | 2023-09-25 09:49 | NA00634V | NA00634V | NA00634V |  | SAHTECH 2 Site Address Supplied Through (Panel Builder or Dealer - Details) 10 Shabhir Bhai & ABBAS BHAI 9820075083 / 9892925577 63A 4P ATS WATSN Transfer Issue UNDER WARRANTY Available Dealer - DIPSY TRADERS Shabhir Bhai - 9820075083 & ABBAS BHAI - 9892925577 13 Service Co-Ordinator 14 EMAIL ID dipsytraders@gmail.com 15 Services Person NAGBHUSHAN - 9886760260 Note : Point nos 1 to 10 are compulsory | 2023-09-25 | 2023-09-25 11:04 | No | Warranty | SAHTECH | BHINDI BAZER , opp Al sada bldg & DCB BANK null | MUMBAI | 400003 | Maharashtra | India FS ED&I CSP West Team R P Electrical Mumbai | Samrat Pawaskar R P Electrical Mumbai | R P Electrical | Checked 10 Nos. 63A, 100A & 400A ATS found physically found in good condition. Also we set ATS voltage setting S1 & S2 with the help of T Helper. Checked ATS manually working found Ok. After the voltage set checking ATS working found Ok. | Repair |  | 9- Service Validated | 2023-09-27 11:12 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11200508 | 103740927 | 2023-09-04 14:33 | 2023-09-06 |  | 2023-09-02 11:32 | SUA1000I-INNBQ | SUA1000I-INNBQ | SUA1000I-IN | BQ1418001168 | UPS Need Calibration ¦¦ Vatika City Homes, Sector 83, Gurgaon Under AMC P:Calibration request S:AMC | 2023-09-02 | 2023-09-06 15:12 | No | Contract | Thyssenkrupp Elevator India Pvt Ltd - Service Location | Vatika India Next City Homes Near Maneshar Toll Plaza null | Gurgaon | 122001 | Haryana | India FS North1 HBN CSP Martech Systems & Services New Delhi | Raju prasad Martech Systems & Services New Delhi | Martech Systems & Services-Gurgaon | ups re[laced, now ups is woring fine | Repair |  | 10- Closed | 2023-09-06 15:13 |  |  | 24 | INR | 24 | ENM SECURE POWER
WO-11304801 | 104230149 | 2023-09-25 15:19 | 2023-09-25 |  | 2023-09-25 13:41 | EZC100F3016 | EZC100F3016 | EZC100F3016 |  | Complaint for non working mccb Dear Sir, Please arrange engineer for following complaint Item Code. and Description EZC250N3200 MG EZC250 25KA 415V 3P 200A Tirupati Agencies to Customer Invoice No. 4044 Dated 01.03.23 Contact Person Name , Address and Mobile No. Amit Industries Khasra No. 509, Gram Pigdambar, Rau Santosh Bhaiya - 9691127947 Thanking You Deepak Goyal Tirupati Agencies 13, Press Complex, AB Road, Indore-452001 email : tirupatiagencies.indore@gmail.com | 2023-09-25 | 2023-09-26 18:47 | No | Warranty | Amit Industries | Godoun No 7, Khasra No. 509, Gram Pigdambar, Rau | Indore | 452001 | Madhya Pradesh | India FS ED&I CSP West Team ABR Technical Service Indore | Chirag Jain_ABR Tecneical Services Indore | ABR Technical Services (9574) | Checked MCCB as per customer it's tripping after running sometime during trial. Then we turn on MCCB and after 2-3 minutes found some sparking in Y-Phase (Outgoing side). Checked temperature and found 58 degree Celsius. Then we turn off MCCB and checked it's tightness and found loose termination. Then we removed all cables. Checked MCCB ON-OFF ok and continuity ok. MCCB used as main incomer for distribution purpose for some lighting load and small machine having heater. As per our primary observation it's not product issue MCCB tripping due to overheating. So we recommend customer to use spreaders and remove damaged lugs / cable and use lugs after proper crimping and place 8.8 grade bolt with proper tightness of cables and now we are closing this case. | Repair |  | 9- Service Validated | 2023-09-26 18:57 |  |  | 24 | INR | 24 | ENM POWER PRODUCTS
WO-11200555 |  | 2023-09-02 12:24 | 2023-09-02 |  | 2023-09-02 12:11 | PRODUCT UNIFLAIR LEONARDO DX MAX R407C TUAV3342A UPFLOW WITH HEATER HUMIDIFIER A | TUAVQ | TUAVQ | JK2217040041 | PM | 2023-09-02 | 2023-09-02 18:35 | No | Commercial Action - Service Ops | M/s Netweb Technologies India Pvt. Ltd. | Plot No. H1, FIT, Sector - 57 Faridabad Haryana null | Faridabad | 121001 | Haryana | India FS North1 Cooling CSP Smart Engineering Services Delhi | Sunil Kumar Smart Engineering Services Delhi | Smart Engineering Services | REGULAR PM | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-02 18:38 |  |  | 65 | INR | 65 | ENM SECURE POWER
WO-11304836 | 104241523 | 2023-09-26 15:29 | 2023-09-25 |  | 2023-09-25 13:53 | LC1D32M7 | LC1D32M7 | LC1D32M7 | 1023116L100464 | LC1D32M7 - 1023116L100464 humming noise Applied Voltage 220Vac Neutral to ground voltage 0.2Vac Site Address: KANISHKA BONDED FOAM G 362 MG ROAD UPSIDC INDUSTRIAL AREA, HAPUR Ghaziabad 201003 Uttar Pradesh Mr. Vikash Ji 9810202898 | 2023-09-25 | 2023-09-26 15:31 | No | Warranty | KANISHKA BONDED FOAM | G 362 MG ROAD UPSIDC INDUSTRIAL AREA, HAPUR null | Ghaziabad | 201003 | Uttar Pradesh | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the contactor found coil burnt due to abnormal voltage, Hence no replacement given to customer. Email : id not provided by customer. | Repair |  | 8- Service Completed | 2023-09-26 15:37 |  |  | 80 | INR | 80 | ENM POWER PRODUCTS
WO-11200556 |  | 2023-09-02 12:25 | 2023-09-02 |  | 2023-09-02 12:11 | TUAVQ | TUAVQ | TUAVQ | JK2217040042 | PM | 2023-09-02 | 2023-09-02 18:38 | No | Commercial Action - Service Ops | M/s Netweb Technologies India Pvt. Ltd. | Plot No. H1, FIT, Sector - 57 Faridabad Haryana null | Faridabad | 121001 | Haryana | India FS North1 Cooling CSP Smart Engineering Services Delhi | Sunil Kumar Smart Engineering Services Delhi | Smart Engineering Services | REGULAR PM | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-02 18:41 |  |  | 65 | INR | 65 | ENM SECURE POWER
WO-11304842 | 104241759 | 2023-09-27 17:30 | 2023-09-25 |  | 2023-09-25 13:57 | LC1E1810M7 | LC1E1810M7 | LC1E1810M7 | invoice | M/S MEMIGHTY INVENTIONS PRIVATE LIMITED 2 Site Address C/O ADANI CNG STATION, SECTOR - 9 FARIDABAD - 121006 Contact Phone / Mob. No: 6354919604 3 Name of contact person at site MR. KETAN BHAI 5 Defective product details LC1E1810 M7 - QTY - 2 6 Product Make SCHNEIDER - CONTACTOR 7 Nature of Defect NOT WORKING 8 Shutdown availability if applicable 9 Warranty status UNDER WARRANTY 10 Commissioned / Installed date 11 Serial No: or DOM of the product BILL NO - : 9320/21-22 DATE - 23-02-2022 12 Name & phone No: of person registering the complaint JOHNSON- 8780431402 | 2023-09-25 | 2023-09-27 17:31 | No | Warranty | MEMIGHTY INVENTIONS PRIVATE LIMITED | Sector:- 9, C/O ADANI CNG STATION | FARIDABAD | 121006 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Pradeep Sharma_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the contactor found coil burnt due to abnormal voltage, Hence no replacement given to customer. Email : id not provided by customer. | Repair |  | 8- Service Completed | 2023-09-28 10:52 |  |  | 45 | INR | 45 | ENM POWER PRODUCTS
WO-11200558 | 103741352 | 2023-09-02 16:41 | 2023-09-02 |  | 2023-09-02 12:12 | SRC10KUXI | SRC10KUXI | SRC10KUXI | B22132013066 | FW: Request for de-installation of UPS at De-hired Pharma DCs-RJ P: de-installation S: de-installation | 2023-09-02 | 2023-09-04 15:16 | No | Commercial Action - Sales | Reliance Retail Limited | Pharma DC ?Ground Floor Rangoli warehouse near Kami Industrial Area Village -8 B Km chak Garbi | Bikaner | 334004 | Rajasthan | India FS North1 HBN CSP Legacy Systems Jaipur | Rajendra Kumar Legacy Systems Jaipur | Legacy Systems | de - installation done | Decommissioning | Uninstall | 9- Service Validated | 2023-09-04 15:16 |  |  | 350 | INR | 350 | ENM SECURE POWER
WO-11305175 | 104235886 | 2023-09-25 16:23 | 2023-09-25 |  | 2023-09-25 15:10 | LV563505 | LV563505 | LV563505 | TC-2022-W01 | Complaint of issue in MCCB 630Amp CVS As Per The serial number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- MASTER SOFTWARE SOLUTIONS plot No I-51, Sector 83 aplha,, IT City,Airport Road Mohali 140306 Punjab India Contact Person Details:- Naseeb ( mob : 9023619712 Product and Issue:- LV563505 S. No.: TC-2022-W01 Tripping Issue occurring in MCCB, Dial setting is at 630 for Ir and 5 at Isd. No loose termination is their as per customer. | 2023-09-25 | 2023-09-30 13:37 | No | Warranty | MASTER SOFTWARE SOLUTIONS | plot No I-51, Sector 83 aplha,, IT City,Airport Road | Mohali | 140306 | Punjab | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Ram Ashish Sharma Electric Chandigarh | Sharma Electric works(1003) | checked the mccb found tripping issue. hence faulty, replaced. LV563505 - 1 Nos. Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-30 13:41 |  |  | 25 | INR | 25 | ENM POWER PRODUCTS
WO-11200569 | 103741392 | 2023-09-05 13:11 | 2023-09-02 |  | 2023-09-02 12:21 | SRC10KUXI | SRC10KUXI | SRC10KUXI | B21949002896 | FW: Request for de-installation of UPS at De-hired Pharma DCs-RJ P: de-installation S: de-installation | 2023-09-02 | 2023-09-06 15:57 | No | Contract | Reliance Retail Limited | Ground Floor Plot No R 13 BR 13 C, B Block Transport Nagar Scheme, Near Goverdhan Villas | Udaipur | 313001 | Rajasthan | India FS North1 HBN CSP G NAGAR & ASSOCIATES Udaipur | Ambalal Menaria_G NAGAR & COMPANY Udaipur | G NAGAR & ASSOCIATES | I looking set UPS Decommissioning by main line & battery. | Decommissioning | Uninstall | 10- Closed | 2023-09-06 16:04 |  |  | 10 | INR | 10 | ENM SECURE POWER
WO-11200637 | 103741601 | 2023-09-02 13:54 | 2023-09-02 |  | 2023-09-02 13:40 | Leonardo EV,DX,R22,EC Fan,TDAV0811A,Downflow Without Heater & Humidifier | TDAV0811AN001 | TDAV0811AN001 | ZK1330017659 | Re: Call log for Reliance Ag2 Ulhasnagar. Under AMC P:HP Alarm S:AMC | 2023-09-02 | 2023-09-02 15:04 | No | Contract | Reliance Industries Ltd. | Reliance Corporate Park, Bldg. no. 6, D-wing, 2nd floor, Thane- Belapur Road, | Mumbai | 400701 | Maharashtra | India FS West1 Cooling CSP Shree Krishma Services Mumbai | Chimmili Trimurthulu Shree Krishma Services Mumbai | Shree Krishna Services | P:HP Alarm Site visit done for PAC unit HP Alarm. PAC unit not working. As per check unit no-2 HP Alarm so alarm reset checked out door unit on / off switch faulty so switch by pass PAC unit normal working ok | Repair |  | 10- Closed | 2023-09-04 12:10 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 50 | INR | 50 | ENM SECURE POWER
WO-11200651 | 103741918 | 2023-09-07 01:13 | 2023-09-02 |  | 2023-09-02 14:03 | EFC Monoblock unit 1.3TER, downflow with start run relay kit | WDF0181BN002 | WDF0181BN002 | ZK1534019334 | FW: Required work order & spare part Under AMC P: Compressor Faulty S:AMC | 2023-09-02 | 2023-09-07 01:22 | No | Contract | RELIANCE JIO INFOCOMM LIMITED | Adivare vilage Rajapur | Rajapur | 416702 | Maharashtra | India FS West2 Cooling CSP Unitec Engineers Pune | Onkar Deshmukh Unitec Engineers Pune | Unitec Engineers | Compressor replacement done . | Repair |  | 10- Closed | 2023-09-07 01:25 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 195 | INR | 195 | ENM SECURE POWER
WO-11200667 | 103742066 | 2023-09-06 11:59 | 2023-09-02 |  | 2023-09-02 14:35 | APC Smart-UPS RT 10000VA 230V Harsh Environment | SURT10000XLI-CC | SURT10000XLI-CC | B21511001914 | FW: UPS battery backup _IM13376148_JC_BNSR_01_B21511001914 Under AMC P: UPS battery backup S:AMC | 2023-09-02 | 2023-09-07 11:25 | No | Contract | Reliance Corporate It Park Limited | Opp ICICI Bank, SBBJ Chorha, Mohan Colony | Banswara | 327001 | Rajasthan | India FS North1 HBN CSP G NAGAR & ASSOCIATES Udaipur | Ambalal Menaria_G NAGAR & COMPANY Udaipur | G NAGAR & ASSOCIATES | I checked UPS all parameter are working fine. battery backup check 1/2 hours UPS work done ( two battery bank set up) | Repair |  | 10- Closed | 2023-09-07 11:30 |  |  | 156 | INR | 156 | ENM SECURE POWER
WO-11200670 | 103742164 | 2023-09-02 16:01 | 2023-09-02 |  | 2023-09-02 14:49 | ANC-MISC | ANC-MISC | ANC-MISC | SRF032293 | FW: Call log for BRIDGE DATA CENTERS LLP IN-WARRANTY P: Main Phase Error Alarm S:Onsite | 2023-09-02 | 2023-09-02 21:45 | No | Warranty | BRIDGE DATA CENTERS LLP | TTC ,Industrial Area,MIDC,Plot No-13, Digha | Mumbai | 400708 | Maharashtra | India FS West1 Cooling CSP Shree Krishma Services Mumbai | Madhu Kadali Shree Krishma Services Mumbai | Shree Krishna Services | P: Main Phase Error Alarm Site visit done for Chiller no-10 Main Phase Error Alarm. as per site visit we have check Electrical parameter found normal verify alarm long main phase Error alarm. we have check all Parameters verify chiller working logic during power check over ATS transfer source B to A then general alarm will be Triger & trip on generals faulty alarm we have working on it for the ATS time relay. Now chiller working ok. | Repair |  | 10- Closed | 2023-09-04 11:52 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 50 | INR | 50 | ENM SECURE POWER
WO-11093779 | 103148863 | 2023-08-09 16:05 | 2023-08-09 |  | 2023-08-09 15:19 | LV431541T | LV431541T | LV431541T |  | Dear Team, Please register below complaint and arrange site visit asap. Checklist for Complaint Registration 1 Name of Customer Hesel Controls, 28W7+H5V, Industrial Estate, South Kalamassery, Kalamassery, Ernakulam, Kochi, Kerala 683104 2 Site Address Hesel Controls, 28W7+H5V, Industrial Estate, South Kalamassery, Kalamassery, Ernakulam, Kochi, Kerala 683104 3 Name of contact person at site Mr Santhosh Narayan Hessel Controls 4 Contact Phone / Mob. No: +91 81298 22510 5 Defective product details LV431541? Motor Mechncism 6 Nature of Defect Not Working Site Visit Required Yes 7 Shutdown availability if applicable YES 8 Warranty status YES 9 Commissioned / Installed date 01-May-23 10 Serial No: or DOM of the product 11 Name & phone No: of person registering the complaint Vivek V Chithambaran/ 09745555411 Note : Point Nos: 1 to 9 are compulsory ?Be Well? & ?Stay Safe? Best Regards VIVEK V CHITHAMBARAN Manager National Sales International Operations Schneider Electric M +91 9745555411 E vivekv.chithambaran@se.com S-04, 6th Floor, Centre A Alapatt Heritage Building MG Road, Kochi Kerala 682035, India | 2023-08-09 | 2023-09-06 14:21 | No | Warranty | Hesel Controls | Plot No 24B, Industrial Developent Plot, South Kalamassery | Eranakulam | 683109 | Kerala | India FS ED&I CSP South Team Geartech Electric Cochin | Vineesh M_Geartech Electric Cochin | Geartech Electric ASC for Schneider Electric | Checked the equipment and found the problem with the malfunction of MCH.To be solve need to replace the MCH. ZVO Material received dt: 06-09-2023 | Repair |  | 9- Service Validated | 2023-09-06 14:22 | Hi Team, Material booked zfre Zvo : 225920356 |  | 10 | INR | 10 | ENM POWER PRODUCTS
WO-11103004 | 103199113 | 2023-08-11 12:39 | 2023-08-11 |  | 2023-08-11 11:43 | LP2K0901BD | LP2K0901BD | LP2K0901BD |  | Checklist for Complaint Registration 1 Site Name & Complete Address Ace Manufacturing Systems No. 467 to 469, 12th Cross, 4th Phase, Peenya Indl. Area, Bangalore-560058 7 Site Contact Name & Mob# Mr. Sumith Mob No.: 7619571898 94498361202 3 Site Contact Email Address** 4 Defective Product Model/Part No As per below 5 Nature of Defect* As per below 6 Shutdown availability if applicable Yes 7 Distributor Name,Invoice # & Date As per below 8 Serial No: or DOM of the product 9 Name & phone No: of person registering the complaint Aruna BR Mob: 8884559336 "Points 1,2,4,5 & (7or8) are mandatory. Point 7 not applicable for Industry Business * Kindly share defect symptoms instead of ""Not working"" ** End user will receive a survey asking feedback on service" SL No. Part No. Qty Invoice No. & Date Nature of Defect 3 LP2K0901BD 2 222312778 01-02-2023 Not Working 8 A9KF71103 1 222314122 01-03-2023 Tripping element is stucked inside 10 GZ1E06 1 222312778 01-02-2023 Contactor stuck up issue | 2023-08-11 | 2023-09-15 12:54 | No | Warranty | Ace Manufacturing system India pvt Ltd | 467-469, 12th Cross Rd, 4th Phase, Peenya Industrial Area, Bengaluru, Karnataka | Bangalore | 560058 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Nagaraja G_P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | Inspected and found 1)Ref: A9KF71103 S/N:D2312 = 1 No, MCB screw threading issue. 2)Ref: GZ1E06 S/N:8C23061 = 01 MPCB ON/OFF push button issue. 3)Ref: LP2K0901BD S/N:2F22453 =1 No contactor ON/OFF issue. Hence we will give the above mentioned contactor, MCB & MPCB warranty replacement ASAP. Defective material is at customer place. | Repair |  | 9- Service Validated | 2023-09-15 12:55 | Hi Team, Material booked zfre Zvo : 225962136 |  | 15 | INR | 15 | ENM POWER PRODUCTS
WO-11200709 |  | 2023-09-05 17:31 | 2023-09-02 |  | 2023-09-02 15:52 | SURT10000XLI-CC | SURT10000XLI-CC | SURT10000XLI-CC | B21524001481 | FW: RR : IM15366088 ¦ Store Code :9539 ¦ SCHNEIDER ¦ MAHARASHTRA -TRENDS Under AMC P: Battery Installation S:Battery Installation | 2023-09-02 | 2023-09-05 10:27 | No | Commercial Action - Sales | RRL Fitch Trends | Plot No-3058 Congress Bhavan Near Azad Garden Bhanapeth null | Chandrapur | 442401 | Maharashtra | India FS West1 HBN CSP_Modular Electronics Pvt Ltd Nagpur | Ritesh Kale Modular Electronics Pvt Ltd Nagpur | Modular Electronics Pvt Ltd - Nagpur | Visited site for batteries Installation. Installation done. then checked charging & discharging voltage. | Commissioning & Installation | Battery Installation | 8- Service Completed | 2023-09-06 10:35 |  |  | 155 | INR | 155 | ENM SECURE POWER
WO-11200818 | 103743233 | 2023-09-02 18:47 | 2023-09-02 |  | 2023-09-02 18:33 | APC Smart-UPS 3000VA USB & Serial 230V | SUA3000I | SUA3000I | B21241000474 | RE: UPS not working, Case: 103312133, [ thread::54CidrjNfI2efKsvU5LJFT4:: ] P:UPS not working S:AMC | 2023-09-02 | 2023-09-04 15:57 | No | Contract | Thyssenkrup Elevators India Pvt Ltd | Ravindra Kumar Plot No 1155 Sec 46 Gurgaon | Gurgaon | 122003 | Haryana | India FS North1 HBN CSP Prokon Hi Tech Systems Gurgaon | Krishna Kumar_Prokon Hi-Tech Systems Gurgaon | Prokon Hi-Tech Systems-Gurgaon | UPS not powering on replaced the new unit now ups working is okay. Model no SUA3000I-IND Serial no B22151026932 | Repair |  | 10- Closed | 2023-09-04 16:02 |  |  | 10 | INR | 10 | ENM SECURE POWER
WO-11208743 | 103754358 | 2023-09-04 10:46 | 2023-09-04 |  | 2023-09-04 09:14 | EFC MONOBLOCK 1.3TR R410A START KIT RS485 SEQ CONTROL | WDF0181BN040-1 | WDF0181BN040-1 | JK2048002601 | PAC cooling issue Serial# JK2048002601 P:PAC cooling issue S:AMC | 2023-09-04 | 2023-09-04 11:23 | No | Contract | Reliance Jio Infocomm Ltd | Prafula Chandra Mahanta,AT-Jaganath market,.Ward No-5,Po/Ps-Rairangpur | Mayurbhanj | 757043 | Odisha | India FS East Cooling CSP Cool Care Refrigerant Bhubaneshwar | Debasis Sahoo_Cool Care Refrigerant Bhubaneshwar | Cool Care Refrigerant | we attend the site found gas leakgae from liquied line drier joint ,leak repairing psi testing vaccuming & gas charging ,now efc running ok . | Repair |  | 10- Closed | 2023-09-04 11:27 |  |  | 300 | INR | 300 | ENM SECURE POWER
WO-11208783 | 103754413 | 2023-09-04 19:29 | 2023-09-04 |  | 2023-09-04 09:30 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | JK1925001284 | LP Alarm P:LP Alarm S:AMC | 2023-09-04 | 2023-09-04 17:00 | No | Contract | Reliance Jio Infocomm Ltd | Kanchan Bajar, Mandi Dhanaura | Amroha | 244231 | Uttar Pradesh | India FS North2 Cooling CSP DTC System Uttrakhand | Devendra Kumar_DTC System Uttrakhand | DTC System | UNit was giving LP alarm, checked and find gas leak from Qtr pipe behind compressor. leak repaired, tested, vacuumed and charged with R-22 gas | Repair |  | 10- Closed | 2023-09-05 08:53 |  |  | 100 | INR | 100 | ENM SECURE POWER
WO-11208837 | 103755000 | 2023-09-04 11:16 | 2023-09-04 |  | 2023-09-04 10:00 | Leonardo EV,DX,R22,EC Fan,TDAV0511A,Downflow Without Heater & Humidifier | TDAV0511AN001 | TDAV0511AN001 | ZK1332017206 | High pressure alarm Serial# ZK1332017206 P:High pressure alarm S:AMC | 2023-09-04 | 2023-09-04 18:03 | No | Contract | Reliance Jio Infocomm Ltd | Plot No30 Ganapathy Thottam Road, Thiruvallur Nagar,Madavaram | Chennai | 600051 | Tamil Nadu | India FS South4 Cooling CSP Unity Air conditioning Engineers Chennai | K Karthick Unity Air-conditioning Engineers Chennai | UNITY AIRCONDITIONING ENGINEERS | HP alarm : Now we checked and found ODU unit clogged due to ageing of the unit. Now we water wash the coil and observe unit working normal. | Repair |  | 10- Closed | 2023-09-04 18:12 |  |  | 38 | INR | 38 | ENM SECURE POWER
WO-11208851 | 103754752 | 2023-09-04 15:12 | 2023-09-04 |  | 2023-09-04 10:07 | InRow DX 300mm 30kW Indoor Unit 200-240V Humidifier & Reheat CE/UL | ACRD301P | ACRD301P | JK2125005089 | CESC BD Call Under AMC P:VFD Earth Fault S:AMC | 2023-09-04 | 2023-09-07 18:30 | No | Contract | CESC Ventures Limited | C/O RPSG Ventures Limited ,2, Lord Sinha Road, 2nd floor, | Kolkata | 700071 | West Bengal | India FS East Cooling CSP Snow Point Kolkata | Jadab Patra_Snow Point Kolkata | Snow Point | COMPRESSOR FAULTY.COMPRESSOR REPLACEMENT DONE.FILTER DIRER RECOMMISSING.OIL SAPARATOR UNINSTALL. ALL PIPE LINE FLASHING (CLEAN).OIL SAPARATOR REINSTALL.OIL SAPARATOR OIL CHANGE.17.8 KG R410 GAS CHARGE.ALL PARAMETER CHECKED.MACHINE OK RUNNING. | Repair |  | 10- Closed | 2023-09-11 18:46 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 30 | INR | 30 | ENM SECURE POWER
WO-11209514 | 103755546 | 2023-09-04 11:07 | 2023-09-04 |  | 2023-09-04 10:39 | Leonardo EV,DX,R22,EC Fan,TDAV0811A,Downflow Without Heater & Humidifier | TDAV0811AN001 | TDAV0811AN001 | ZK1330006564 | Outdoor fan faulty Serial# ZK1330006564 P: Outdoor fan faulty S: AMC | 2023-09-04 | 2023-09-12 11:32 | No | Contract | Reliance Jio Infocom Ltd | Reliance Jio Infocomm 1st Floor, Bhaskar Complex Pumpwell junction (Canara Bank Building) | Mangalore | 575002 | Karnataka | India FS South3 Cooling CSP Fresco solutions Bangalore | SIBIN S_Fresco solutions Bangalore | Fresco solutions | condenser motor 2no's replaced | Repair |  | 8- Service Completed | 2023-09-12 11:34 |  |  | 350 | INR | 350 | ENM SECURE POWER
WO-11209600 | 103755588 | 2023-09-04 11:28 | 2023-09-04 |  | 2023-09-04 10:40 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | C21706000038 | P: c21706000038--HP Alarm Under AMC P: c21706000038--HP Alarm S:AMC | 2023-09-04 | 2023-09-04 18:27 | No | Contract | Reliance Jio Infocom Ltd | Bandana Saikia,Vill Bardangerikuchi,Baihata Chariali | Kamrup | 781366 | Assam | India FS East Cooling CSP SYSCOMP POWERSOL Guwahati | SHUBHAM PATHAK SYSCOMP POWERSOL Guwahati | SYSCOMP POWERSOL - GUWAHATI | controller faulty.change the controller and checked all wire tightness parameters found normal.unit is working properly. | Repair |  | 10- Closed | 2023-09-05 18:33 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 60 | INR | 60 | ENM SECURE POWER
WO-11210399 | 103755797 | 2023-09-04 11:29 | 2023-09-04 |  | 2023-09-04 10:53 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | C21716001245 | P: c21716001245----Controller fault Under AMC P: c21716001245----Controller fault S:AMC | 2023-09-04 | 2023-09-04 18:46 | No | Contract | Reliance Jio Infocomm Ltd | Sani bazar, Near Morigaon ASTC counter. Dist -Morigaon. PO- Morigaon | Morigaon | 782105 | Assam | India FS East Cooling CSP SYSCOMP POWERSOL Guwahati | Vikash Kumar SYSCOMP POWERSOL Guwahati | SYSCOMP POWERSOL - GUWAHATI | change the controller.controler foulty.all wire tightness ok.parameter found normal.now unit is working properly | Repair |  | 10- Closed | 2023-09-05 18:50 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 90 | INR | 90 | ENM SECURE POWER
WO-11210570 | 103756350 | 2023-09-04 12:06 | 2023-09-04 |  | 2023-09-04 11:27 | APC Symmetra LX 8kVA Scalable to 16kVA N+1 Rack-mount, 220/230/240V or 380/400/4 | SYA8K16RMI | SYA8K16RMI | QD0738380772 | FW: WB-NDI-01 ups not working Site code: WB-NDI-01 ups not working Serial# QD0738380772 P: ups not working S:AMC | 2023-09-04 | 2023-09-05 12:12 | No | Contract | Central Board of Excise & Customs-CBEC | B- 12/135 & 145 Central Park Kalyani Dist | Nadia | 741137 | West Bengal | India FS East HBN CSP SYSCOMP POWERSOL Sodepur | Prasenjit Mondal_SYSCOMP POWERSOL Sodepur | Syscomp Infotech Pvt Ltd - KOLKATA | Found power , battery and mim faulty. Replaced 1 nos power module, 2 nos battery module and 1 nos mim. AQ2115110370(SYPM4KIQ) 5D2306T91813(SYBT5) 5D2306T66763(SYBT5) 5D2311T71319(WSYMIM5) Now UPS is working properly. | Repair |  | 10- Closed | 2023-09-05 17:40 |  |  | 120 | INR | 120 | ENM SECURE POWER
WO-11210596 | 103756482 | 2023-09-04 12:37 | 2023-09-04 |  | 2023-09-04 11:34 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | C21806001352 | PAC cooling issue Serial# C21806001352 P:PAC cooling issue S:AMC | 2023-09-04 | 2023-09-05 21:30 | No | Contract | Reliance Jio Infocomm Ltd | Pratapgarh 230204, Kunda AG-1 | Pratapgarh | 230204 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Harinder Yadav Freezeotech Airconditioning & Refrigeration Lucknow | Freezeotech Airconditioning & Refrigeration Corporation | SITE VISIT FOUND THE CONDENSORE FAN FAULTY NOW CHANGE THE PART UNIT IS WORKING OK | Repair |  | 10- Closed | 2023-09-07 10:48 |  |  | 145 | INR | 145 | ENM SECURE POWER
WO-11210613 | 103757017 | 2023-09-04 19:30 | 2023-09-04 |  | 2023-09-04 11:43 | Leonardo EV,DX,R22,EC Fan,TDAV0811A,Downflow Without Heater & Humidifier | TDAV0811AN001 | TDAV0811AN001 | ZK1330009940 | Outdoor not working and alarm not generating---zk1330009940 Under AMC P:Outdoor not working and alarm not generating---zk1330009940 S:AMC | 2023-09-04 | 2023-09-10 20:44 | No | Contract | Reliance Jio Infocomm Ltd. | Bareilly 320 Akash Floor city satation road civilline Street No -1, P S -Prem Nagar, | Bareilly | 243001 | Uttar Pradesh | India FS North2 Cooling CSP DTC System Uttrakhand | Tahir DTC System Uttrakhand | DTC System | visited and find condenser fan faulty, condenser fan repalced. | Repair |  | 10- Closed | 2023-09-11 06:02 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 245 | INR | 245 | ENM SECURE POWER
WO-11210620 | 103757199 | 2023-09-04 19:31 | 2023-09-04 |  | 2023-09-04 11:49 | EFC Monoblock unit 0.8TR, downflow with start run relay kit | WDF0101BN002 | WDF0101BN002 | JK1317000797 | Controller faulty- PAC Serial# JK1317000797 P: Controller faulty- PAC S:AMC | 2023-09-04 | 2023-09-07 18:00 | No | Contract | RELIANCE JIO INFOCOMM LIMITED | Mr Hazi Furkat Ali Village Athseni Near NH-24 | Garhmukteshwar | 245205 | Uttar Pradesh | India FS North2 Cooling CSP DTC System Uttrakhand | Devendra Kumar_DTC System Uttrakhand | DTC System | Unit was giving LP alarm, Checked and find Tex-2 Chock, TeX-2 with orifac and drier replaced, leak tested,vacuumed and charged with R-22 gas, also infocool kit replaced as alarms were not genrating in old set | Repair |  | 10- Closed | 2023-09-08 08:36 |  |  | 55 | INR | 55 | ENM SECURE POWER
WO-11210677 | 103757626 | 2023-09-04 12:40 | 2023-09-04 |  | 2023-09-04 12:04 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | C21806000156 | P:Blower fan issue and cooling---c21806000156 Under AMC P:Blower fan issue and cooling---c21806000156 S:AMC | 2023-09-04 | 2023-09-05 23:30 | No | Contract | Reliance jio infocomm Ltd | Ag1, Unchahar | Unchahar | 229404 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Karuna Tripathi Freezeotech Airconditioning & Refrigeration Lucknow | Freezeotech Airconditioning & Refrigeration Corporation | site visit found the condenser fan faulty now change the part unit is working ok | Repair |  | 10- Closed | 2023-09-07 17:18 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 122 | INR | 122 | ENM SECURE POWER
WO-11134247 | 103346821 | 2023-08-20 11:16 | 2023-08-22 |  | 2023-08-18 09:56 | LC1G500KUEN | LC1G500KUEN | LC1G500KUEN |  | Name of Customer:-MKK METAL SECTIONS PVT LTD. Site Address:-PLOT NO. M1, 3, 632405, Ranipet Sipcot, Ranipet,Tamil Nadu 632520 Name of contact person at site:-Sarath P Kaimal Contact Phone / Mob. No:-+91 97373 70262 Defective product details:-LC1G500KUEN(1 QTY) Invoice no:-PSI/22012250(20/01/2023) Nature of Defect:-Not getting on. | 2023-08-18 | 2023-08-22 23:30 | No | Warranty | MKK Metals Sections Pvt. Ltd. | Plot No. M1, Ph 3, Nilikuppam, Mukundraipuram null | Vellore | 632405 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Site Visit Done | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-06 13:53 |  |  | 118 | INR | 118 | ENM POWER PRODUCTS
WO-11210694 | 103757755 | 2023-09-06 15:47 | 2023-09-04 |  | 2023-09-04 12:10 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | C21705001466 | PAC cooling issue Serial# C21705001466 P: PAC cooling issue S:AMC | 2023-09-04 | 2023-09-08 17:50 | No | Contract | RELIANCE JIO INFOCOMM LIMITED | Azizur Rahaman Vill +P O +P S | Birbhum | 731301 | West Bengal | India FS East Cooling CSP Snow Point Kolkata | Chandan Nandi_Snow Point Kolkata | Snow Point | LP ALARM.CONTROLER NOT WORKING.DUMPER BROKEN,SUCTION PRESSURE LESS THEN 15 PSI.CONTROLER AND DUMPER CHANGE.LEAKAGE TESTING.N2 HOLD VACCUM.AND 2KG R22 GAS CHARGE.ALL PARAMETER CHECKED.MACHINE OK RUNNING. | Repair |  | 10- Closed | 2023-09-08 18:00 |  |  | 220 | INR | 220 | ENM SECURE POWER
WO-11103560 | 103215317 | 2023-08-11 17:13 | 2023-08-11 | NA | 2023-08-11 14:43 | GCR_NW_CB | GCR_NW_CB | GCR_NW_CB |  | As per the invoice, The Product is in Warranty. Kindly arrange the site visit. Issue:Hardware issue Address Hitech Cooling DH Road, Nanda Bhanga, Guljar More, 24 Parganas ( S), Bishnupur 743503 West Bengal India Contact person Details: - Mr.Ghatak 9836655549 | 2023-08-11 | 2023-08-31 14:30 | No | Warranty | Hitech Cooling | DH Road, Nanda Bhanga, Guljar More, 24 Parganas ( S), null | Bishnupur | 743503 | West Bengal | India FS ED&I CSP East Team B.D Electroservices Kolkata | RAHUL RAY_B.D Electroservices Kolkata | B.D Electroservices(500017330) | We close this complain and we will do the physically work tomorrow. | Repair |  | 9- Service Validated | 2023-09-02 16:12 | =S= Free Order 225975305 has been saved |  | 12 | INR | 12 | ENM POWER PRODUCTS
WO-11210764 | 103756295 | 2023-09-05 14:28 | 2023-09-04 |  | 2023-09-04 12:31 | TDAV1021AN009 | TDAV1021AN009 | TDAV1021AN009 | ZK1440001217 | New Complain Logged Under AMC P:HP Alarm Generat. S:AMC | 2023-09-04 | 2023-09-10 12:00 | No | Contract | Reliance Jio Infocomm Ltd. | Shyam Shangani Kumbhariya Road Surat | Surat | 395009 | Gujarat | India FS West2 Cooling CSP DECENT HVAC SYSTEM Gandhinagar | Mickey Kabrawala DECENT HVAC SYSTEM Gandhinagar | DECENT HVAC SYSTEM | Complaint attend, PCO Card replaced. (> 240 KM) | Repair |  | 8- Service Completed | 2023-09-11 10:34 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 304 | INR | 304 | ENM SECURE POWER
WO-11210828 | 103758463 | 2023-09-04 13:32 | 2023-09-04 |  | 2023-09-04 12:46 | Amico DX Model 0331 thru 0601 | UFAMDX0601 | UFAMDX0601 | NUCX4830 | Request for breakdown call P:Compressor contactor fail S:AMC | 2023-09-04 | 2023-09-09 15:23 | No | Contract | NXTRA DATA LIMITED | Survey No.127/2A, 2B Done Atkur Village, Nidamanuru gram Panchayat, Vijayawada Rural Mandal Near Delhi Public School Krishna Dist | Krishna | 521104 | Andhra Pradesh | India FS South1 Cooling CSP Sri Venkateshwara Engineering Enterprise Visakhapatn | Lokesh_ Sri Venkateshwara Engineering Enterprise Visakhapatn | Sri Venkateshwara Engineering Enterprises | Attended the call checked the unit clock card was not working. So replaced the clock card. Now the unit was running. | Repair |  | 8- Service Completed | 2023-09-09 15:30 |  |  | 350 | INR | 350 | ENM SECURE POWER
WO-11135975 | 103367679 | 2023-08-19 12:26 | 2023-08-22 |  | 2023-08-18 16:57 | LV432641 | LV432641 | LV432641 |  | Checklist for Complaint Registration 1 Site Name & Complete Address Hotel Lance International, 77E2/1 Medical Colege Road, Opp to Bishop Hosue, Nagerkoi, Tamilnadu .Pin 629001 2 Site Contact Name & Mob# Mr Kumar Ph 9486610162 3 Site Contact Email Address** vettripowers@gmail.com 4 Defective Product Model/Part No LV432641 5 Nature of Defect* Motor Mechanism / Spring charge not working 6 Shutdown availability if applicable N A 7 Distributor Name,Invoice # & Date SHRIKRISHNA,, CHENNAI - Invoice No : AA320096758 & 9008249380 Dt 14.09.2022 8 Serial No: or DOM of the product 9 Name & phone No: of person registering the complaint B.VENKATRAMAN 97909-83346 "Points 1,2,4,5 & (7or8) are mandatory. Point 7 not applicable for Industry Business * Kindly share defect symptoms instead of ""Not working"" ** End user will receive a survey asking feedback on service" | 2023-08-18 | 2023-09-05 10:04 | No | Warranty | Hotel Lance International | 77E2/1 Medical Colege Road Opp to Bishop Hosue Nesamoni nager Nagercoil null | KANYAKUMARI | 629001 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | George KJ_Omicon Engineering Madurai | Omicon Engineering | Inspected the site and checked the motor mechanism continuosly running opened the front cover and found gear damaged condition . | Repair |  | 9- Service Validated | 2023-09-05 10:10 |  |  | 250 | INR | 250 | ENM POWER PRODUCTS
WO-11210887 | 103759245 | 2023-09-04 13:38 | 2023-09-05 |  | 2023-09-04 12:54 | APC Symmetra LX 16kVA N+1 Ext. Run Tower Frame, 220/230/240V or 380/400/415V | SYAF16KXR9I | SYAF16KXR9I | QD0827260097 | FW: KA-BGM-01 UPS NOT WORKING Site code: KA-BGM-01 UPS NOT WORKING Serial# QD0827260097 P: UPS NOT WORKING S: AMC | 2023-09-04 | 2023-09-05 14:35 | No | Contract | CBEC-To The Commissioner of Central Excise and Customs | CBEC To The Commissioner of Central Excise and Customs | Belgaum | 590001 | Karnataka | India FS South1 HBN CSP ABPowerSystems Hubli | Adrushappa MB ABPowerSystems Hubli | AB Power Systems | check the ups and battery ups check battery mode working but not working mains mode because input voltage is very high 289VAC inform the customer resolved the electrical problem as soon as possible | Repair |  | 10- Closed | 2023-09-05 14:52 |  |  | 200 | INR | 200 | ENM SECURE POWER
WO-11210907 | 103759661 | 2023-09-04 15:09 | 2023-09-04 |  | 2023-09-04 13:03 | APC Easy UPS On-Line SRV 6000VA RT 230V India - No Battery | SRV6KUXI-IN | SRV6KUXI-IN | 9S2124A73755 | IN-WARRANTY p:BDC error c:1server t:Customer has checked problem persist s:Onsite | 2023-09-04 | 2023-09-04 21:23 | No | Warranty | NTT Data Business Solutions Pvt Ltd | Plot No 4,3rd Floor,B-wing Softsol Tower 2, Software Units Layout,Madhapur | Hyderabad | 500081 | Andhra Pradesh | India FS South3 HBN CSP Param Technologies Hyderabad | Kodanda Ramudu_Param Technologies Hyderabad | Param Technologies | 1st onsite date 04-09-2023 Replaced unit old sr no: SRV6KUXI-IN 9S2124A73755 New sr no: SRV6KUXI-IN 9S2313A01526 Now UPS is working fine on both modes | Repair |  | 10- Closed | 2023-09-05 09:29 |  |  | 6 | INR | 6 | ENM SECURE POWER
WO-11211058 | 103761381 | 2023-09-04 19:32 | 2023-09-04 |  | 2023-09-04 13:48 | LEONARDO EV,DX,R22,EC FAN,( HCM109-DANFOSS ), DOWNFLOW WITHOUT HEATER & HUMIDIFI | TDAV0811AN005 | TDAV0811AN005 | ZK1602019697 | Under AMC P:AC device not generating alarm--zk1602019697 S:AMC | 2023-09-04 | 2023-09-06 15:30 | No | Contract | Reliance Jio Infocomm Ltd. | Bareilly 320 Akash Floor city satation road civilline Street No -1, P S -Prem Nagar, | Bareilly | 243001 | Uttar Pradesh | India FS North2 Cooling CSP DTC System Uttrakhand | Tahir DTC System Uttrakhand | DTC System | the call was raised for alarm sink, but customer is giving time to do the activity on 8 th september So the work will be completed on 8th september | Repair |  | 10- Closed | 2023-09-06 19:05 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 245 | INR | 245 | ENM SECURE POWER
WO-11211164 | 103760807 | 2023-09-04 22:11 | 2023-09-04 |  | 2023-09-04 14:26 | APC Smart-UPS RC 6000VA 230V for India - No Batteries | SRC6KUXI | SRC6KUXI | B21508000114 | Call id INC0004358662 UPS Vendor Format 1. Asset Code : 15A-AIR-H-00234 2. Serail No : B21508000114 3. Type : UPS / UPS - Battery : UPS 4. Make: APC 6. Model : APC 6 KVA UPS 7. WSD : 04/01/2019 8. WED : 03/31/2020 9. Asset Status as per SCCD : Active 1 S:AMC | 2023-09-04 | 2023-09-06 14:50 | No | Contract | HDFC Bank Ltd | HDFC Bank B4/5 Princess Road Model Town Delhi | New Delhi | 110009 | Delhi | India FS North1 HBN CSP TCS IT Solutions Delhi | Sanjay Kumar_TCS IT Solutions Delhi | TCS IT Solutions | on site visit checked ups found input supply voltage down ups working fine but ups working on observation mode still no any calls from user side so as discussed with engineer this time doing case close if any receive complaint from user side that time we will re-log this case | Repair |  | 10- Closed | 2023-09-10 19:12 |  |  | 8 | INR | 8 | ENM SECURE POWER
WO-11211260 | 103764279 | 2023-09-05 17:02 | 2023-09-04 |  | 2023-09-04 15:11 | EFC 1.3TR, Downflow, Bottom Discharge | WDF0181BN001 | WDF0181BN001 | JK1327030195 | P:AC Cooling issue---jk1327030195 Under AMC P:AC Cooling issue---jk1327030195 S:AMC | 2023-09-04 | 2023-09-05 17:04 | No | Contract | Reliance Jio Infocomm Ltd. | Nandeo Vilas Rao Ghungrud Plot Survey no 60/2 Mouza Kawadghat | Wardha | 442301 | Maharashtra | India FS West2 Cooling CSP Gale HVAC Pune | Yesudas Sing Gale HVAC Pune | GALE HVAC | We have attend your site found Unit capacity is low in order to site load, need to be replace/ upgrade the unit | Repair |  | 10- Closed | 2023-09-05 17:06 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 700 | INR | 700 | ENM SECURE POWER
WO-11211361 | 103765454 | 2023-09-04 18:11 | 2023-09-04 |  | 2023-09-04 15:49 | APC Symmetra LX 16kVA N+1 Tower Frame, 220/230/240V or 380/400/415V | SYAF16KI | SYAF16KI | QD0850160469 | FW: IM02982677 MH-BYR-02 UPS POWER MODULE ISSUE Site code: IM02982677 MH-BYR-02 UPS POWER MODULE ISSUE Serial# QD0850160469 P: Power module faulty S: AMC | 2023-09-04 | 2023-09-06 18:29 | No | Contract | Central Board of Excise & Customs-CBEC | ?Atharva 3rd and 4th Floor, Behind Payyade Residency,Mira Bhayander Road, Bhayander(East),Distt Thane | Thane | 401105 | Maharashtra | India FS West1 HBN CSP_Mahavir Sys Power Pvt Ltd Goregoan | SAGAR PANDHARE_Mahavir Sys Power Pvt Ltd Goregoan | Mahavir Sys Power Pvt Ltd -Goregaon | FSR visited customer site found fault L1 after reset power module working call 2day under observation ups working fine call closed | Repair |  | 8- Service Completed | 2023-09-06 18:35 |  |  | 25 | INR | 25 | ENM SECURE POWER
WO-11211460 | 103765991 | 2023-09-05 18:14 | 2023-09-04 |  | 2023-09-04 16:12 | EFC MONOBLOCK 1.3TR R410A START KIT RS485 SEQ CONTROL | WDF0181BN040-1 | WDF0181BN040-1 | JK2046002180 | FW: Log Repair call RJIL Dholka In-warranty P: Unit not working S:Onsite | 2023-09-04 | 2023-09-04 23:00 | No | Warranty | Reliance Jio Infocomm Ltd. | Kheda-Bagodara highway Dhalaka Babdura highway swamy narayan society Maghiya Dholka | Dholka | 382225 | Gujarat | India FS West2 Cooling CSP Comfort HVAC Solutions Ahd | Rajesh Pramanik_Comfort HVAC Solutions Ahd | Comfort HVAC Solutions | Site Visit done | Repair |  | 10- Closed | 2023-09-05 18:18 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 55 | INR | 55 | ENM SECURE POWER
WO-11211562 | 103742789 | 2023-09-04 21:10 | 2023-09-04 |  | 2023-09-04 16:35 | MISCELLANEOUS ANCILLARY EQUIPMENT | ANC-MISC | ANC-MISC | IK-RAC-35A-SS-AF-5600 | Serial Number:B21504002541,Ac Serial No-IK-RAC-35A-55-AF-5600 Model Number:APC / APC 6 KVA UPS Customer Site Address along with Pin Code:HDFC BANK LTD, Plot Number - 634, Ganesh Bazaar, Main Road, Phulbani, Odisha - 762001 Name of the contact person at s | 2023-09-04 | 2023-09-05 19:36 | No | Contract | HDFC Bank Ltd | HDFC Bank Branch 4238_Phulabani Plot Number - 634, Ganesh Bazaar, Main | Phulbani | 762001 | Odisha | India FS East Cooling CSP Cool Care Refrigerant Bhubaneshwar | Madhusudan Nayak_Cool Care Refrigerant Bhubaneshwar | Cool Care Refrigerant | WE attend the site found compresor capacitor faulty ,replaced capacitor ,now ac running ok . | Repair |  | 10- Closed | 2023-09-05 19:37 |  |  | 245 | INR | 245 | ENM SECURE POWER
WO-11211583 | 103766565 | 2023-09-04 17:43 | 2023-09-04 |  | 2023-09-04 16:45 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | JK1930002442 | HP Alaram Serial# JK1930002442 P:HP Alaram S:AMC | 2023-09-04 | 2023-09-05 16:24 | No | Contract | Reliance JIO | Village Sakras Post-Sakras Tehsil Firozpur Zhirka Dist ? NUH | Mewat | 122108 | Haryana | India FS North1 Cooling CSP Smart Engineering Services Delhi | Sunil Kumar Smart Engineering Services Delhi | Smart Engineering Services | VISIT AND FOUND DISPAY UNDER LOW VOLTAGE ALARM (185) FROM CUSTOMER SIDE ISSUE, WE HAVE ADJUST THE VOLTAGE, CHECKED ALL PARAMETERS, NOW UNIT IS WORKING OK | Repair |  | 10- Closed | 2023-09-05 16:29 |  |  | 74 | INR | 74 | ENM SECURE POWER
WO-11211585 | 103766831 | 2023-09-04 17:05 | 2023-09-04 |  | 2023-09-04 16:46 | Leonardo EV,DX,R22,EC Fan,TDAV0811A,Downflow Without Heater & Humidifier | TDAV0811AN001 | TDAV0811AN001 | ZK1329003910 | FW: Call log for Reliance Ag2 Ulhasnagar. Under AMC P: Low Pressure Alarm S:AMC | 2023-09-04 | 2023-09-04 18:04 | No | Contract | Reliance Industries Ltd. | Reliance Corporate Park, Bldg. no. 6, D-wing, 2nd floor, Thane- Belapur Road, | Mumbai | 400701 | Maharashtra | India FS West1 Cooling CSP Shree Krishma Services Mumbai | Mahendra Suryabali Sharma_Shree Krishma Services Mumbai | Shree Krishna Services | P: Low Pressure Alarm Site visit done for Low pressure alarm. As per site visit we have checked all Electricals Parameter's and wire connections found ok check Expansions checked and found Expansion valve status not showing so reset programmer & install new programing and started the unit working ok. Now showing Expansions valve status 7 all parameter's now unit workings ok. | Repair |  | 10- Closed | 2023-09-04 18:10 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 50 | INR | 50 | ENM SECURE POWER
WO-11211641 | 103763593 | 2023-09-05 10:30 | 2023-09-04 |  | 2023-09-04 17:11 | SRCE6KUXIQ | SRCE6KUXIQ | SRCE6KUXI | BQ1910010462 | HDFC -call Under AMC P:not working no out put S:AMC | 2023-09-04 | 2023-09-05 11:54 | No | Contract | HDFC Bank Ltd | HDFC Bank Branch Raisinghnagar 24 Purani Dhanmandi Raisinghnagar Dist Ganganagar | Raisinghnagar | 335051 | Rajasthan | India FS North1 HBN CSP Legacy Systems Jaipur | Rajendra Kumar Legacy Systems Jaipur | Legacy Systems | visit the site unit no out put issue so reset all the setting and test working fine . | Repair |  | 9- Service Validated | 2023-09-05 11:54 |  |  | 450 | INR | 450 | ENM SECURE POWER
WO-11211716 | 103768277 | 2023-09-04 21:05 | 2023-09-04 |  | 2023-09-04 17:38 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | JK1920004084 | P:Cooling issue--jk1920004084 Under AMC P:Cooling issue--jk1920004084 S:AMC | 2023-09-04 | 2023-09-06 11:58 | No | Contract | Reliance Jio Infocomm Ltd | manikpur chock, sariya muzaffarpur | Muzaffarpur | 843143 | Bihar | India FS East Cooling CSP Cool Care Refrigerant Bhubaneshwar | Satyaranjan Rout_Cool Care Refrigerant Bhubaneshwar | Cool Care Refrigerant | we attend the site found condensor fan faulty ,repalced condensor motor ,now efc running ok . | Repair |  | 10- Closed | 2023-09-06 12:00 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 319 | INR | 319 | ENM SECURE POWER
WO-11211776 | 103769080 | 2023-09-05 09:07 | 2023-09-07 |  | 2023-09-04 18:08 | APC Smart-UPS RT 10000VA 230V Harsh Environment | SURT10000XLI-CC | SURT10000XLI-CC | B21609000438 | FW: RR : IM15437511 ¦ Store Code : 5908 ¦ SCHNEIDER ¦ JHARKHAND -TRENDS Under AMC P:UPS not working S:AMC | 2023-09-04 | 2023-09-07 15:23 | No | Contract | Reliance Retail | Reliance Trends Indra Lok Tower Gwala Toli Main Road | Hazaribagh | 825301 | Jharkhand | India FS East HBN CSP Power Solution Ranchi | KAMRANUL HAQUE_Power Solution Ranchi | Power Solution-Ranchi | unit replaced part no SRC10KUXIQ SL# BQ1602000527 old SURT10000XLI-CC sl# B21609000438 unit is working ok 02 nos RBC44 hand over call has been closed. | Repair |  | 10- Closed | 2023-09-07 15:23 |  |  | 102 | INR | 102 | ENM SECURE POWER
WO-11213552 | 103780167 | 2023-09-05 18:34 | 2023-09-05 |  | 2023-09-05 08:58 | TDAV1822AN004 | TDAV1822AN004 | TDAV1822AN004 | C21844000954 | Pac complaint P:High condensing pressure or compr.contactor failed S:AMC | 2023-09-05 | 2023-09-05 21:02 | No | Contract | Bharti Airtel Ltd | C1 18 patliputra industrial area, Near coca cola bottling plant | Patna | 800024 | Bihar | India FS East Cooling CSP Cool Care Refrigerant Bhubaneshwar | Satyaranjan Rout_Cool Care Refrigerant Bhubaneshwar | Cool Care Refrigerant | WE ATTEND the site found hp switch faulty ,replaced hp switch ,now pac running ok . | Repair |  | 10- Closed | 2023-09-05 21:03 |  |  | 300 | INR | 300 | ENM SECURE POWER
WO-11213593 | 103780938 | 2023-09-05 12:12 | 2023-09-05 |  | 2023-09-05 09:31 | BR1500G-INNBQ | BR1000G-INNBQ | BR1000G-IN | EQ1419004936 | CALL LOCK TO BE MARUTI SUZUKI P:F02 ERROR S:AMC | 2023-09-05 | 2023-09-05 13:10 | No | Contract | Maruti Suzuki India Pvt ltd | Plot No 1 Phase 3A IMT | Manesar | 122051 | Haryana | India FS North1 HBN CSP Prokon Hi Tech Systems Gurgaon | Deshraj D_Prokon Hi-Tech Systems Gurgaon | Prokon Hi-Tech Systems-Gurgaon | UPS properly checked but no problem found now ups working is okay. | Repair |  | 9- Service Validated | 2023-09-05 13:10 |  |  | 25 | INR | 25 | ENM SECURE POWER
WO-11213602 | 103781087 | 2023-09-05 12:13 | 2023-09-05 |  | 2023-09-05 09:38 | BR1500G-INNBQ | BR1500G-INNBQ | BR1500G-IN | BQ1821020184 | CALL LOCK TO BE MARUTI SUZUKI P:aut on / offissue S:AMC | 2023-09-05 | 2023-09-05 13:12 | No | Contract | Maruti Suzuki India Pvt ltd | Plot No 1 Phase 3A IMT | Manesar | 122051 | Haryana | India FS North1 HBN CSP Prokon Hi Tech Systems Gurgaon | Krishna Kumar_Prokon Hi-Tech Systems Gurgaon | Prokon Hi-Tech Systems-Gurgaon | UPS battery faulty replaced the new battery now ups working is okay. | Repair |  | 10- Closed | 2023-09-05 13:23 |  |  | 25 | INR | 25 | ENM SECURE POWER
WO-11213603 | 103781093 | 2023-09-05 12:14 | 2023-09-05 |  | 2023-09-05 09:38 | BR1500G-INNBQ | BR1500G-INNBQ | BR1500G-IN | BQ1825006638 | CALL LOCK TO BE MARUTI SUZUKI F02 ERROR | 2023-09-05 | 2023-09-05 13:13 | No | Contract | Maruti Suzuki India Limited | Plot No-1 Phase 3A, IMT Manesar | Gurgaon | 121001 | Haryana | India FS North1 HBN CSP Prokon Hi Tech Systems Gurgaon | Krishna Kumar_Prokon Hi-Tech Systems Gurgaon | Prokon Hi-Tech Systems-Gurgaon | UPS properly checked but no problem found in ups, now ups working is okay. | Repair |  | 10- Closed | 2023-09-05 13:24 |  |  | 25 | INR | 25 | ENM SECURE POWER
WO-11213609 | 103781171 | 2023-09-05 12:16 | 2023-09-05 |  | 2023-09-05 09:42 | BR1500G-INNBQ | BR1500G-INNBQ | BR1500G-IN | EQ1415025959 | CALL LOCK TO BE MARUTI SUZUKI P:aut on / offissue S:AMC | 2023-09-05 | 2023-09-05 13:16 | No | Contract | Maruti Suzuki India Pvt ltd | Plot No 1 Phase 3A IMT | Manesar | 122051 | Haryana | India FS North1 HBN CSP Prokon Hi Tech Systems Gurgaon | Krishna Kumar_Prokon Hi-Tech Systems Gurgaon | Prokon Hi-Tech Systems-Gurgaon | UPS properly checked but no problem found in ups, now ups working is okay. | Repair |  | 10- Closed | 2023-09-05 13:24 |  |  | 25 | INR | 25 | ENM SECURE POWER
WO-11213613 | 103781217 | 2023-09-05 12:17 | 2023-09-05 |  | 2023-09-05 09:45 | BR1500G-INNBQ | BR1500G-INNBQ | BR1500G-IN | BQ1703001811 | CALL LOCK TO BE MARUTI SUZUKI P:aut on / offissue S:AMC | 2023-09-05 | 2023-09-05 15:09 | No | Contract | Maruti Suzuki India Limited | Plot No-1 Phase 3A, IMT Manesar | Gurgaon | 121001 | Haryana | India FS North1 HBN CSP Prokon Hi Tech Systems Gurgaon | Deshraj D_Prokon Hi-Tech Systems Gurgaon | Prokon Hi-Tech Systems-Gurgaon | UPS not powering on replaced the new ups, now ups working is okay. Model no BR1500G-INNBQ Serial no BQ2248001000 | Repair |  | 10- Closed | 2023-09-05 15:13 |  |  | 25 | INR | 25 | ENM SECURE POWER
WO-11216086 | 103792250 | 2023-09-05 18:02 | 2023-09-05 |  | 2023-09-05 15:42 | APC Symmetra LX 16kVA N+1 Ext. Run Tower Frame, 220/230/240V or 380/400/415V | SYAF16KXR9I | SYAF16KXR9I | QD0826360022 | Ups Power Module issue P:Ups Power Module issue S:AMC | 2023-09-05 | 2023-09-06 15:00 | No | Contract | Central Board of Excise & Customs-CBEC | IP Estate D Block IP Bhawan 5th Floor | New Delhi | 110002 | Delhi | India FS North1 HBN CSP HITEK BUSINESS SYSTEMS PVT LTD Delhi | Mangal M_Hitek Business Systems New Delhi | Hitek Business Systems Pvt Ltd | Engineer this site UPS check found battery module reset UPS working ok | Repair |  | 10- Closed | 2023-09-06 15:55 |  |  | 15 | INR | 15 | ENM SECURE POWER
WO-11161817 | 103525960 | 2023-08-26 15:50 | 2023-08-25 |  | 2023-08-25 10:22 | LV563510 | LV563510 | LV563510 |  | Checklist for Complaint Registration 1 Name of Customer DELTA ELCTRONICS INDIA PVT LTD 2 Site Address PLOT NO 15 SEC-33 INFOCITY 2 NEAR BY HERO HONDA CHOWK GURUGRAM 122003 3 Name of contact person at site Chaman Ranga -9212796973 4 Contact Phone / Mob. No: 9910015705 5 Defective product details LV563510=01, A9N3P63C=01, A9N4P32D=06, A9N2P32D=01, LC1DT55ED=01, A9N1P63C=01 6 Nature of Defect SWITCH FREE AND CONNECTING ISSUE 7 Shutdown availability if applicable 8 Warranty status 1 YEAR 9 Distributor Name,Invoice # & Date ELECTRICAL CONTROL SYSTEMS,INV N0- 9008626913 DT. 01/07/23, 9008639920 DT. 12/07/23 10 Serial No: or DOM of the product 11 Name & phone No: of person registering the complaint Ashish Malik : 9910015705 | 2023-08-25 | 2023-08-30 17:48 | No | Warranty | Delta Elctronics India Pvt Ltd | Plot No 15 Sec-33 Infocity 2 Near By Hero Honda Chowk | Gurgaon | 122003 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mcb found phase missing / dolly free and contactor found phase missing, Hence faulty replaced. LV563510 - 1 nos A9N3P63C - 1 nos A9N1P63C - 1 nos A9N4P32D - 6 nos A9N2P32D - 1 nos LC1DT55ED - 1 nos | Repair |  | 9- Service Validated | 2023-09-03 14:29 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11214466 |  | 2023-09-06 11:09 | 2023-09-05 |  | 2023-09-05 10:47 | Leonardo EV,DX,R407c,EC Fan,TDAV1021A,Downflow With Heater & Humidifier | TDAV1021AN002 | TDAV1021AN002 | NUCU3424 | pm | 2023-09-05 | 2023-09-06 13:20 | No | Contract | paschimanchal Vidyut Vitran Nigam limited | Plot # B1 DR Center, Sector 58 Sector 58 | GAUTAM BUDDHA NAGAR | 201301 | Uttar Pradesh | India FS North2 Cooling CSP D K AIRCON Delhi | Pintu Kumar D K AIRCON Delhi | DK AIRCON | Preventive Maintenance work done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-06 14:54 |  |  | 14 | INR | 14 | ENM SECURE POWER
WO-11214569 |  | 2023-09-06 11:18 | 2023-09-05 |  | 2023-09-05 10:48 | Leonardo EV,DX,R407c,EC Fan,TDAV1021A,Downflow With Heater & Humidifier | TDAV1021AN002 | TDAV1021AN002 | NUCU3427 | pm | 2023-09-05 | 2023-09-06 12:40 | No | Contract | paschimanchal Vidyut Vitran Nigam limited | Plot # B1 DR Center, Sector 58 Sector 58 | GAUTAM BUDDHA NAGAR | 201301 | Uttar Pradesh | India FS North2 Cooling CSP D K AIRCON Delhi | Pintu Kumar D K AIRCON Delhi | DK AIRCON | Preventive Maintenance work done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-06 14:49 |  |  | 14 | INR | 14 | ENM SECURE POWER
WO-11214984 |  | 2023-09-23 12:26 | 2023-09-05 |  | 2023-09-05 10:54 | IDAV1311AN-CPD | UFDX | UFDX | JK2132001871 | pm | 2023-09-05 | 2023-09-26 15:50 | No | Commercial Action - Service Ops | Samsung India Electronics Pvt Ltd | Tower No.11 ,Plot No.20-21,IT/ITES SEZ,SECTOR 135 null | NOIDA | 201304 | Uttar Pradesh | India FS North2 Cooling CSP D K AIRCON Delhi | Ajay Kumar_D K AIRCON Delhi | DK AIRCON | Preventive Maintenance work done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-27 12:00 |  |  | 32 | INR | 32 | ENM SECURE POWER
WO-11214567 |  | 2023-09-06 11:13 | 2023-09-05 |  | 2023-09-05 10:47 | Leonardo EV,DX,R407c,EC Fan,TDAV1021A,Downflow With Heater & Humidifier | TDAV1021AN002 | TDAV1021AN002 | NUCU3425 | pm | 2023-09-05 | 2023-09-06 13:00 | No | Contract | paschimanchal Vidyut Vitran Nigam limited | Plot # B1 DR Center, Sector 58 Sector 58 | GAUTAM BUDDHA NAGAR | 201301 | Uttar Pradesh | India FS North2 Cooling CSP D K AIRCON Delhi | Pintu Kumar D K AIRCON Delhi | DK AIRCON | Preventive Maintenance work done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-06 14:52 |  |  | 14 | INR | 14 | ENM SECURE POWER
WO-11214571 |  | 2023-09-06 11:27 | 2023-09-05 |  | 2023-09-05 10:48 | Leonardo EV,DX,R407c,EC Fan,TDAV1021A,Downflow With Heater & Humidifier | TDAV1021AN002 | TDAV1021AN002 | NUCU3429 | pm | 2023-09-05 | 2023-09-06 12:20 | No | Contract | paschimanchal Vidyut Vitran Nigam limited | Plot # B1 DR Center, Sector 58 Sector 58 | GAUTAM BUDDHA NAGAR | 201301 | Uttar Pradesh | India FS North2 Cooling CSP D K AIRCON Delhi | Mubarak Ali_D K AIRCON Delhi | DK AIRCON | Preventive Maintenance work done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-06 14:43 |  |  | 14 | INR | 14 | ENM SECURE POWER
WO-11214983 |  | 2023-09-23 12:24 | 2023-09-05 |  | 2023-09-05 10:54 | IDAV1311AN-CPD | IDAV1021A | IDAV1021A | JK2130000809 | pm | 2023-09-05 | 2023-09-26 15:30 | No | Commercial Action - Service Ops | Samsung India Electronics Pvt Ltd | Tower No.11 ,Plot No.20-21,IT/ITES SEZ,SECTOR 135 null | NOIDA | 201304 | Uttar Pradesh | India FS North2 Cooling CSP D K AIRCON Delhi | Ajay Kumar_D K AIRCON Delhi | DK AIRCON | Preventive Maintenance work done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-27 10:02 |  |  | 32 | INR | 32 | ENM SECURE POWER
WO-11214568 |  | 2023-09-06 11:21 | 2023-09-05 |  | 2023-09-05 10:47 | Leonardo EV,DX,R407c,EC Fan,TDAV1021A,Downflow With Heater & Humidifier | TDAV1021AN002 | TDAV1021AN002 | NUCU3426 | pm | 2023-09-05 | 2023-09-06 12:50 | No | Contract | paschimanchal Vidyut Vitran Nigam limited | Plot # B1 DR Center, Sector 58 Sector 58 | GAUTAM BUDDHA NAGAR | 201301 | Uttar Pradesh | India FS North2 Cooling CSP D K AIRCON Delhi | Pintu Kumar D K AIRCON Delhi | DK AIRCON | Preventive Maintenance work done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-06 14:50 |  |  | 14 | INR | 14 | ENM SECURE POWER
WO-11215092 |  | 2023-09-23 12:35 | 2023-09-05 |  | 2023-09-05 10:56 | TUAVQ | TUAVQ | TUAVQ | JK2202001256 | pm | 2023-09-05 | 2023-09-26 17:00 | No | Commercial Action - Service Ops | Samsung India Electronics Pvt Ltd | Tower No.11 ,Plot No.20-21,IT/ITES SEZ,SECTOR 135 null | NOIDA | 201304 | Uttar Pradesh | India FS North2 Cooling CSP D K AIRCON Delhi | Pintu Kumar D K AIRCON Delhi | DK AIRCON | Preventive Maintenance work done | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-27 15:10 |  |  | 32 | INR | 32 | ENM SECURE POWER
WO-11214570 |  | 2023-09-06 11:24 | 2023-09-05 |  | 2023-09-05 10:48 | Leonardo EV,DX,R407c,EC Fan,TDAV1021A,Downflow With Heater & Humidifier | TDAV1021AN002 | TDAV1021AN002 | NUCU3428 | pm | 2023-09-05 | 2023-09-06 12:30 | No | Contract | paschimanchal Vidyut Vitran Nigam limited | Plot # B1 DR Center, Sector 58 Sector 58 | GAUTAM BUDDHA NAGAR | 201301 | Uttar Pradesh | India FS North2 Cooling CSP D K AIRCON Delhi | Mubarak Ali_D K AIRCON Delhi | DK AIRCON | Preventive Maintenance work done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-06 14:46 |  |  | 14 | INR | 14 | ENM SECURE POWER
WO-11214672 |  | 2023-09-06 11:30 | 2023-09-05 |  | 2023-09-05 10:48 | Leonardo EV,DX,R407c,EC Fan,TDAV1021A,Downflow With Heater & Humidifier | TDAV1021AN002 | TDAV1021AN002 | NUCU3430 | pm | 2023-09-05 | 2023-09-06 12:10 | No | Contract | paschimanchal Vidyut Vitran Nigam limited | Plot # B1 DR Center, Sector 58 Sector 58 | GAUTAM BUDDHA NAGAR | 201301 | Uttar Pradesh | India FS North2 Cooling CSP D K AIRCON Delhi | Mubarak Ali_D K AIRCON Delhi | DK AIRCON | Preventive Maintenance work done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-06 14:41 |  |  | 14 | INR | 14 | ENM SECURE POWER
WO-11214674 |  | 2023-09-06 11:32 | 2023-09-05 |  | 2023-09-05 10:49 | Leonardo EV,DX,R407c,EC Fan,TDAV1021A,Downflow With Heater & Humidifier | TDAV1021AN002 | TDAV1021AN002 | NUCU3431 | pm | 2023-09-05 | 2023-09-06 12:00 | No | Commercial Action - Service Ops | paschimanchal Vidyut Vitran Nigam limited | Plot # B1 DR Center, Sector 58 Sector 58 | GAUTAM BUDDHA NAGAR | 201301 | Uttar Pradesh | India FS North2 Cooling CSP D K AIRCON Delhi | Mubarak Ali_D K AIRCON Delhi | DK AIRCON | Preventive Maintenance work done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-06 14:38 |  |  | 14 | INR | 14 | ENM SECURE POWER
WO-11215086 |  | 2023-09-23 12:28 | 2023-09-05 |  | 2023-09-05 10:54 | IDAV1311AN-CPD | IDAV0601A | IDAV0601A | JK2132001872 | pm | 2023-09-05 | 2023-09-26 16:00 | No | Commercial Action - Service Ops | Samsung India Electronics Pvt Ltd | Tower No.11 ,Plot No.20-21,IT/ITES SEZ,SECTOR 135 null | NOIDA | 201304 | Uttar Pradesh | India FS North2 Cooling CSP D K AIRCON Delhi | Ajay Kumar_D K AIRCON Delhi | DK AIRCON | Preventive Maintenance work done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-27 12:28 |  |  | 32 | INR | 32 | ENM SECURE POWER
WO-11178335 | 103597361 | 2023-08-29 15:49 | 2023-08-29 |  | 2023-08-29 11:56 | LC1E65M7 | LC1E65M7 | LC1E65M7 |  | Checklist for Complaint Registration Doc. Ref :- SE/CCC/001 1 Company Name & Complete Address with pin code - Where product is installed Hari Shankar Singhania Elastomer & Tyre Research Institute Raghupati Singhaniya Center of Excellence 437,Hebbal Industrial Area, Mysor-570016, Karnataka 2 Contact Person at Site : Name & Mobile No. Mr. Pranav Tripathi Alternate Mobile No : 9784124424 3 Contact Person at Site - Email Address** cooleng@outlook.com 4 Defective Product Model/Part No (Pls refer FAQ sheet ) LC1E65M7 5 Nature of Defect* - Defects Video and Photographs Y & B -Phase is heating 6 Shutdown availability if applicable 0 7 POP - SE Authorised Partner Invoice soft copy S.K.Traders Invoice No: 231028 dated 14/07/22 to Cool Engg. 8 Photograph of product where Serial No/Batch Code or Date of Manufacturing printed - Please refer FAQ sheet 9 Name & phone No: of person registering the complaint Kothale S.S 9373169403 "Points 1,2,3,4,5 & (7or8) are mandatory. * Kindly share defect symptoms instead of ""Not working"", Please share the link of large files(product photoes or videoes) ** End user will receive a survey asking feedback on service " POP - Proof of Purchase Please fill above details and send this sheet to customer care, Customer care contact link is give below https://www.se.com/in/en/work/support/contacts.jsp Please mention Complaint as key word and Product Name in email subject line e.g for Masterpact NW ACB complaint - Complaint for Masterpact NW Our web site :- https://www.se.com/in/en/ | 2023-08-29 | 2023-09-01 14:05 | No | Warranty | HASETRI | 437, Raghupati Singhania Centre of Excellence, Hebbal Industrial Estate, Hebbal Industrial Area | Mysore | 570016 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Chethan SC P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | Inspected and found 1)LC1E65M7 S/N:WH2207 contactor output side. We suspected cable loose termination. customer as use new cable termination, after tested contactor output working fine.Contactor ON/OFF also tested working found ok. There is no problem in our products. | Repair |  | 9- Service Validated | 2023-09-01 14:06 |  |  | 155 | INR | 155 | ENM POWER PRODUCTS
WO-11215087 |  | 2023-09-23 12:30 | 2023-09-05 |  | 2023-09-05 10:55 | IDAV1311AN-CPD | UFDX | UFDX | JK2137003597 | pm | 2023-09-05 | 2023-09-26 16:20 | No | Commercial Action - Service Ops | Samsung India Electronics Pvt Ltd | Tower No.11 ,Plot No.20-21,IT/ITES SEZ,SECTOR 135 null | NOIDA | 201304 | Uttar Pradesh | India FS North2 Cooling CSP D K AIRCON Delhi | Ajay Kumar_D K AIRCON Delhi | DK AIRCON | Preventive Maintenance work done | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-27 15:01 |  |  | 32 | INR | 32 | ENM SECURE POWER
WO-11215089 |  | 2023-09-23 12:32 | 2023-09-05 |  | 2023-09-05 10:55 | IDAV1311AN-CPD | UFDX | UFDX | JK2151000241 | pm | 2023-09-05 | 2023-09-26 16:30 | No | Commercial Action - Service Ops | Samsung India Electronics Pvt Ltd | Tower No.11 ,Plot No.20-21,IT/ITES SEZ,SECTOR 135 null | NOIDA | 201304 | Uttar Pradesh | India FS North2 Cooling CSP D K AIRCON Delhi | Pintu Kumar D K AIRCON Delhi | DK AIRCON | Preventive Maintenance work done | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-27 15:20 |  |  | 32 | INR | 32 | ENM SECURE POWER
WO-11215090 |  | 2023-09-23 12:33 | 2023-09-05 |  | 2023-09-05 10:55 | IDAV1311AN-CPD | UFDX | UFDX | JK2151000242 | pm | 2023-09-05 | 2023-09-26 16:40 | No | Commercial Action - Service Ops | Samsung India Electronics Pvt Ltd | Tower No.11 ,Plot No.20-21,IT/ITES SEZ,SECTOR 135 null | NOIDA | 201304 | Uttar Pradesh | India FS North2 Cooling CSP D K AIRCON Delhi | Pintu Kumar D K AIRCON Delhi | DK AIRCON | Preventive Maintenance work done | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-27 15:14 |  |  | 32 | INR | 32 | ENM SECURE POWER
WO-11183144 | 103653890 | 2023-08-31 11:02 | 2023-08-30 |  | 2023-08-30 12:13 | LC1F1504M7 | LC1F1504M7 | LC1F1504M7 | pk2141 | lc1f1504m7 pk2141 Not holding at 220 padma city mall Karnal Road Near Mini Secretariat near jat ground Haryana 136027 Pawan kumar 95186311199 chawlapawan.chawla4141@gmail.com | 2023-08-30 | 2023-08-31 16:36 | No | Warranty | padma city mall | Karnal Road Near Mini Secretariat near jat ground null | KAITHAL | 136027 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the contactor found mechanism interlocking b / w AMF Circuit panel , contactor on/ off afferently no problem in contactor, suggest to customer for check control wiring or logic circuit. Hence no replacement given to customer. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-01 21:03 |  |  | 130 | INR | 130 | ENM POWER PRODUCTS
WO-11215194 |  | 2023-09-23 12:37 | 2023-10-28 |  | 2023-09-05 10:56 | TUAVQ | TUAVQ | TUAVQ | JK2204006471 | pm | 2023-09-05 | 2023-09-26 17:30 | No | Commercial Action - Service Ops | Samsung India Electronics Pvt Ltd | Tower No.11 ,Plot No.20-21,IT/ITES SEZ,SECTOR 135 null | NOIDA | 201304 | Uttar Pradesh | India FS North2 Cooling CSP D K AIRCON Delhi | Pintu Kumar D K AIRCON Delhi | DK AIRCON | Preventive Maintenance work done | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-27 15:27 |  |  | 32 | INR | 32 | ENM SECURE POWER
WO-11183187 | 103653462 | 2023-08-30 19:46 | 2023-08-30 |  | 2023-08-30 12:36 | INA_4P93284_20 | INA_4P93284_20 | INA_4P93284_20 |  | Dear Sir, With reference to the above subject, please note that, 1 no. of the 800A 4P MOT. MCCB is not working properly, in the sense that, the MCCB is in ON condition only & it is not getting Off. Please note that it has been purchased by M/s Maiyar Techno systems in Jan 2023 & photo of the MCCB Sl. nO. is attached with this mail for your reference. Kindly depute your service engineer & rectify the same asap. Contact Person : Mr. Ganesh + 91 9900018182 Address; As below -- S.V.KARANTH TECHNO SYSTEMS No.09 & 10, Sy.No.79/4, 4th Cross, Doddamma Industrial area, Hulimavu, Bannerghatta road, Bangalore-76 | 2023-08-30 | 2023-09-01 11:00 | No | Warranty | S.V.KARANTH TECHNO SYSTEMS | No.09 & 10, Sy.No.79/4, 4th Cross, Doddamma Industrial area, Hulimavu, Bannerghatta road, | Bangalore | 560068 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Mohammad Riyaz_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported ns800A 4P mccb, the problem found was mccb not getting ON due to main mechanism issue. So we had arranged for the replacement and zvo directly booked to maiyar techno systems. | Repair |  | 9- Service Validated | 2023-09-01 19:24 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11215196 | 103782136 | 2023-09-05 14:29 | 2023-09-05 |  | 2023-09-05 10:56 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | C21651000219 | Request for log of repair call Reliance Jio, Songadh under AMC P:Temp. Sensor problem. S:AMC | 2023-09-05 | 2023-09-05 12:00 | No | Contract | Reliance Jio Infocomm Ltd | CS No. 1785,1786, 1787/P, Junagam Main Road, Songadh | Tapi | 394670 | Gujarat | India FS West2 Cooling CSP DECENT HVAC SYSTEM Gandhinagar | Mickey Kabrawala DECENT HVAC SYSTEM Gandhinagar | DECENT HVAC SYSTEM | Complaint attend, temp. sensor replaced. (> 240 Km) | Repair |  | 10- Closed | 2023-09-05 14:42 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 360 | INR | 360 | ENM SECURE POWER
WO-11183534 | 103661017 | 2023-08-31 11:03 | 2023-08-30 |  | 2023-08-30 15:31 | GV2ME08 | GV2ME08 | GV2ME08 | th2217 | gv2me08 th2217 Phase missing Mohit 9588315857 JP electricals | 2023-08-30 | 2023-09-02 16:36 | No | Warranty | J.P. Electricals | 45B, Narain Singh Park, Opp Hali Park, | Panipat | 132103 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | checked the mcb found phase missing and mpcb found not getting on due to mechanism faulty, replaced. A9N3P63C- 1NOS GV3P50- 1 NOS Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-02 16:40 |  |  | 165 | INR | 165 | ENM POWER PRODUCTS
WO-11215330 | 103782210 | 2023-09-05 11:13 | 2023-09-05 |  | 2023-09-05 11:07 | WDF0181BN003 | ANC-MISC | ANC-MISC | C21708001054 | RJIL BF Call log - Mandya - M/s. Fresco under AMC P:No cooling & water leakage S:AMC | 2023-09-05 | 2023-09-05 17:34 | No | Contract | Reliance Jio | No.1761, 1st Cross, bandigowda Layout | Mandya | 571401 | Karnataka | India FS South3 Cooling CSP Fresco solutions Bangalore | Shivalinga S_Fresco solutions Bangalore | Fresco solutions | rat bite issue rectified | Repair |  | 10- Closed | 2023-09-05 17:37 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 125 | INR | 125 | ENM SECURE POWER
WO-11215386 | 103781271 | 2023-09-05 14:54 | 2023-09-05 |  | 2023-09-05 11:22 | Big Chillers | BREC | BREC | SRF032716 | "Fans Thermal circuit 2" alarm observed on Chiller #13. P:"Fans Thermal circuit 2" alarm observed on Chiller #13 S:AMC | 2023-09-05 | 2023-09-05 18:15 | No | Contract | Netmagic IT Services Pvt. Ltd. | DC-08, Lighthall, C Wing, Hiranandani Business Park, Saki Vihar Road, Chandivali, | MUMBAI | 400072 | Maharashtra | India FS West1 Cooling CSP Unique India Mumbai | Shameem Akhter_Unique India Mumbai | Unique India- Mumbai HBN CSP | Site visited for fan thermal alarm in chiller no 13, we have checked and found the chiller fan no 16 not running, checked all electrical inputs found okay , declared fan faulty which need to be replace. | Repair |  | 10- Closed | 2023-09-05 22:23 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11188002 | 103691925 | 2023-08-31 19:05 | 2023-08-31 |  | 2023-08-31 14:26 | LC1DMK11M7 | LC1DMK11M7 | LC1DMK11M7 |  | LC1DMK11M7 3nos 2F23042 2F23044 2F21465 2F23044 Chattering sound when 220V applied Dileep 7022694574 Guru Industrial supplier No 48 railway station road periyarnagar shanthi nagar east opposit murugan temple Hosur 635109 | 2023-08-31 | 2023-09-01 15:00 | No | Warranty | GURU INDUSTRIAL SUPPLIERS | NO. 48, GURU INDUSTRIAL SUPPLIERS, RAILWAY STATION ROAD, HOSUR null | Krishnagiri | 635109 | Tamil Nadu | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | MANOJ GANESAN SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported cap duty contactors the problem found was chattering sound issue due to dust at e core. We cleaned the dust and checked found working ok. The same shown to the customer. | Repair |  | 9- Service Validated | 2023-09-01 19:40 |  |  | 55 | INR | 55 | ENM POWER PRODUCTS
WO-11215388 |  | 2023-09-21 17:24 | 2023-09-21 |  | 2023-09-05 11:27 | SDC0600BN001 | SDC0600BN001 | SDC0600BN001 | C21643003470 | pm | 2023-09-05 | 2023-09-21 22:30 | No | Commercial Action - Service Ops | Sify Technologies Limited | Plot N7 Block-B Sector-132 G B Nagar Alwar Thirunagar | Noida | 201304 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Govind Tomar Freezeotech Airconditioning & Refrigeration GZB | Freezeotech Airconditioning & Refrigeration Corporation | PM DONE CLEAN THE FILTER WATER TREY DRAIN PIPE HUMDITIY BOTAL CHECK ALL PARAMETER UNIT IS WORKING OK | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-21 17:39 |  |  | 28 | INR | 28 | ENM SECURE POWER
WO-11194618 | 103720630 | 2023-09-02 12:08 | 2023-09-04 |  | 2023-09-01 14:19 | LV525303 | LV525303 | LV525303 |  | Checklist for the Registration of Service Request Sr. No Particulars Doc. Ref :- SE/CCC/001/V0.1 1 Company Name & Complete Address with pin code - Where product is installed "M/s. Suryadev Alloys & Power Pvt. Ltd No: 298/2, New Gummidipoondi Tiruvallur District - 601201" 2 Contact Person at Site : Name & Mobile No. Mr.Prashanth - 8925828949 Alternate Mobile No : Mr.Venkatesan - 9500144386 3 Contact Person at Site - Email Address** support@vectorsolutionsindia.com 4 Product Issue Type (Please select from drop down of column C-9) 5 Are you ready to troubleshoot the issue remotely ? Yes/NO. If Yes, Our technical support engineer will call back to troubleshoot the issue remotely. 6 Defective Product Model/Part No (Pls refer FAQ sheet ) LV525303 7 Nature of Defect* - Defects Video and Photographs MCCB tripping Frequently 8 Shutdown availability if applicable 9 Photograph of product where Serial No/Batch Code or Date of Manufacturing printed - Please refer FAQ sheet to find the Batch code details on the products 10 Proof Of Purchase - Pease attach SE*** Authorised Partner Invoice soft copy along with this check list Please send soft compies along with this check list. 11 Name & phone No: of person registering the Service Request Bharath Waj P - 90870 09321 "All fields are mandatory. Free of cost service visit subjected to warranty policy of the product and contract between Schneider Electric and buying party . Warranty will be check either by serial no/Batch code/DOM printed on the product or date of invoice of our authorised partner /Schneider Electric direct invoice or Contract . Warranty policy may be change product to product or contract with the customer. * Kindly share defect symptoms instead of ""Not working"", Please share the link of large files(product photoes or videoes) ** End user will receive a survey asking feedback on service " SE*** - Schneider Electric Please fill above details and send this sheet to customer care, Customer care contact link is give below https://www.se.com/in/en/work/support/customer-care/contact-schneider-electric.jsp Please mention Service Request as key word and Product Name in email subject line e.g for Masterpact NW ACB Service Request - Service Request for Masterpact NW Our web site :- https://www.se.com/in/en/ Product Issue Type Software/communication Issue Programing/Configuration Issue Hardware Issue Commissioning/ Installation Request Are you ready to troubleshoot the issue remotely ? Yes No | 2023-09-01 | 2023-09-04 18:00 | No | Warranty | Suryadev Alloys and Power Pvt Ltd | No.298/2, New Gummidipoondi, Gummidipoondi taluk | Thiruvallur dist | 601201 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | MCCB Tripping Issue | Repair |  | 9- Service Validated | 2023-09-04 18:56 |  |  | 55 | INR | 55 | ENM POWER PRODUCTS
WO-11195164 | 103720862 | 2023-09-01 17:16 | 2023-09-01 |  | 2023-09-01 16:40 | LV516302 | LV516302 | LV516302 |  | Dear Team, Inv. copy attached herewith. Checklist for Complaint Registration Doc. Ref :- SE/CCC/22-23/349 1 Company Name & Complete Address with pin code - Where product is installed GOYAL ELECTRICAL 2 SIDE ADRESS United Chemie Pvt. Ltd.,A/1/27, Nr. Doshian Ltd.,GIDC, Phase-2, Vatva, Ahmedabad-382445 3 Contact Person at Site: Name & Mobile No. 9687643917 4 Altemate Mobile No. : Nirav Patel - Cell No. : +91 76210 00796/ 76230 04562 5 Contact Person at Site - Email Address**. 6 Defective Product Model/Part No (Pls refer FAQ sheet ) LV516302 - 1 PC 6-a Defective Product Model/Part No (Pls refer FAQ sheet ) 6-b Defective Product Model/Part No (Pls refer FAQ sheet ) 6-c Defective Product Model/Part No (Pls refer FAQ sheet ) 6-d Defective Product Model/Part No (Pls refer FAQ sheet ) 6-e Defective Product Model/Part No (Pls refer FAQ sheet ) 6-f Defective Product Model/Part No (Pls refer FAQ sheet ) 7 Nature of Defect* - Defects Video and Photographs R - PHASE DISCONTINUE. 8 Shutdown availability if applicable 9 POP - SE Authorised Partner Invoice soft copy Invoice No - 105621 , Date - 12/07/2023 10 Photograph of product where Serial No/Batch Code or Date of Manufacturing printed - Please refer FAQ sheet 11 Name & phone No: of person registering the complaint SHAILESH MAKWANA - 9924227896 Points 1,2,3,4,5 & (7or8) are mandatory. * Kindly share defect symptoms instead of "Not working", Please share the link of large files(product photoes or videoes) ** End user will receive a survey asking feedback on service POP - Proof of Purchase Please fill above details and send this sheet to customer care, Customer care contact link is give below https://www.se.com/in/en/work/support/contacts.jsp | 2023-09-01 | 2023-09-02 12:36 | No | Warranty | UNITED CHEMIE PRIVATE LIMITED | G I D C Estate Vatva, A/1/27, Phase-2, Winzol Road Vatva null | Ahmedabad | 382445 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | Parthiv Patel JKS Ahmedabad | JKS Engineering Co. | We visit at site check mccb on/off working ok.check mccb tarminal y incomer fuse burning check the cable size of the cble 120mm alu check cable lug alu.we checked that spider link was not pinched between cable and lug.we suggest then to used to spider link. | Repair |  | 9- Service Validated | 2023-09-02 12:43 |  |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11215391 |  | 2023-09-21 17:41 | 2023-09-21 |  | 2023-09-05 11:27 | SDC0600BN001 | SDC0600BN001 | SDC0600BN001 | C21643002313 | pm | 2023-09-05 | 2023-09-21 23:30 | No | Commercial Action - Service Ops | Sify Technologies Limited | Plot N7 Block-B Sector-132 G B Nagar Alwar Thirunagar | Noida | 201304 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Govind Tomar Freezeotech Airconditioning & Refrigeration GZB | Freezeotech Airconditioning & Refrigeration Corporation | PM DONE CLEAN THE FILTER WATER TREY DRAIN PIPE HUMDITIY BOTAL CHECK ALL PARAMETER UNIT IS WORKING OK | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-21 17:51 |  |  | 28 | INR | 28 | ENM SECURE POWER
WO-11195205 | 103723116 | 2023-09-02 15:10 | 2023-09-01 | as per serial no. product in warranty raise ZVO for replacement | 2023-09-01 16:56 | CAD32B7 | CAD32B7 | CAD32B7 |  | Dear Sir/Madam Please Provide Complain number has per Attached Deta Checklist for Complaint Registration 1 Name of Customer M/S J K ELECTRONICS 2 Site Address A-19, JIVAN JYOT NAGAR FLATS NEAR DREAM HONDA, UDHNA, Gujarat, 394210 Contact Phone / Mob. No: 9375960626 3 Name of contact person at site MR.SUNIL. PATEL. 5 Defective product details CAD32 B7 - QTY - 2 6 Product Make SCHNEIDER-CONTACTOR 7 Nature of Defect NOT WORKING (1 POLE IS OPEN) 8 Shutdown availability if applicable 9 Warranty status UNDER WARRANTY 10 Commissioned / Installed date 11 Serial No: or DOM of the product BILL NO - : 1093/23-24 DATE - 04-05-2023 12 Name & phone No: of person registering the complaint JOHNSON- 8780431402 13 NOTE Note : Point Nos: 1 to 9 are compulsory JOHNSON.. Mob No:8780431402 EPABX No: 0261-2432308, 2420774 / 7383732308 / 9737326676 Hi-Tech Marketing NOTE: our new address is Hi-Tech Marketing "HI-TECH House" SHOP NO: 209, SNS INTERIO, E-Block,Bhatar-Althan Road,Surat-395007 | 2023-09-01 | 2023-09-02 13:04 | No | Warranty | J K ELECTRONICS | JIVAN JYOT NAGAR FLATS, A-19, Surat, NEAR DREAM HONDA null | Surat | 394210 | Gujarat | India FS ED&I CSP West Team VARDHAMAN ELECTROSOFT Vadodara | GIRISH CHAUHAN VARDHAMAN ELECTROSOFT Vadodara | VARDHAMAN ELECTROSOFT | we visited the site and check the CAD32B7 10A contactor NO/NC found physically ok. Checked & found contactor NO/NC operation & test to manually working ok. Checked & found NO/NC continuity ok. A1, A2 operating coil continuity open. We suspect to CAD32 contactor 3 NO/2NC, 24 VDC, operating coil open S/N no 91) 1022421 & 1023053. Raised ZVO for site case. Product under warranty | Repair |  | 9- Service Validated | 2023-09-05 13:04 | =S= Consig Fill up226025316 ( Two work order WO-11199062 number having same OA # 226025316 ) |  | 20 | INR | 20 | ENM POWER PRODUCTS
WO-11215427 | 103783329 | 2023-09-05 12:20 | 2023-09-05 |  | 2023-09-05 11:39 | SURTD5000XLI-CC | SURTD5000XLI-CC | SURTD5000XLI-CC | B22129111302 | FW: [External]RE: RR : IM15437589 ¦ Store Code : FRQS ¦ SCHNEIDER ¦ HARYANA -RELIANCE SMARTPOINT- P1 Critical Call IN-WARRANTY P: UPS not Powering on S:Onsite | 2023-09-05 | 2023-09-08 18:43 | No | Warranty | Reliance Retail Ltd_FRQS | SAI PLAZA TIGAON ROAD SECTOR-86 null | Faridabad | 121007 | Haryana | India FS North1 HBN CSP Prokon Hi Tech Systems Gurgaon | Subodh Pasupat Prokon Hi-Tech Systems Faridabad | Prokon Hi-Tech Systems-Faridabad-Haryana | UPS not powering on replaced the new cards , now ups working is okay. Model no 0J-0P8842Q 0J-0P8843Q Serial no 570944AD23600108 ,578842992351698 | Repair |  | 10- Closed | 2023-09-08 18:52 |  |  | 25 | INR | 25 | ENM SECURE POWER
WO-11195328 | 103728971 | 2023-09-01 22:25 | 2023-09-01 |  | 2023-09-01 18:06 | LC1D1506M7 | LC1D1506M7 | LC1D1506M7 |  | Hi Team, Kindly register a case and share WO number under repair category to book ZVO. Product : LC1D15006M7, SL :PK22314, Issue : Coil Not Working. Customer : Craftsman Automation Limited Address: Plot No.282/9,10 Bommasandra-Jigani Link Road Industrial Area Rajapura Village, Jigani Hobli, Anekal Taluk, Bengaluru, Karnataka 560105. Contact Person : Mr. Veeresh , 9964526648 Regards, P.BALAKUMAR, Field Service Team, Schneider Electric , PH: 7428380635, Bangalore. | 2023-09-01 | 2023-09-07 16:08 | No | Warranty | Craftsman Automation Pvt Ltd | Plot No.282/9,10 Bommasandra-Jigani Link Road Industrial Area Rajapura Village, Jigani Hobli, Anekal Taluk, Bengaluru, Karnataka | Bangalore | 560105 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | MANOJ GANESAN SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | As per SE engineer Mr.balakumar request we had booked ZVO contactor and handover to balakumar. And close this WO. | Repair |  | 9- Service Validated | 2023-09-08 07:13 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11215484 |  | 2023-09-05 17:49 | 2023-09-05 |  | 2023-09-05 11:59 | SRC10KUXI | SRC10KUXI | SRC10KUXI | B21904013364 | FW: RR : IM15358955 ¦ Store Code :TR65 ¦ SCHNEIDER ¦ MAHARASHTRA - DIGITAL Pending Contract P: Battery Installation S:Battery Installation | 2023-09-05 | 2023-09-06 13:58 | No | Commercial Action - Sales | Reliance Retial Ltd | RRL CDIT- Latur, Sabde Tower S No 27, First and Second Floor CTS No 9906, Ausa Road Latur null | Latur | 413531 | Maharashtra | India FS West1 HBN CSP_United Solutions Aurangabad | Sameer Sayyad United Solutions Aurangabad | UNITED SOLUTIONS | Done batterty installation. checked ups on mains and on battery mode is working fine | Commissioning & Installation | Battery Installation | 8- Service Completed | 2023-09-06 14:01 |  |  | 0 | INR | 0 | ENM SECURE POWER
WO-11195366 | 103724525 | 2023-09-01 22:13 | 2023-09-01 |  | 2023-09-01 18:36 | LC1E1210M7 | LC1E1210M7 | LC1E1210M7 |  | Our Ref: CRF -010 Date:01.09.2023 COMPLAINT REPORT FORM (For Automation Products) Name & Address of system house: Fluid Controls & Systems, No.31, Annapoorneshwari Industrial Area, Kanakapura road, Doddakallasandra P.O,Bangalore-62 End Customer?s name and address: Fluid Controls & Systems, No.31, Annapoorneshwari Industrial Area, Kanakapura road, Doddakallasandra P.O,Bangalore-62 Contact- Mohan 9686112973 Product Ref LC1E1210M7- 3 Nos LRE10 CAE22M5 Serial Nos. 1023091 1023091 1023091 8C2304 1022235 Mfg Ref Our invoice NO & Date Detailed description of problem: Contactors- screw not able to tight. OLR- stop button not working. Contactors- not getting ON. Duration for which products was in operation: NO. Did any temporary arrangement made for products failed: NO. Name & signature of person sending complaint with date: Name: MOHAN Mob:9686112973 Date:01.09.2023 | 2023-09-01 | 2023-09-02 22:10 | No | Warranty | Fluid Controls & Systems | 3A,Sarakki Industrial Estate, , Bannerghatta Road JP Nagar, 3rd Phase | Bangalore | 560076 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Mohammad Riyaz_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported materials the problem found was, - LC1E1210M7- 3nos, found screw threading issue. so we had arranged the replacement from our stock. - CAE22M5-1nos found changeover continuity issue, - LRE10-1nos stop button not working, holding issue. Zvo booked directly to fluid controls. | Repair |  | 9- Service Validated | 2023-09-03 07:49 | Hi Team, Zfre booked for the below LC1E1210M7 ? 3 nos to sree lakshmi Zvo : 226022894 LRE10 - 1 nos CAE22M5 ? 1 nos booked to fluid controls Zvo : 225925385 |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11215559 | 103785093 | 2023-09-06 18:12 | 2023-09-05 |  | 2023-09-05 12:37 | MISCELLANEOUS ANCILLARY EQUIPMENT | ANC-MISC | ANC-MISC | IK-RAC-35A-SS-BF-5868 | FW: CALL ID:INC0004317446 ¦ Branch code & Name : 4258_BECHRAJI HDFC Bank Under AMC P: This is a All-In-One-Rack and Water leakage issue from AC unit. S:AMC | 2023-09-05 | 2023-09-05 23:00 | No | Contract | HDFC Bank Ltd | Shop No 3/4/5/6/7, First Floor, KD Plaza, Near Balaji Complex | Mehsana | 384210 | Gujarat | India FS West2 Cooling CSP Comfort HVAC Solutions Ahd | Rajesh Pramanik_Comfort HVAC Solutions Ahd | Comfort HVAC Solutions | Leakage Repairing/EEV replacement done & gas supply done | Repair |  | 10- Closed | 2023-09-06 18:17 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 115 | INR | 115 | ENM SECURE POWER
WO-11196202 | 103726416 | 2023-09-02 09:48 | 2023-09-01 |  | 2023-09-01 18:54 | LC1E0910M7 | LC1E0910M7 | LC1E0910M7 |  | Name of Customer:-DARSHIL AUTOMATION CONTROL & SERVICE Site Address:-D-11,ARUNPRAKASH SOCIETY,OPP DEVASHISH SCHOOL, NE SAIBABA MANDIR SATELLITE Ahmedabad, 380015 Name of contact person at site:-sanjay bhai Contact Phone / Mob. No:-9726939930 Defective product details:-LC1E0910M7(1 QTY) Invoice no.:-PSI/22000061(19/01/2023) Nature of Defect:-Not getting on Serial No: or DOM of the product:-1023253 | 2023-09-01 | 2023-09-02 14:41 | No | Warranty | DARSHIL AUTOMATION CONTROL & SERVICE | D-11 ARUNPRAKASH SOCIETY OPP DEVASHISH SCHOOL NEAR SAIBABA MANDIR SATELLITE null | Ahmedabad | 380015 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Mistri Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physically observed ok. LC1E0910M7 SR NO : 1022462 observed physically ok but l1 pole open. for customer satisfaction free replacement. | Repair |  | 9- Service Validated | 2023-09-02 14:42 | =S= Consig Fill up 226019137 |  | 36 | INR | 36 | ENM POWER PRODUCTS
WO-11215584 | 103785774 | 2023-09-05 13:12 | 2023-09-05 |  | 2023-09-05 12:51 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | C21707001322 | P:No cooling/Compressor and controller issue/ c21707001322 under AMC P:No cooling/Compressor and controller issue/ c21707001322 S:AMC | 2023-09-05 | 2023-09-08 17:30 | No | Contract | Reliance Jio Infocomm Ltd | Paresh Chandra Mondal(9775869956) Po+Ps- Maynaguri | Jalpaiguri | 735224 | West Bengal | India FS East Cooling CSP Snow Point Kolkata | Jadab Patra_Snow Point Kolkata | Snow Point | UNIT NOT COOLING.OUT DOOR FAN,RELAY KIT,EXV FAULTY.OUT DOOR FAN,RELAY KIT,EXV CHANGE.ALL PARAMETER CHACKED.MACHINE OK RUNNING. LADER NOT AVALABLE. | Repair |  | 10- Closed | 2023-09-09 10:50 |  |  | 620 | INR | 620 | ENM SECURE POWER
WO-11196219 | 103726112 | 2023-09-02 12:26 | 2023-09-01 |  | 2023-09-01 19:04 | LC1E0901M7 | LC1E0901M7 | LC1E0901M7 |  | Dear SE Team, Please book direct complaint of below customer details Customer Name:- RUDRAKSHA ELECTRICALS Address:- 10, Manthan industrial estate, nr. Sbi bank phase - 1 vatva GIDC, Ahmedabad 382445. Contact person:- Mr. Jatin (7698999775) Part Reff.:- LC1E0901M7 Fault:- Coil not working properly -- | 2023-09-01 | 2023-09-02 12:30 | No | Warranty | Rudraksha Electricals | 10 , Manthan industrial estate , R.M. Engineering Compound ,Gidc vatva null | Ahmedabad | 382445 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | Jayesh J_JKS Rajkot | JKS Engineering Co. | Check contactor on/off working ok.check contactor terminal and body found.check contactor coil voltage ok found.check our products site not any problems ok working. | Repair |  | 9- Service Validated | 2023-09-02 12:33 |  |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11200601 | 103728984 | 2023-09-02 14:05 | 2023-09-02 |  | 2023-09-02 12:49 | LC1E250M5 | LC1E250M5 | LC1E250M5 |  | Dear Team Please find below mail from customer and kindly do the needful Name of the customer : VERTEX POWER SOLUTIONS PVT LTD Address : 38 MUTHU PALANIAPPAN NAGAR PAMMAL CHENNAI-75 Contact person : A RAJMOHAN ( 9790930244) Product: LC1E250M5 Schneider invoice no : AA3330013771 Qty : 1 no Problem: Contactor not working Please rush service person and resolve the issue immediately Regards R Sriidhar-ELCON-Chennai-17 Mob 9884059169 / 65 | 2023-09-02 | 2023-09-05 17:00 | No | Warranty | VERTEX POWER SOLUTIONS PVT LTD | No:14, Mosque Street, Easwaran Nagar; Anna Salai, Pammal | Chennai | 600075 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Site Visit Done | Repair |  | 9- Service Validated | 2023-09-06 06:37 | Hi Team, As attached Requested alternate correct reference is booked zfre Zfre : 226027762 LX9FG220 - 1 nos |  | 17 | INR | 17 | ENM POWER PRODUCTS
WO-11200768 | 103742715 | 2023-09-02 17:27 | 2023-09-02 |  | 2023-09-02 17:06 | C63N46E630 | C63N46E630 | C63N46E630 |  | Dear sir, This is to inform you that we have purchased the Schneider 630A Motorized MCCB from the Mohini Enterprises and found that the Breaker is not working properly so I request you to please arrange the Engineer Visit. - - Thanks & Regards, Mohammed Wahedullah Maintenance Engineer Contact No:8341992280. | 2023-09-02 | 2023-09-05 12:00 | No | Warranty | Renova Hospital | No.253/A Second & Third floor Road Number 12 Venkateshwara Colony Banjara Hills null | Hyderabad | 500034 | Telangana | India FS ED&I CSP South Team Sumanth Electrical Services Hyderabad | Venkata Prasad_SUMANTH ELECTRICAL SERVICES HYDERABAD | Sumanth Electrical Services | Self Visited Site and Inspected Schneider Electric MCCB and Motor Mechanism MT630 and LV429407 MN UVR Not Working and Accessories to be fixed we have explained how to fix accessories and we found MN UVR not working MN UVR Need to be replaced and we have replaced from ASC CSP Stock and complaint is closed | Repair |  | 9- Service Validated | 2023-09-05 18:10 |  |  | 15 | INR | 15 | ENM POWER PRODUCTS
WO-11219281 | 103685446 | 2023-09-06 16:49 | 2023-09-06 |  | 2023-09-06 09:49 | LV563306 | LV563306 | LV563306 | TC-2023-W06-3U2 | LV563306 - Tripping Issue TC-2023-W06-3U2 | 2023-09-06 | 2023-09-06 17:16 | No | Warranty | Malakshmi Enterprises | chajjpur kalan bapoli road | Panipat | 132103 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the MCCB found tripping issue / heat up, due to loose termination. Hence case is closed. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-06 17:22 |  |  | 165 | INR | 165 | ENM POWER PRODUCTS
WO-11219340 | 103795147 | 2023-09-06 12:23 | 2023-09-06 | FRee repalcement of the NVC for customer satisfaction | 2023-09-06 10:34 | LC1D09M7 | LC1D09M7 | LC1D09M7 |  | Name of Customer:-PRASAD KOCH-TECHNIK PVT LTD Site Address:-PLOT NO. 14 & 16-B, PHASE -I, VATVA,,G.I.D.C. ESTATE Ahmedabad, 382445 Name of contact person at site:-Yagnik Contact Phone / Mob. No:-7227899615.00 Defective product details:-LC1D09M7(1QTY), Invoice no.:-PSI/23006137(19/08/2023) Nature of Defect:-Contacter not on and off Serial No: or DOM of the product:-102304 | 2023-09-06 | 2023-09-06 22:24 | No | Warranty | Prasad Koch Technik Pvt. Ltd. | 14 & 16 - D, Phase-1, GIDC Estate Vatva, | Ahmedabad | 382445 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Sitpuriya_Anik Engineering Ahmedabad | Anik Engineering (554) | visited site and checked the product, Observed physically o, COntactor not operating, hence checked the NVC, observed burnt, It may be burnt due to over volateg. For customer satisfaction replacement of the NVC only | Repair |  | 9- Service Validated | 2023-09-06 22:30 | =S= Consig Fill up 226035510 |  | 15 | INR | 15 | ENM POWER PRODUCTS
WO-11229405 | 103883618 | 2023-09-11 17:13 | 2023-09-08 |  | 2023-09-08 13:00 | LC1D25M7 | LC1D25M7 | LC1D25M7 |  | LC1D25M7 1022114 Phase missing SP Sharma +918700282672 BC84 Mangolpuri truck market Pocket BA phase 2 induatrial area near english wines 110034 | 2023-09-08 | 2023-09-11 17:14 | No | Warranty | SP Sharma | BC84 Mangolpuri truck market Pocket BA phase 2 induatrial area near english wines | Delhi | 110034 | Delhi | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the contactor found not working and melting issue due customer used to comp. motor without overload relay, Hence no replacement given to customer. Email : id not provided by customer. | Repair |  | 9- Service Validated | 2023-09-11 17:18 |  |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11241499 | 103918588 | 2023-09-11 17:52 | 2023-09-12 |  | 2023-09-11 13:05 | GCR_MVS_CB | GCR_MVS_CB | GCR_MVS_CB |  | Checklist for the Registration of Service Request Sr. No Particulars Doc. Ref :- SE/CCC/001/V0.1 1 Company Name & Complete Address with pin code - Where product is installed " M/s. PCBL (TN) " Plot no A-7, SIPCOT Industrial Park, Thervoy Kandigai, Gummidipoondi Taluk, Tiruvallur District, Tamil Nadu- 601202, 2 Contact Person at Site : Name & Mobile No. Satyendra Bharati/ 8980041962 Alternate Mobile No : 9432167300 3 Contact Person at Site - Email Address** Satyendra.bharati@rpsg.in 4 Product Issue Type (Please select from drop down of column C-9) Hardware Issue 5 Are you ready to troubleshoot the issue remotely ? Yes/NO. If Yes, Our technical support engineer will call back to troubleshoot the issue remotely. No 6 Defective Product Model/Part No (Pls refer FAQ sheet ) 3200A ACB typical tripping 7 Nature of Defect* - Defects Video and Photographs photographs attached in the mail 8 Shutdown availability if applicable yes 9 Photograph of product where Serial No/Batch Code or Date of Manufacturing printed - Please refer FAQ sheet to find the Batch code details on the products attached 10 Proof Of Purchase - Pease attach SE*** Authorised Partner Invoice soft copy along with this check list "MAIYAR INVOICE NO. 4145, date: 27.09.2022 " 11 Name & phone No: of person registering the Service Request PAVAN/ 8892878463 "All fields are mandatory. Free of cost service visit subjected to warranty policy of the product and contract between Schneider Electric and buying party . Warranty will be check either by serial no/Batch code/DOM printed on the product or date of invoice of our authorised partner /Schneider Electric direct invoice or Contract . Warranty policy may be change product to product or contract with the customer. * Kindly share defect symptoms instead of ""Not working"", Please share the link of large files(product photoes or videoes) ** End user will receive a survey asking feedback on service " SE*** - Schneider Electric Please fill above details and send this sheet to customer care, Customer care contact link is give below https://www.se.com/in/en/work/support/customer-care/contact-schneider-electric.jsp Please mention Service Request as key word and Product Name in email subject line e.g for Masterpact NW ACB Service Request - Service Request for Masterpact NW Our web site :- https://www.se.com/in/en/ Product Issue Type Software/communication Issue Programing/Configuration Issue Hardware Issue Commissioning/ Installation Request Are you ready to troubleshoot the issue remotely ? Yes No | 2023-09-11 | 2023-09-15 18:30 | No | Warranty | PCBL (TN) Limited (Chennai _ EPC) | No A-7, SIPCOT Industrial Park, Thervoy Kandigai, Gummidipoondi Taluk, | Tiruvallur | 601202 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Site Visit Done | Repair |  | 9- Service Validated | 2023-09-16 11:20 |  |  | 67 | INR | 67 | ENM POWER PRODUCTS
WO-11215840 | 103789051 | 2023-09-05 16:07 | 2023-09-05 |  | 2023-09-05 14:16 | APC Symmetra RM 4kVA Scalable to 6kVA N+1 220-240V | SYH4K6RMI | SYH4K6RMI | JD0831011038 | FW: IM02974225 HP-SML-02 UPS BACKUP ISSUE Site code: IM02974225 HP-SML-02 UPS BACKUP ISSUE Serial# JD0831011038 P: battery module fault S: AMC | 2023-09-05 | 2023-09-06 14:47 | No | Contract | Central Board of Excise & Customs-CBEC | Railway Board Building The Mall Shimla | Shimla | 171001 | Himachal Pradesh | India FS North2 HBN CSP Computer Care Shimla | Pankaj Panwar_Computer Care Shimla | Computer Care Service Provider | VISITED AND CHECKED BATTERY MODULES . REFIX CONNECTION . WORKING FINE | Repair |  | 10- Closed | 2023-09-06 15:01 |  |  | 5 | INR | 5 | ENM SECURE POWER
WO-11241900 | 103921839 | 2023-09-12 11:00 | 2023-09-11 |  | 2023-09-11 15:50 | EZC400H4320N | EZC400H4320N | EZC400H4320N |  | Sr. no. Checklist for Complaint Registration 1 Name of Customer Gourav EnerGen India Pvt. Ltd. 2 Site Address Administrative Block, Industrial Estate C.B. Gunj, Bareilly (UP) - INDIA - 243502 3 End Client Gourav EnerGen India Pvt. Ltd. 4 Name of contact person at site Mr. Omkar 5 Contact No. / Mob. No: 9756892996 6 Defective product details MCCB (4P) EZC400H4320N - 1 Nos 8 Product Make Schneider 9 Nature of Defect On/Off Problem 10 Shutdown availability (if applicable) Anytime 11 Warranty status In warranty 12 Commissioned / Installed date N/A 13 Name & phone No. of person registering Ankit Sharma the complaint Mob.- 7505404102 | 2023-09-11 | 2023-09-19 16:35 | No | Warranty | Gourav Energen India (P) Ltd. | Administrative Block, Industrial Estate, C.B Ganj | Bareilly | 243502 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Aman Khare_Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found MCCB having on/off (STUCK) issue, so we replaced. | Repair |  | 8- Service Completed | 2023-09-19 16:37 | 226050230 zfre booked. |  | 275 | INR | 275 | ENM POWER PRODUCTS
WO-11215881 | 103787745 | 2023-09-05 14:52 | 2023-09-05 |  | 2023-09-05 14:31 | TDAVQ | TDAVQ | TDAVQ | C22005000931 | Re: Call Log for Netmagic DC-07, Chandivali & Assign to CSS P:BMS configuration S:AMC | 2023-09-05 | 2023-09-05 21:24 | No | Contract | Netmagic Solutions Pvt Ltd | Hiranandani Business Park,Saki Vihar Road, Chandiwali | Mumbai | 400072 | Maharashtra | India FS West1 Cooling CSP Unique India Mumbai | Shameem Akhter_Unique India Mumbai | Unique India- Mumbai HBN CSP | Site visit done for Unit Parameters not showing in BMS, cross checked and found the motherboard faulty, Arranged and replaced with a new one, Now Unit Parameters showing in BMS and also unit maintaining desire temperature. | Repair |  | 10- Closed | 2023-09-05 22:32 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11216034 | 103790129 | 2023-09-06 09:36 | 2023-09-05 |  | 2023-09-05 15:16 | EFC MONOBLOCK UNIT 1.3TR ( START RUN RELAY KIT, SEQUENCING , RS485 ) | WDF0181BN003 | WDF0181BN003 | JK1909005342 | Login complain from blower issue under AMC P:Blower fan not working S:AMC | 2023-09-05 | 2023-09-06 23:45 | No | Contract | RELIANCE JIO INFOCOMM LIMITED | Ramdevra Road Pokaran, Distt Jaisalmer | Jaisalmer | 345023 | Rajasthan | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Alok Sharma Freezeotech Airconditioning & Refrigeration GZB | Freezeotech Airconditioning & Refrigeration Corporation | we visited the site and found blower and damper faulty we replaced it now unit is working ok | Repair |  | 10- Closed | 2023-09-07 12:08 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 480 | INR | 480 | ENM SECURE POWER
WO-11247216 | 103928801 | 2023-09-12 17:22 | 2023-09-12 |  | 2023-09-12 14:35 | LV431540T | LV431540T | LV431540T |  | Hi We have installed 1 no NSX250B breaker in our PRISMA panel of PreFAB datacenter solution to be delivered to our overseas customer. Motor mechanism of this breaker is having a issue in status indication When breaker is in OFF condition the status is showing as ON on the motor assembly. Kindly provide your service to resolve this issue. Thanks Durgaprasad Shettigar Electronics Hardware, Experienced Senior Test Engineer Schneider Electric ¦ India ¦ IT Business ¦ Mobile: +91-9980425473 Email: Durgaprasad.Shettigar@schneider-electric.com Site:www.schneider-electric.com Address:#187/3 & 188/3 , Jigani ,Bangalore -562 106 | 2023-09-12 | 2023-09-13 15:00 | No | Warranty | Schneider Electric | 187/3,188/3 , Jigani Rd, Bommasandra Industrial Area | Bangalore | 562106 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | C Gunasekaran_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported motor mechanism the problem found was on/off indication not coming due to motor mechanism not fixed properly. We re-fixed the same and checked the on,off operations found working ok. The same shown to the customer. | Repair |  | 9- Service Validated | 2023-09-13 15:09 |  |  | 37 | INR | 37 | ENM POWER PRODUCTS
WO-11251190 | 103962296 | 2023-09-13 10:18 | 2023-09-13 | MCCB On/off issue | 2023-09-13 09:10 | C40N32D400 | C40N32D400 | C40N32D400 |  | Checklist for Complaint Registration 1 Name of Customer Suvarn Enterprises 2 Site Address Plot No-14/A Gat No-255/A, Jyotiba Nagar, Talwade 411062 3 Name of contact person at site Vinayak Manugade. 4 Contact Phone / Mob. No: 9225530219 5 Defective product details C40N32D400 6 Nature of Defect Shunt Coil Opreting Problem 7 Shutdown availability if applicable NA 8 Warranty status IN WARRENTY 9 Commissioned / Installed date 2023 Jun 10 Serial No: or DOM of the product BKCD0073900 11 Name & phone No: of person registering the complaint Sagar - 9225630217 Note : Point Nos: 1 to 9 are compulsory A ,Gat No-255/A , Jyotiba Nagar, Talwade, Pune-411062.India. | 2023-09-13 | 2023-09-13 16:10 | No | Warranty | SUVARN ENTERPRISES | plot no 14 A, gat no 255 A jotiba Nagar, Talawade | Pune | 411062 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Sachin Jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the MCCB On/off issue. observed MCCB coil operating leaver found bend due to mishandling. then customer demand we straight the MCCB leaver and refitted it. then we taken operation found ok. problem resolved after making leaver straight. | Repair |  | 9- Service Validated | 2023-09-13 16:15 |  |  | 40 | INR | 40 | ENM POWER PRODUCTS
WO-11216077 | 103792071 | 2023-09-05 17:40 | 2023-09-05 |  | 2023-09-05 15:37 | EFC MONOBLOCK 1.3TR R410A START KIT RS485 SEQ CONTROL | WDF0181BN040-1 | WDF0181BN040-1 | JK2049001753 | Rack damage Serial# JK2049001753 P:Rack damage S:AMC | 2023-09-05 | 2023-09-05 19:02 | No | Contract | Reliance Corporate IT Park Ltd | NO 227/3,MAIN ROAD,DRAKSHARAMAM | EAST GODAVARI | 533262 | Andhra Pradesh | India FS South1 Cooling CSP Sri Venkateshwara Engineering Enterprise Visakhapatn | Lokesh_ Sri Venkateshwara Engineering Enterprise Visakhapatn | Sri Venkateshwara Engineering Enterprises | Attended the call checked the unit & found that the unit wiring was damaged, due to rat bit. So rewiring the system. Now the unit was running. | Repair |  | 8- Service Completed | 2023-09-05 19:06 |  |  | 260 | INR | 260 | ENM SECURE POWER
WO-11251240 | 103977392 | 2023-09-13 14:18 | 2023-09-13 |  | 2023-09-13 09:57 | METSEEM6433HCL05RS | METSEEM6433HCL05RS | METSEEM6433HCL05RS |  | Dear sir, We purchased 2 Nos SCHNEIDER Energy meters in 07 Feb 2023 from the supplier(Venus Elecrtricals-chennai), One No Not Working ( No Display) at Site (Client-D MART -Kattupakkam in Chennai ), Kindly Check and rectify issues. ASSP Meter Details: Model No : EM64XXH S.No : 540400045774 Date of purcharded: 07-Feb-2023 Contact Name & Number. P.Ramesh 8754571213 | 2023-09-13 | 2023-09-16 17:00 | No | Warranty | Dmart | 47 Mount Poonamallee Rd Kamatchi Nagar Mahalakshmi Nagar Kattupakkam | Chennai | 600056 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Site Visit Done | Repair |  | 9- Service Validated | 2023-09-17 07:14 |  |  | 10 | INR | 10 | ENM POWER PRODUCTS
WO-11253810 | 103999314 | 2023-09-15 10:02 | 2023-09-13 |  | 2023-09-13 17:04 | C40F32D400 | C40F32D400 | C40F32D400 |  | Dear Sir/ma?am We have received MCCB SCHNEIDER 400A 3 POLE 50KA COMPACT NSX-400N MICROLOGIC 6.3A, INVOICE NO.- AA2730122757, INVOICE DATE- 21/08/2023, Qty- 2, but this MCCB electrically ON, OFF not working properly Qty- 01, So please send site engineer on urgent basis. Site Address:- Advance Panels & Switchgears (P) Ltd. PLOT NO. 30-31, SECTOR-5, SIDCUL, I.I.E. RANIPUR HARIDWAR- 249403, UTTRAKHAND Contact name and number:- Name- Ashish Goswami, Number- 6392578145 Thanks & Regards Ashish Goswami (IQC) +916392578145 cid:image001.png@01D87A66.04B05EF0 Goodwill Co-operation Trust Advance Panels & Switchgears (P) Ltd. PLOT NO. 30-31, SECTOR-5, SIDCUL, I.I.E. RANIPUR HARIDWAR (UTTRAKHAND) cid:image002.png@01D87A66.04B05EF0 | 2023-09-13 | 2023-09-15 14:51 | No | Warranty | Advance Panel & Switchgear Pvt. Ltd. | Plot No. 30 & 31, Sector - 5, I.I.E. Ranipur, SIDCUL, | Haridwar | 249403 | Uttarakhand | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | checked the MT found working ok. and also checked the demand controller found display blank. Hence faulty, replaced. EM7290 (30002975) - 2 Nos. Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-16 16:35 |  |  | 210 | INR | 210 | ENM POWER PRODUCTS
WO-11216097 | 103792426 | 2023-09-05 16:27 | 2023-09-05 |  | 2023-09-05 15:48 | SYH4K6RMI | SYH4K6RMI | SYH4K6RMI | JD0831011104 | Ups is not working P:Ups is not working S: AMC Service needed for standby unit-YQ0437221028 | 2023-09-05 | 2023-09-05 16:28 | No | Contract | Central Board of Excise & Customs-CBEC | Hotel Mini Ikhwan Bishambar Nagar | Srinagar | 110001 | Jammu and Kashmir | India FS North2 HBN CSP SMPowercom Srinagar | Muzamil M_SM Powercom Srinagar | SM Power Com | POWER BOARD & CONTROL CARD DAMAGED | Repair |  | 10- Closed | 2023-09-15 14:03 |  |  | 0 | INR | 0 | ENM SECURE POWER
WO-11253865 | 104000635 | 2023-09-13 17:47 | 2023-09-13 |  | 2023-09-13 17:23 | LC1E1810M7 | LC1E1810M7 | LC1E1810M7 |  | COMPANY NAME - NM AUTOMATION & CONTROL PVT . LTD ADDRESS- 6, SHUKAN MALL NR. VISAT PETROL PUMP SABARMATI AHMEDABAD -380005 CON NUM- +91 9173689721 CATALOG NUM SERIAL NUM PROBLEM LC1E1810M7 < 2 NOS> 1022361 1022465 POLE PROBLEM 1492/2 , MAHADEV'S KHANCHOMAMUNAYK'S POLE NR. MUNICIPAL HOSPITAL GANDHI ROAD AHMEDABAD EMAIL ID- MCBCENTRE2021@GMAIL.COM Call No- PRADIP MAKWANA =9173689721 | 2023-09-13 | 2023-09-14 19:03 | No | Warranty | NM AUTOMATION | SABARMATI | AHMEDABAD | 380005 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | Parthiv Patel JKS Ahmedabad | JKS Engineering Co. | We visited at site check a9n4p32c mcb dolly free check gz1e06 on/off button not working check lc1e3210m7 l2 and t2 terminal not working check lre03 reset button not working | Repair |  | 9- Service Validated | 2023-09-15 10:11 | =S= Consig Fill up 226053102 |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11216104 | 103792576 | 2023-09-05 15:57 | 2023-09-05 |  | 2023-09-05 15:53 | APC Symmetra LX 16kVA N,1 Ext. Run Tower Frame 220/230/240V or 380/400/415V | SYAF16KXR9I | SYAF16KXR9I | AD1638220866 | Back up issue P:Back up issue S:AMC | 2023-09-05 | 2023-09-06 17:56 | No | Contract | CBEC | Pragati Plaza, 5th Floor , Ranchi Road , Purulia ( Beside Govt. Girls High School) | Purulia | 723101 | West Bengal | India FS East HBN CSP Computer Care Asansol | Sanjay Prasad_Computer Care Asansol | COMPUTER CARE | Backup time checked 1hr 21min.Reset all the batteries now ups is working ok. | Repair |  | 10- Closed | 2023-09-06 18:05 |  |  | 110 | INR | 110 | ENM SECURE POWER
WO-11262650 | 104055037 | 2023-09-15 17:39 | 2023-09-15 |  | 2023-09-15 10:28 | LRD10 | LRD10 | LRD10 |  | LRD10 NC contact issue TH2237 10amp A9N3P10C DD-2022-W16-4-8 R phase missing Geo Slair greentech India pvt ltd S5 Brindavan garden hakitath marg near raj bagh metro station GHAZIABAD 201005 Jitesh kumar 8743992031 | 2023-09-15 | 2023-09-15 17:42 | No | Warranty | Geo Flair Greentech India Pvt Ltd | S-5, Vridavan Garden, Hakikat Marg, Sahibabad, | Ghaziabad | 201005 | Uttar Pradesh | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mcb found phase missing and relay not working, Hence faulty replaced. A9N3P10C - 1 nos LRD08 - 1 nos Email : | Repair |  | 8- Service Completed | 2023-09-19 16:36 |  |  | 52 | INR | 52 | ENM POWER PRODUCTS
WO-11216132 |  | 2023-09-05 16:12 | 2023-09-05 |  | 2023-09-05 16:03 |  | RBC44-IN |  |  | Battery Installation--RBC44-IN | 2023-09-05 | 2023-09-07 15:33 | No | Commercial Action - Sales | Reliance Retails | RRL TRENDS BARIPADA, NEAR BANK OF INDIA STATION ROAD, DIST MAYURBHANJ STATION BAZAR, BARIPADA, Orissa, null | MAYURBHANJ | 757001 | Odisha | India FS East HBN CSP Disha Computers Bhubneshwar | SUJIT SENAPATI Disha Computers Bhubneshwar | Disha Computers-Bhubaneshwar | Battery installation done RBC44-IN 1NOS 0A2334G04928/0A2334G04904 | Commissioning & Installation | Battery Installation | 10- Closed | 2023-09-08 08:38 |  |  | 260 | INR | 260 | ENM SECURE POWER
WO-11216148 |  | 2023-09-07 17:46 | 2023-09-05 |  | 2023-09-05 16:13 |  | SURT6000XLI-CC | SURT6000XLI-CC |  | Battery details-RBC44-1 no. | 2023-09-05 | 2023-09-08 11:42 | No | Commercial Action - Sales | Reliance Trends | Plot No. CP-3 Sector 3, Jankipuram Extension null | Lucknow | 226031 | Uttar Pradesh | India FS North2 HBN CSP BK Technologies Kanpur | Anand Gupta B.K. Technologies Lucknow | BK TECHNOLOGIES | Battery RBC44 replaced and UPS ok on both mode. Sr. 0H2334G05815 | Commissioning & Installation | Battery Installation | 10- Closed | 2023-09-08 11:59 |  |  | 29 | INR | 29 | ENM SECURE POWER
WO-11265214 | 104064936 | 2023-09-15 20:06 | 2023-09-15 |  | 2023-09-15 17:20 | LC1D09BD | LC1D09BD | LC1D09BD |  | Dear Team, We have purchased a contactor (LC1D09BD) from M/s BHAIRAVESHWARA CONTROL SYSTEMS, while inspecting we found the below contactor was not latching. Contactor Serial Number:- 1023195L105618 Please look into it and address the same. Regards Ankush Dogra ¦ 7760146162 3>Site name and complete postal address with pin code : FANUC India Private Limited, Plot No.155, KIADB Industrial area, Bommasandra,, BANGALORE,KARNATAKA, 560099 3>Contact person details ? Ashish ? 77177 65322 | 2023-09-15 | 2023-09-16 16:00 | No | Warranty | FANUC INDIA PRIVATE LIMITED | PLOT NO.155 KIADB INDUSTRIAL AREA BOMMASANDRA | Bangalore | 560099 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | MANOJ GANESAN SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported contactor the problem found was contactor not getting On, even 24vdc given to auxillary, due to coil resistance varying (0-60ohm) so we arranged for the replacement and checked found working ok. | Repair |  | 9- Service Validated | 2023-09-16 20:48 |  |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11267727 | 104066447 | 2023-09-16 15:12 | 2023-09-16 |  | 2023-09-16 10:12 | LC1D80 | LC1D80 | LC1D80 | 8B23053 | Complaint for Lc1d80 Sr.no.8B23053 one pc | 2023-09-16 | 2023-09-19 16:51 | No | Warranty | Singh automation | Gularpur road Nissing distt. Karnal hr | Karnal | 132024 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the contactor found "y" phase missing and capacitor found leakage issue and Glass relay found not getting on.Hence faulty replaced. LC1D80AM7 - 1 Nos. MEHVCSDY200A44- 1 Nos. RXM2LB2P7- 1 Nos. email : singhautomation.business@gmail.com | Repair |  | 8- Service Completed | 2023-09-19 17:10 |  |  | 130 | INR | 130 | ENM POWER PRODUCTS
WO-11216172 | 103793360 | 2023-09-05 16:50 | 2023-09-05 |  | 2023-09-05 16:22 | APC Symmetra LX 4kVA Power Module 220/230/240V | SYAF16KXR9I | SYAF16KXR9I | AD1704120147 | UPS is not working P:UPS is not working S:AMC | 2023-09-05 | 2023-09-09 13:19 | No | Contract | Central Board of Excise & Customs-CBEC | Knowledge Park 3, 3rd Floor, Wegman Business Park, G | Noida | 201306 | Uttar Pradesh | India FS North1 HBN CSP Martech Systems & Services Noida | Uttam Yadav_Martech Systems & Services Noida | Martech Systems & Services-Noida | SYAFSU14I AA2212110737 Input/Output wiring tray replaced at site so call closed | Repair |  | 10- Closed | 2023-09-09 13:20 |  |  | 22 | INR | 22 | ENM SECURE POWER
WO-11269377 | 104076720 | 2023-09-18 13:05 | 2023-09-16 |  | 2023-09-16 12:11 | METSEEM6436HCL10RS | METSEEM6436HCL10RS | METSEEM6436HCL10RS |  | Checklist for Complaint Registration Doc. Ref :- SE/CCC/001 1 Company Name & Complete Address with pin code - Where product is installed HORIZON METALTECH PVT LTD JHARMAJRI, Himachal Pradesh 173205 2 Contact Person at Site : Name & Mobile No. MANOJ KUMAR 8591403898 Alternate Mobile No : 8591403898 3 Contact Person at Site - Email Address** natbaddi@gmail.com 4 Defective Product Model/Part No (Pls refer FAQ sheet ) METSEEM EM 6436H LED 5 Nature of Defect* - Defects Video and Photographs METER NOT GEETTING ON 6 Shutdown availability if applicable YES 7 POP - SE Authorised Partner Invoice soft copy ATTACHED 8 Photograph of product where Serial No/Batch Code or Date of Manufacturing printed - Please refer FAQ sheet ATTACHED 9 Name & phone No: of person registering the complaint MANJEETSINGH 9805402290 "Points 1,2,3,4,5 & (7or8) are mandatory. * Kindly share defect symptoms instead of ""Not working"", Please share the link of large files(product photoes or videoes) ** End user will receive a survey asking feedback on service " POP - Proof of Purchase Please fill above details and send this sheet to customer care, Customer care contact link is give below https://www.se.com/in/en/work/support/contacts.jsp Please mention Complaint as key word and Product Name in email subject line e.g for Masterpact NW ACB complaint - Complaint for Masterpact NW Our web site :- https://www.se.com/in/en/ | 2023-09-16 | 2023-09-18 13:09 | No | Warranty | HORIZON PEX | PLOT 19 ,EPIP,PHASE -1, Baddi Jhar Majri Rd, | Baddi | 173205 | Himachal Pradesh | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Vinod Kumar_Sharma Electric Chandigarh | Sharma Electric works(1003) | checked the meter found not power up. hence faulty, replaced. METSEEM6436HCL10RS - 1 nos. Email ; id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-18 15:41 |  |  | 45 | INR | 45 | ENM POWER PRODUCTS
WO-11275073 | 104077681 | 2023-09-18 10:05 | 2023-09-18 |  | 2023-09-18 09:45 | GCR_MVS_CB | GCR_MVS_CB | GCR_MVS_CB |  | Subject: Rectify the MVS 1600A 4P EDO ACB - 1No. ACB Photos enclosure with reference to the above subject, The ACB is not working due to nuisance Tripping. Please kindly check & rectify immediately, So we request you to give prior importance to the above problem & do the needful in this regard at the earliest. Waiting for your reply, Site Location for repair or replacement: M/S. PES University., EC Campus Hosur Road, Electronic City., Bangalore 5600100 Contact: Mr. Karapswamy 9945784393 Regards, Ahmed 8762692172 With Regards, M/s. STAR Switchgears NO.15, 3rd MAIN RD, BEGUR ROAD CROSS BOMMANAHALLI, BANGALORE - 560068 PHONE: +91 080-41010774 / +91 9448357373 www.starswitchgears.in | 2023-09-18 | 2023-09-19 10:00 | No | Warranty | PES University | Hosur Road Konappana Agrahara Electronic City | Bangalore | 560100 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | MANOJ GANESAN SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | We had visited the site and checked the customer reported MVS ACB tripping through external LVM and ELR there is no no related our ACB same has been explained to the customer Mr Karupasamy. | Repair |  | 9- Service Validated | 2023-09-19 12:08 |  |  | 21 | INR | 21 | ENM POWER PRODUCTS
WO-11216179 |  | 2023-09-05 16:33 | 2023-09-05 |  | 2023-09-05 16:24 | SRC10KUXIQ | SRC10KUXIQ | SRC10KUXI | BQ1833002675 | Battery Installation | 2023-09-05 | 2023-09-06 11:43 | No | Commercial Action - Sales | Reliance Retail Ltd | GROUND & UPPER GROUND FLOOR, THE RISE PLOT NO 8/B SECTOR 8, PRATAP NAGAR JAIPUR null | Jaipur | 302033 | Rajasthan | India FS North1 HBN CSP Legacy Systems Jaipur | Rudresh Kumawat Legacy Systems Jaipur | Legacy Systems | battery installation done unit ok | Commissioning & Installation | Battery Installation | 10- Closed | 2023-09-06 12:29 |  |  | 15 | INR | 15 | ENM SECURE POWER
WO-11276754 | 104084606 | 2023-09-20 17:03 | 2023-09-18 |  | 2023-09-18 11:35 | METSEEM6436HCL10RS | METSEEM6436HCL10RS | METSEEM6436HCL10RS |  | DOM-10-10-22 EM6436H No display at 220V Dipankar paul 9351764173 Keestrack Crusher Pvt ltd A203 RICO industrial area Ghiloth neemrana alwar 301706 dipankar.paul@keestrack.net | 2023-09-18 | 2023-09-23 16:37 | No | Warranty | E-track Crusher Pvt. Ltd | A203,RIICO Industrial Area,Ghiloth | Alwar | 301706 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the meter found display not showing, Hence faulty replaced. METSEEM6436HCL10RS - 1 nos Email : | Repair |  | 8- Service Completed | 2023-09-23 16:41 |  |  | 170 | INR | 170 | ENM POWER PRODUCTS
WO-11216193 |  | 2023-09-07 16:00 | 2023-09-05 |  | 2023-09-05 16:32 | SRC10KUXI | SRC10KUXI | SRC10KUXI | B21925008308 | Pending Contract P: Battery Installation S:Battery Installation | 2023-09-05 | 2023-09-07 15:15 | No | Commercial Action - Sales | Reliance Trends Ltd | Reliance Trends Fabric DC, Neelamangla, Sy 33/2 A3 Mahimapura Village, Nelamangala TK null | Bangalore | 562111 | Karnataka | India FS South1 HBN CSP UBM Autopower Pvt. Ltd Bangalore | Kamal UBM Autopower Pvt. Ltd Bangalore | Autopower systems and solutions | RBC44-IN - 4 set Battery Installation Done, UPS Working Normal. | Commissioning & Installation | Battery Installation | 10- Closed | 2023-09-07 16:02 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11277266 | 104086822 | 2023-09-18 16:14 | 2023-09-18 |  | 2023-09-18 15:40 | MVS40N4MW6L | MVS40N4MW6L | MVS40N4MW6L |  | Checklist for Complaint Registration 1 Name of Customer Samaro Building Lifestyles 2 Site Address Survey no 2308,2310,2312,2314 Kalgam village,opp,NBR Camp, off Coastal highway,Umbergaon 396140 3 Name of contact person at site Mr. Girish Mishra 4 Contact Phone / Mob. No: 9574647229 5 Defective product details MVS40N4MW6L 6 Product Make Schneider 7 Nature of Defect Nuisance Tripping 8 Shutdown availability if applicable Yes 9 Warranty status Under Warranty 10 Commissioned / Installed date 11 Invoice No: or DOM of the product 12 Name & phone No: of person registering the complaint Deep Mistry - 8879667041 Note : Point Nos: 1 to 9 are compulsory | 2023-09-18 | 2023-09-20 14:31 | No | Warranty | SAMARO GLOBAL INDUSTRIES PVT LTD | SURVEY NO 2306,2308,2310,2312,VILLAGE BARIYAWAD,NEAR NRB CAMP,TA-UMBERGAON,DIST VALSAD,KALGAM | Valsad | 396140 | Gujarat | India FS ED&I CSP West Team SHIV SAI ELECTRICALS Vapi | SHIVAM LAD SHIV SAI ELECTRICALS VAPI | shivsai electricals | AS PER SITE VISIT WE HAVE FOUND THAT THE 4000A ACB ON AND WORKING OK.WHEN FOUND WAS THE ACB ARE NOT TRIPPING ON VOLTAGE .ROM THE ACB POINT OF WIEW THREE WAS NO INTER FOUND IN THE ACB.CUSTOMER HAS INFORMED THE VOLTAGE TO THE ACB 429VAC IN RTW POWER.VFD INSTALLED VOLTAGE IS 405VAC 429VAC IN RTW POWER.THERE WE ARE CLOSING THE CASE | Repair |  | 9- Service Validated | 2023-09-21 19:22 |  |  | 42 | INR | 42 | ENM POWER PRODUCTS
WO-11216233 | 103792986 | 2023-09-06 11:37 | 2023-09-05 |  | 2023-09-05 16:52 | 4LGD31D10005BWE Uniflair LEONARDO DX Unit - Air Cooled - Downflow - E.C. Radial | TDAV0511A00001 | TDAV0511A00001 | ZK1345001489 | Docket required for I-NE-KOHM-AG2-0001 PAC Fault alarm (High condensing pressure or comp. contactor failed ) under AMC P:High condensing pressure or comp. contactor failed S:AMC | 2023-09-05 | 2023-09-08 09:12 | No | Contract | Reliance Jio Infocom Limited | Above HDFC building, Razhu Point, Kohima, Nagaland | Kohima | 797121 | Nagaland | India FS East Cooling CSP SYSCOMP POWERSOL Guwahati | SHUBHAM PATHAK SYSCOMP POWERSOL Guwahati | SYSCOMP POWERSOL - GUWAHATI | Found HP alarm, change outdoor fan and check all parameters, now working properly. | Repair |  | 10- Closed | 2023-09-11 01:16 |  |  | 400 | INR | 400 | ENM SECURE POWER
WO-11277336 | 104090842 | 2023-09-18 17:17 | 2023-09-18 |  | 2023-09-18 16:26 | GCR_MVS | GCR_MVS | GCR_MVS |  | Dear Sir, Greetings from ACCU PANELS ENERGY PVT LTD!! Please find attached herewith details & Photos of faulty Contactor & ACB, For Contactor Cat No. LC1D18M7 Supplier: Marsden & Bakubhai Invoice No: MB/2388/2324 Fault: Aux Contacts not Working. For ACB, Cat No. MVS08N3NW6L Supplier: Marsden & Bakubhai Invoice No: MB/2388/2324 Fault: ACB not getting closed on load, it's working on only test mode. Site details: In below Signature Feel free to call us for any related queries. Please arrange Er at the location for a solution. Thanks With Best Regards, Sandip Panchal ACCU-PANELS ENERGY PVT.LTD. Plot No.303, Road No.-4A, Kathwada GIDC, Odhav Ahmedabad-382430 M: +91-7016405007 Visit us: https://www.accupanels.com/ | 2023-09-18 | 2023-09-23 10:58 | No | Warranty | Accu-Panels Energy Private Limited | Plot No 303, Road No 4A, Kathwada GIDC, Ahmedabad, Gujarat 382430 | Ahmedabad | 382430 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Nijesh Patel_Anik Engineering Ahmedabad | Anik Engineering (554) | Visited site and checked the above product physically observed ok. give a close command in test position with TNC working on off observed ok. but in servicing position acb not getting close. with thc only open with tnc. so change the chasis but problem remain same. so change connection acb in this chasis and trial taken working satisfactory in same . take a video and photograph and video for further action. LC1D18M7 SR NO : 102316 nc contact not working so no f/r. | Repair |  | 9- Service Validated | 2023-09-23 10:58 | =S= Consig Fill up 226061097 =S= Free Order 226074846 has been saved |  | 10 | INR | 10 | ENM POWER PRODUCTS
WO-11216402 | 103796644 | 2023-09-06 17:18 | 2023-09-08 |  | 2023-09-05 18:11 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | C21708001312 | P:Cooling issue under AMC P:Cooling issue S:AMC | 2023-09-05 | 2023-09-08 14:54 | No | Contract | Reliance Corporate It Park Limited | Ms Plaza, Nmc Xx /36 C, Thannimoodu, Amaravila P.O, Neyyattinkara | Trivandrum | 695122 | Kerala | India FS South2 Cooling CSP Evergreen Thiruvananthapuram | Anil M Nair_Evergreen Thiruvananthapuram | Evergreen | Gas leakge | Repair |  | 8- Service Completed | 2023-09-08 15:02 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 50 | INR | 50 | ENM SECURE POWER
WO-11277346 | 104088335 | 2023-09-18 18:17 | 2023-09-18 |  | 2023-09-18 16:32 | LV540630 | LV540630 | LV540630 |  | Sir, we have problem in 400A LSIG mccb, it is not trip on fault. please check attached invoice copy, and please resolve the same as soon as possible. MATERIAL PURCHASED BY - RK TRADING CO. against bill no. 3952 dtd 30-12-2022. And panel dispatch from solution system 4-1-2023. Site address- BHOPAL RNG PVT. LTD. add- Adampura, infront of christ college, Bhopal contact no- Ajay birla- 9752510465 (Sunil Kumar Singh) Solution System Sec.I, 121 Industrial Area Govindpura BHOPAL M: 09826362598,0755-2601306 | 2023-09-18 | 2023-09-19 15:19 | No | Warranty | BHOPAL RNG PVT LTD | Gram Adampura chavni Post Kolua Raisen Road infront of christ college | Bhopal | 462011 | Madhya Pradesh | India FS ED&I CSP West Team ABR Technical Service Indore | Lalu Sen_ABR Tecneical Services Indore | ABR Technical Services (9574) | Reached at site and as per customer MCCB display not getting on then we check (using power pact) and found display working properly then we change ETS 6.3 parameters and found MCCB working properly no issue in this product, And we guide to customer MCCB display turn on minimum 20-30% load Now this time MCCB working OK no any problem and we are close this case | Repair |  | 9- Service Validated | 2023-09-19 15:22 |  |  | 250 | INR | 250 | ENM POWER PRODUCTS
WO-11280916 | 104123783 | 2023-09-20 11:06 | 2023-09-19 |  | 2023-09-19 16:13 | LC1D95M7 | LC1D95M7 | LC1D95M7 | pk2247200 | LC1D95M7 pk2247200 Not hoding Lochan singh 8273346387 BS Polyfill pvt ltd khasra no 129 mauza lakhanpur sikandra industrial area Agra 282007 Near lifeline school bspolyfill@gmail.com | 2023-09-19 | 2023-09-22 15:57 | No | Warranty | B S Polyfill Pvt Ltd | Khasra Number 129 Mojha Lakhanpur Sikandra Agra 282007 | Agra | 282007 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Monu Pandey_Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found contactor having pole open issue , so we replaced | Repair |  | 8- Service Completed | 2023-09-22 16:00 |  |  | 360 | INR | 360 | ENM POWER PRODUCTS
WO-11284972 | 104144879 | 2023-09-21 14:20 | 2023-09-20 |  | 2023-09-20 11:18 | LC1D25M7 | LC1D25M7 | LC1D25M7 | 1021455 | lc1d25m7 3 nos 1021455 1023157 1021455 Not holding at 220V Sanjay Kumar +919711411778 | 2023-09-20 | 2023-09-21 15:20 | No | Warranty | RUDRA ALUMINIUM FORMWORK SYSTEM | Sector 69, Plot NO 745, IMT , Industrial Model Township | Faridabad | 121001 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the contactor found coil burnt due abnormal voltage and found dust / damage, Hence no replacement given to customer. Email : id not provided by customer . | Repair |  | 8- Service Completed | 2023-09-21 15:43 |  |  | 52 | INR | 52 | ENM POWER PRODUCTS
WO-11217365 | 103797313 | 2023-09-06 09:48 | 2023-09-08 |  | 2023-09-05 20:13 | SUA2200I-IN | SUA2200I-IN | SUA2200I-IN | B21846017525 | UPS need Calibration ¦¦ Ramsons under AMC P:Calibration support S:AMC | 2023-09-05 | 2023-09-08 16:11 | No | Contract | Thyssenkrupp Elevator India Pvt Ltd | DLF Corporate Green Sector 74 A | Gurgaon | 122004 | Haryana | India FS North1 HBN CSP Prokon Hi Tech Systems Gurgaon | Deshraj D_Prokon Hi-Tech Systems Gurgaon | Prokon Hi-Tech Systems-Gurgaon | UPS calibration done now ups working is okay. | Repair |  | 10- Closed | 2023-09-08 16:28 | 08-09-2023 visit done |  | 30 | INR | 30 | ENM SECURE POWER
WO-11285220 | 104147618 | 2023-09-21 10:46 | 2023-09-20 |  | 2023-09-20 12:50 | LC1D40M7 | LC1D40M7 | LC1D40M7 | 8b21432 | lc1d40m7 8b21432 lc1d50am7 8b23101 lc1d18m7 1021216 a9n4p63c 2 nos d2019 Phase missing and not holding at 220V Lakshay Mittal Click to dial09545500001 | 2023-09-20 | 2023-09-27 10:41 | No | Warranty | JAI DURGA COTTEX | 70 KM MILESTONE PATTI KALIYANA NESTLE ROAD SAMHALKHA | Panipat | 132101 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the contactor and mcb found phase missing, Hence faulty replaced. LC1D40AM7 - 1 nos. LC1D50AM7- 1 nos. A9N3P63C - 1 nos. email : lakshay72060@gmail.com | Repair |  | 8- Service Completed | 2023-09-27 10:45 |  |  | 182 | INR | 182 | ENM POWER PRODUCTS
WO-11217377 | 103796695 | 2023-09-06 11:19 | 2023-09-06 |  | 2023-09-05 20:20 | Leonardo EV,DX,R22,EC Fan,TDAV0811A,Downflow Without Heater & Humidifier | TDAV0811AN001 | TDAV0811AN001 | ZK1330017658 | under AMC P:Outdoor fan faulty S:AMC | 2023-09-05 | 2023-09-07 21:30 | No | Contract | Reliance Jio Infocomm Ltd. | sector 29 d iron market plot no 214 | Chandigarh | 140119 | Chandigarh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Abhishek Sharma Freezeotech Airconditioning & Refrigeration Chandigarh | Freezeotech Refrigeartion & Air Conditioning Corporation | We visited the site and found condenser fan faulty we replaced it now unit is working ok | Repair |  | 10- Closed | 2023-09-07 17:47 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 15 | INR | 15 | ENM SECURE POWER
WO-11285503 | 104146162 | 2023-09-20 14:59 | 2023-09-20 |  | 2023-09-20 14:21 | EZC250H3160 | EZC250H3160 | EZC250H3160 |  | Dear Team, We had supplied MCCB to our customer (invoice attached) The MCCB is not getting powered up or the output is not coming Kindly log our complaint and resolve the issue at the earliest Customer - Amber Garden And Resorts Address -- Bhamian Road Sector 32-A Backside Police Colony Chandigarh Road , Ludhiana - 141010 Contact Person - Manjot Singh Contact Number - 7888695380 Regards Aakash Gupta NMA Automation Ludhiana - 141010 | 2023-09-20 | 2023-09-20 15:01 | No | Warranty | AMBER GARDEN & RESORTS | BHAMIAN KALAN, BHAMIN KALAN, CHANDHIGARH ROAD, JAMALPUR | Ludhiana | 141010 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | checked the mccb found working properly. Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-20 15:06 |  |  | 25 | INR | 25 | ENM POWER PRODUCTS
WO-11217415 | 103802353 | 2023-09-06 09:07 | 2023-09-05 |  | 2023-09-05 20:40 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | C21746000209 | FW: [External]RE: I-MH-KRML-ILA-0001 Karmala ILA AC Not working_Need Service engineer to close the issue., Case: 103730288, , Case: 103731637, [ thread::Cdk7X0kCc2m8K5te_sMTfz4:: ] Under AMC P:Temp issue S:AMC | 2023-09-05 | 2023-09-07 18:37 | No | Commercial Action - Sales | Reliance jio infocomm Ltd | Ganesh Nagar , Karmala Tembhurni Road Opp reliance petrol pump tal karmala null | Solapur | 413211 | Maharashtra | India FS West2 Cooling CSP Gale HVAC Pune | Gaurav More_Gale HVAC Pune | GALE HVAC | We have replaced the startupkit of the unit then unit working normally | Repair |  | 10- Closed | 2023-09-07 20:15 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 180 | INR | 180 | ENM SECURE POWER
WO-11285556 | 104151658 | 2023-09-21 16:52 | 2023-09-20 |  | 2023-09-20 14:37 | LC1DMKM7 | LC1DMKM7 | LC1DMKM7 |  | LC1DMKM7 FT23095 Coil shorted Rakesh kumar 09057232756 | 2023-09-20 | 2023-09-21 16:55 | No | Warranty | Nav Power System | Japanese Zone, Neemrana | Alwar | 301705 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the contactor found not giving output due wrong product selection, Hence no replacement given to customer. Email : id not provided by customer. | Repair |  | 8- Service Completed | 2023-09-22 16:59 |  |  | 170 | INR | 170 | ENM POWER PRODUCTS
WO-11173437 | 103598782 | 2023-08-28 18:36 | 2023-08-28 |  | 2023-08-28 18:09 | Leonardo Ev,DX,R22,TUAR0721A,Upflow with Heater & Humidifier (Front Suction) | TUAR0721AN001 | TUAR0721AN001 | NUCU3272 | AMC P: Heater faulty S: AMC | 2023-08-28 | 2023-09-02 14:00 | No | Contract | International Tobacco Co. Ltd. | Meerut Road, Guldhar, | Ghaziabad | 201003 | Uttar Pradesh | India FS North2 Cooling CSP D K AIRCON Delhi | Pintu Kumar D K AIRCON Delhi | DK AIRCON | We have checked the PAC unit and found PAC was showing Heater faulty.New Heater replacement work done and all parameter check. Now PAC unit is working. | Repair |  | 9- Service Validated | 2023-09-02 16:47 |  |  | 34 | INR | 34 | ENM SECURE POWER
WO-11219224 |  | 2023-09-06 17:14 | 2023-09-06 |  | 2023-09-06 09:00 | APC Smart-UPS RT 10000VA 230V Harsh Environment | SURT10000XLI | SURT10000XLI | B21516002173 | FW: RR : IM15329269 ¦ Store Code :5827 ¦ SCHNEIDER ¦ TELANGANA - TRENDS Pending Contract P: Battery installation. RBC44-IN Qty-4 S:Battery installation. RBC44-IN Qty-4 | 2023-09-06 | 2023-09-07 16:19 | No | Commercial Action - Sales | Reliance Corporate It Park Limited | S V R S Neeladri H No.17-1-382/K/1 Survey No.89 & 90 Ward No.17 Block No.01 Saidabad Vill & Mandal Champapet null | Hyderabad | 500059 | Telangana | India FS South3 HBN CSP Param Technologies Hyderabad | KSurya Prakash_Param Technologies Hyderabad | Param Technologies | 1st Onsite Date:07-09-2023 Battery Installation is done successfully Now UPS is working fine on both modes | Commissioning & Installation | Battery Installation | 10- Closed | 2023-09-07 16:27 |  |  | 30 | INR | 30 | ENM SECURE POWER
WO-11286123 | 104147727 | 2023-09-21 11:14 | 2023-09-21 |  | 2023-09-20 17:04 | LC1D115M7 | LC1D115M7 | LC1D115M7 |  | Dear Sir, Please find the below complaint. ITEM CODE : LC1D115M7 ? QTY 1NO (CONTACTOR NOT IN WORKING CONDITION). Invoice No. 9008706245 Kindly send your service person to below mentioned site address. CUSTOMER SITE ADDRESS: S. A. REVANTH High Current Rectifiers (SCR / IGBT) GE TEK Electronics Private Limited (An ISO 9001 : 2015 Certified Co.) Shed No:8, Phase VI, SIDCO Industrial Estate, Maraimalai Nagar, Chennai - 603209,Tamil Nadu, India GST:33AAFCG2745N1ZF Mobile: +91-9498334929 Fixed Line: +91 44 22414272 | 2023-09-20 | 2023-09-21 17:00 | No | Warranty | GE TEK ELECTRONICS PVT LTD | Shed No 8 Phase 6 Sidco Industrial Area Marai Malai Nagar | CHENNAI | 603209 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Visit the site and inspect above mention contactor customer report to me contactor is not pickup. Today visit the site and we check the given control supply 230V AC to checked the contactor not getting and stuck sound small broken part to stuck removed the same and checked the operations ON and OFF by giving control supply contactor working normally. We have front cover locking part, mounting area at the contactor. Now contactor working normally. | Repair |  | 9- Service Validated | 2023-09-21 17:17 |  |  | 45 | INR | 45 | ENM POWER PRODUCTS
WO-11173789 |  | 2023-09-29 14:57 | 2023-09-29 |  | 2023-08-28 18:45 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | C21703000745 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-08-28 | 2023-09-29 21:30 | No | Contract | Reliance Jio Infocomm Ltd | Azad Nagar, Tatri Bazar, The- Naugarh null | Siddharth Nagar | 272207 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Harinder Yadav Freezeotech Airconditioning & Refrigeration Lucknow | Freezeotech Airconditioning & Refrigeration Corporation | Pm done clean the filter and condensore coil clean and all parameter check unit is working ok | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-29 15:21 |  |  | 268 | INR | 268 | ENM SECURE POWER
WO-11289176 | 104096105 | 2023-09-22 13:51 | 2023-09-21 |  | 2023-09-21 09:40 | LV563510 | LV563510 | LV563510 |  | Dear sir, Please find the attached rejection report of Mccb which details mentioned below . MCCB 630A TP 50KA = S/N; 7KN00180724 (LV563510) Complaints Remark? Mccb shunt liver not working. Organization Name & Address: Advance Panels & Switchgears Pvt ltd Plot No- 1267, HSIIDC Rai , Sonipat , Haryana kindly depute service engineer for the same ASAP. Thanks & Regards SANJIT SINGH Advance Panels & Switchgears (P) Ltd. Unit-III ? Plot No.1267, HSIIDC Industrial Estate, Rai, Distt. Sonepat (Haryana) Mobile ? +918651386064 / Email : rai@advancepanels.com | 2023-09-21 | 2023-09-22 13:52 | No | Warranty | Advance Panels & Switchgears (P) Ltd. | Plot No.1267, HSIIDC,Rai Industrial Estate | SONEPAT | 131028 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Pradeep Sharma_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mccb found on / off operation ok,shunt coil not getting hold due to lever bend / damage. Hence no replacement given to customer. Email : id not provided by customer. | Repair |  | 8- Service Completed | 2023-09-22 16:14 |  |  | 65 | INR | 65 | ENM POWER PRODUCTS
WO-11173801 |  | 2023-09-29 15:43 | 2023-09-29 |  | 2023-08-28 18:48 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | JK1909005747 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-08-28 | 2023-09-29 21:30 | No | Contract | Reliance Jio Infocomm Ltd | village Baibha, Post Aira null | Lakhimpur | 262722 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Harinder Yadav Freezeotech Airconditioning & Refrigeration Lucknow | Freezeotech Airconditioning & Refrigeration Corporation | Pm done clean the filter and condensore coil clean and all parameter check unit is working ok | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-29 15:52 |  |  | 149 | INR | 149 | ENM SECURE POWER
WO-11219242 |  | 2023-09-08 10:36 | 2023-09-06 |  | 2023-09-06 09:20 | SURT6000XLI-CC | SURT6000XLI-CC | SURT6000XLI-CC | B21943005484 | FW: RR : IM15378286 ¦ Store Code :TU30 ¦ SCHNEIDER ¦ UTTAR PRADESH - TRENDS Under AMC P: Battery Installation S:Battery Installation | 2023-09-06 | 2023-09-08 10:42 | No | Commercial Action - Sales | Reliance Trends | Plot No. CP-3 Sector 3, Jankipuram Extension null | Lucknow | 226031 | Uttar Pradesh | India FS North2 HBN CSP BK Technologies Kanpur | Kuldeep Gutam B.K. Technologies Lucknow | BK TECHNOLOGIES | Battery Module RBC44-IN installed and UPS ok on both mode. Sr. 0H2334G05815 | Commissioning & Installation | Battery Installation | 10- Closed | 2023-09-08 11:12 |  |  | 29 | INR | 29 | ENM SECURE POWER
WO-11289183 | 104151700 | 2023-09-21 11:18 | 2023-09-21 |  | 2023-09-21 09:43 | LV429406AE | LV429406AE | LV429406AE |  | Name of Customer:-INTERPOWER INDUCTION PVT LTD Site Address:-PLOT NO 815, SHED NO 5 KOTHARI CROSS ROAD, SOLA KALOL ROAD, PO SANTEJ, Gandhinagar, 382721 Name of contact person at site:-Vicky Panchal Contact Phone / Mob. No:-9106138066.00 Defective product details:-LV429406(1 qty) Invoice no.:-PSI/22000597(06/02/2023) Nature of Defect:-Not Working. Serial No: or DOM of the product:-TC-2023-W10 | 2023-09-21 | 2023-09-21 16:48 | No | Warranty | INTERPOWER INDUCTION PVT LTD | PLOT NO 815, SHED NO 5, KOTHARI CROSS ROAD, | Gandhinagar | 382721 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | Parthiv Patel JKS Ahmedabad | JKS Engineering Co. | We visit at side customer not educated the installation this uvt.then check and install proper for the Schneider guidelines.now mccb working found ok. | Repair |  | 9- Service Validated | 2023-09-21 16:55 |  |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11173881 |  | 2023-09-01 13:24 | 2023-09-29 |  | 2023-08-28 18:59 | TDAVQ | TDAVQ | TDAVQ | JK2106001543 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-08-28 | 2023-09-29 20:15 | No | Contract | RELIANCE JIO INFOCOMM LIMITED | GHATA NO 662, SITUATED AT VILLAGE JAMAYATPUR, PARGANA KHAIRABAD null | SITAPUR | 261131 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Karuna Tripathi Freezeotech Airconditioning & Refrigeration Lucknow | Freezeotech Airconditioning & Refrigeration Corporation | pm done clean the filter condenser unit with jet pump check all parameter unit is working ok | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-29 10:49 |  |  | 88 | INR | 88 | ENM SECURE POWER
WO-11289932 | 104144374 | 2023-09-21 12:20 | 2023-09-21 |  | 2023-09-21 10:43 | LV540306 | LV540306 | LV540306 |  | COMPLAINT REGISTRATION FORM Name of Organization K P ELECTRICAL SOLUTION Contact Person Mr. Kishan Panchal Contact No. 7486902854 Site Address 48, Crystal Ind. Hub, Opp. Aasudev Ind. Estate,Singarva-Kathwada Road, Kathwada, Ahmedabad-382430 Contact Person at Site Mr. Kishan Panchal Contact No. 7486902854 DEFECTIVE PRODUCT DETAILS S. No. Product Description/ Reference Quantity of defective product Nature of Defect Date of Commissioning/ Installation* Invoice/ Bill No. & Date Serial No. or DOM of Product** 1 LV500606 1 Not Working Purchase From : Tele Switchgears Pvt Ltd Purchase Bill No. : PSI/23007003 Purchase Date : 11-SEP-23 2 Kindly attach this form and send it to customercare.in@schneider-electric.com to register your complaint. *Applicable only for Projects **Required in case Invoice/ Bills details are not available | 2023-09-21 | 2023-09-23 16:11 | No | Warranty | K P ELECTRICAL SOLUTION | 48 Crystal Ind Hub Singarva Kathwada Road Kathwada | Ahmedabad | 382430 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Mistri Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the above mccb LV508241 CVS800N 800A - 4 pole customer used undervolrage coil extended rotarya handle with the mccb first time. set undervoltage coil in mccb and trial taken with extended working handle satisfactory. | Repair |  | 9- Service Validated | 2023-09-23 16:11 |  |  | 15 | INR | 15 | ENM POWER PRODUCTS
WO-11173983 |  | 2023-09-15 17:03 | 2023-09-22 |  | 2023-08-28 19:14 | WDF0181BN040-1 | WDF0181BN040-1 | WDF0181BN040-1 | JK2041003365 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-08-28 | 2023-09-25 21:30 | No | Contract | Reliance Jio Infocomm Ltd | Khasra No. ? 3068, Village ? Bisanda, Tahsil ? Attarra null | Banda | 210203 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Sunil Kumar Freezeotech Airconditioning & Refrigeration Lucknow | Freezeotech Airconditioning & Refrigeration Corporation | Pm done clean the filter condenser coil check all parameter unit is working ok | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-28 11:32 |  |  | 200 | INR | 200 | ENM SECURE POWER
WO-11289948 | 104174680 | 2023-09-23 10:59 | 2023-09-21 |  | 2023-09-21 10:51 | LC1D65AM7 | LC1D65AM7 | LC1D65AM7 | 8b233083 | LC1D65AM7 8b233083 No output from all phase C33 Ananad enclave vasantvihar delhi 110092 Claudia 9818232168 request by dealer 9717296584 | 2023-09-21 | 2023-09-23 11:01 | No | Warranty | Claudia Claudia | C33 Ananad enclave vasantvihar | Delhi | 110092 | Delhi | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the contactor found not working due to wrong connection after reset now contactor found working ok. Email : id not provided by customer. | Repair |  | 8- Service Completed | 2023-09-23 11:06 |  |  | 25 | INR | 25 | ENM POWER PRODUCTS
WO-11173993 |  | 2023-09-02 16:38 | 2023-09-02 |  | 2023-08-28 19:15 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | JK1940004161 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-08-28 | 2023-09-02 21:30 | No | Contract | Reliance Jio Infocomm Ltd | Ram Lakhan Pal, Chacheri Mod, Dumduma, Chunar null | Mirzapur | 231304 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Harinder Yadav Freezeotech Airconditioning & Refrigeration Lucknow | Freezeotech Airconditioning & Refrigeration Corporation | PM DONE CLEAN THE FILTER CONDENSORE COIL CHECK ALL PARAMETER UNIT IS WORKING OK | Preventive Maintenance | Regular Preventive Maintenance | 9- Service Validated | 2023-09-02 16:44 |  |  | 288 | INR | 288 | ENM SECURE POWER
WO-11290150 | 104156061 | 2023-09-21 12:56 | 2023-09-21 |  | 2023-09-21 12:41 | MVS25N4NW6L | MVS25N4NW6L | MVS25N4NW6L |  | Dear Sir, We have received ACB with Under Voltage coil as per below details. 1) MVS25N4NW6L - 1 nos Sys Inv. No. 9008687409 Date.: 24-08-23 O.A. No.: 225931703 As per above subject, under voltage coil is not working. Please send your engineer and Clear this issue with most priority. We are Share Schneider Invoice copy for your Reference. Site Address : POOJAN ENGINEERS, 18/8, G.I.D.C. Estate, Nr. Somany Ceramics Ltd, G.I.D.C., Kadi. Contact Person Name : Mr. Sanjay Patel Contact Person Mo. No.: 9925142855 Please reply. Thanks, From, Suresh Thakor, Poojan Enterprise,Kadi. | 2023-09-21 | 2023-09-25 13:27 | No | Warranty | Poojan engineers | Adrress: 18/9, GIDC, Nr.Somany Ceramics Ltd, Kadi | Kadi | 382715 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Nijesh Patel_Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physically observed ok. checked the uv coil it not operating hence acb not getting on. replaced the uv coil in the same control wiring .tested the acb observed wokring ok. furthe checked the uv coil observed the internal ic burnt resolved by replacing another uv coil benefit of doubt replacement to cross check verify control voltage. | Repair |  | 9- Service Validated | 2023-09-25 13:28 | 226079620 |  | 65 | INR | 65 | ENM POWER PRODUCTS
WO-11174000 |  | 2023-09-01 13:20 | 2023-09-03 |  | 2023-08-28 19:16 | WDF0181BN040-1 | WDF0181BN040-1 | WDF0181BN040-1 | JK2043002919 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-08-28 | 2023-09-12 21:30 | No | Contract | Reliance Jio Infocomm Ltd | Khata No. 102, Khasra No 593, Village - Inayatpur Barra, Pargana - Auras null | Unnao | 209801 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Karuna Tripathi Freezeotech Airconditioning & Refrigeration Lucknow | Freezeotech Airconditioning & Refrigeration Corporation | Pm done we have check the PAC unit air filter and condenser coil clean and all parameter check | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-19 10:09 |  |  | 73 | INR | 73 | ENM SECURE POWER
WO-11174016 |  | 2023-09-01 13:07 | 2023-09-03 |  | 2023-08-28 19:19 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | JK1942007649 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-08-28 | 2023-09-10 21:30 | No | Contract | Reliance Jio Infocomm Ltd | khata no.0395, gata no.0317, Vill- Tikari Post - Babhani Hethar null | Prayagraj | 212303 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Harinder Yadav Freezeotech Airconditioning & Refrigeration Lucknow | Freezeotech Airconditioning & Refrigeration Corporation | pm done clean the filter condenser coil check all parameter unit is working ok | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-25 15:14 |  |  | 246 | INR | 246 | ENM SECURE POWER
WO-11221075 | 103814854 | 2023-09-06 12:15 | 2023-09-06 |  | 2023-09-06 11:28 | SRC10KUXI | SRC10KUXI | SRC10KUXI | B22120014080 | FW: UPS dismantling request for 10 KVA UPS at Pharma DC-Silchar ¦¦ Store Code: SK10. P: UPS dismantling S: UPS dismantling | 2023-09-06 | 2023-09-06 13:27 | No | Commercial Action - Sales | Reliance Retail Limited | SK10 Silchar Pharma DC, Dag No. 305 & 306, Patta No 78, Mouza Bahadurpur ,PS And Pargana, Udarbond Silchar | Cachar | 788009 | Assam | India FS East HBN CSP Neha Enterprise Silchar | ARVIND RAI_Neha Enterprise Silchar | NEHA ENTERPRISE | ups and battery fully disconnected from rack | Decommissioning | Uninstall | 10- Closed | 2023-09-07 13:37 |  |  | 35 | INR | 35 | ENM SECURE POWER
WO-11172679 | 103577178 | 2023-08-31 09:22 | 2023-08-28 |  | 2023-08-28 12:09 | LC1F185 | LC1F185 | LC1F185 | PK2232211 | As per the sr. no, The Product is in Warranty. Kindly arrange the site visit. Issue: Overheating and chattering issue Address Electric loco shed Near Puliyamangalam Railway Station, Arakonam Ranipet 631001 Tamil Nadu India Contact person Details: - Mr.Rodricks 7904565788 | 2023-08-28 | 2023-09-02 13:00 | No | Warranty | Electric loco shed | Near Puliyamangalam Railway Station, Arakonam null | Ranipet | 631001 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Visited Done | Repair |  | 9- Service Validated | 2023-09-02 13:30 |  |  | 72 | INR | 72 | ENM POWER PRODUCTS
WO-11290558 | 104177083 | 2023-09-22 15:57 | 2023-09-21 |  | 2023-09-21 15:15 | LC1D09F7 | LC1D09F7 | LC1D09F7 |  | Dear Sir, Please depute engineer on urgent basis because some material not working. Material Description as given below:- Contactor 9A 3P 110VAC Cat No. LC1D09F7 = 2 Nos ( Not Operating After supply ) Sr. No.1023224 O/L Relay 2.5 to 4.0 A 1NO+1NC Cat No. LRD09 = 1 No. ( Tripping Problem ) Sr. No. TH2316 Site Address:- Tricolite Electrical Industries Limited. Plot No.5 Sector 6 IMT Manesar Gurgaon Haryana Shivram Yadav Engg. QC Tricolite Electrical Industries Ltd 9717209723 shivram.yadav@tricolite.com | 2023-09-21 | 2023-09-22 15:59 | No | Warranty | Tricolite Electrical Industries Ltd.(1720) | Plot No- 5 & 32, Sector -6, IMT Manesar | Gurugram | 122052 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the relay found trip issue and contactor found not getting on due coil open, Hence faulty replaced. LRD08 - 1 nos LX1DF7 2 nos | Repair |  | 8- Service Completed | 2023-09-22 17:27 |  |  | 55 | INR | 55 | ENM POWER PRODUCTS
WO-11171815 | 103548399 | 2023-08-29 16:14 | 2023-08-28 |  | 2023-08-28 10:32 | 30002566 | 30002566 | 30002566 |  | As per the invoice, The Product is in Warranty. Kindly arrange the site visit. Issue: display issue Address Tricolite Electrical Industries Ltd Plot No 11, Sector 6, IMT Manesar Gurgaon 122052. Haryana India Contact person Details: - Mr.Shresth 8923395626 | 2023-08-28 | 2023-09-02 18:01 | No | Warranty | Tricolite Electrical Industries Limited | Plot No 11, Sector 6, IMT Manesar | Gurgaon | 122052 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the meter found display not showing, Hence faulty replaced 30002566 - 1 nos Email : id not provided by cusotmer . | Repair |  | 9- Service Validated | 2023-09-04 16:05 |  |  | 55 | INR | 55 | ENM POWER PRODUCTS
WO-11174017 |  | 2023-09-01 13:09 | 2023-09-03 |  | 2023-08-28 19:19 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | JK1942007651 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-08-28 | 2023-09-11 21:30 | No | Contract | Reliance Jio Infocomm Ltd | khata no.0395, gata no.0317, Vill- Tikari Post - Babhani Hethar null | Prayagraj | 212303 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Harinder Yadav Freezeotech Airconditioning & Refrigeration Lucknow | Freezeotech Airconditioning & Refrigeration Corporation | pm done clean the filter condenser coil check all parameter unit is working ok | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-25 15:25 |  |  | 246 | INR | 246 | ENM SECURE POWER
WO-11221214 | 103815615 | 2023-09-06 14:54 | 2023-09-07 |  | 2023-09-06 11:53 | EFC Monoblock unit 1.3TER, downflow with start run relay kit | WDF0181BN002 | WDF0181BN002 | ZK1533008687 | P:zk1533008687---Cooling issue zk1533008687 | 2023-09-06 | 2023-09-09 18:29 | No | Contract | Reliance Jio Infocomm Ltd. | 24 Telangu tirmandapam Harur bus stand Harur | Dharmapuri | 636903 | Tamil Nadu | India FS South4 Cooling CSP Unity Air conditioning Engineers Chennai | K.Mohan Raj_ Unity Air conditioning Engineers Chennai | UNITY AIRCONDITIONING ENGINEERS | HP alarm: Now we checked and found ODU fan fault in system now we changed new fan and observe unit working Normal. | Repair |  | 8- Service Completed | 2023-09-09 18:32 |  |  | 271 | INR | 271 | ENM SECURE POWER
WO-11290844 | 104187007 | 2023-09-22 17:30 | 2023-09-21 |  | 2023-09-21 17:42 | LC1D32M7 | LC1D32M7 | LC1D32M7 |  | lc1d32m7 3 nos 1021451800 Coil stuck at 220V 9760994783 shailendra | 2023-09-21 | 2023-09-23 17:57 | No | Warranty | Aman Electricals | T 99 Shivalik Nagar Bhel | Haridwar | 249403 | Uttarakhand | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the contactors LC1D32M7 found phase missing. Hence faulty, need replacement. LC1D32M7- 3 nos. email : id not provided by the customer. | Repair |  | 8- Service Completed | 2023-09-23 17:58 |  |  | 210 | INR | 210 | ENM POWER PRODUCTS
WO-11174022 |  | 2023-09-01 13:06 | 2023-09-03 |  | 2023-08-28 19:19 | WDF0181BN040-1 | WDF0181BN040-1 | WDF0181BN040-1 | JK2043002525 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-08-28 | 2023-09-10 21:30 | No | Contract | Reliance Jio Infocomm Ltd | Khata No. 1450, Gata No. 413, Village- Mauaima, Pargana- Mirzapur Chauhaari, Tehsil- Soraon null | Allahabad | 212507 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Harinder Yadav Freezeotech Airconditioning & Refrigeration Lucknow | Freezeotech Airconditioning & Refrigeration Corporation | Pm done clean the filter and condensore coil clean and all parameter check unit is working ok | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-27 16:43 |  |  | 235 | INR | 235 | ENM SECURE POWER
WO-11221468 | 103819102 | 2023-09-06 15:27 | 2023-09-06 |  | 2023-09-06 13:33 | WDF0181BN001 | WDF0181BN001 | WDF0181BN001 | ZK1549009582 | P:zk1549009582---Blower fan not working. Under AMC P:zk1549009582---Blower fan not working. S:AMC | 2023-09-06 | 2023-09-08 09:20 | No | Contract | Reliance Jio Info Com Limited | Dist BongaiGaon North Salmara | Bongaigaon | 783384 | Assam | India FS East Cooling CSP SYSCOMP POWERSOL Guwahati | SHUBHAM PATHAK SYSCOMP POWERSOL Guwahati | SYSCOMP POWERSOL - GUWAHATI | Found relay kit faulty, relay kit replaced, now working properly. | Repair |  | 10- Closed | 2023-09-11 01:22 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 400 | INR | 400 | ENM SECURE POWER
WO-11174035 |  | 2023-09-29 11:30 | 2023-09-29 |  | 2023-08-28 19:21 | EFC MONOBLOCK 1.3TR R410A START KIT RS485 SEQ CONTROL | WDF0181BN040-1 | WDF0181BN040-1 | JK2043000619 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-08-28 | 2023-09-29 21:00 | No | Contract | Reliance Jio Infocomm Ltd | BHINGA Nagar Palika null | SHRAVASTI | 271831 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Karuna Tripathi Freezeotech Airconditioning & Refrigeration Lucknow | Freezeotech Airconditioning & Refrigeration Corporation | pm done clean the filter condenser unit with jet pump check all parameter unit is working ok | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-29 11:39 |  |  | 169 | INR | 169 | ENM SECURE POWER
WO-11305482 | 104239340 | 2023-09-26 10:42 | 2023-09-25 |  | 2023-09-25 16:36 | LV540306 | LV540306 | LV540306 | TC-2022-W15-1 | MCCB having pole open issue Dear sir, Model - LV540306 Serial no - TC-2022-W15-1 Problem - POLE OPEN so plzz dispute the service engineer to check the MCCB and resolve the issue as soon as possible customer Name - subhas plywood contact person - subhas JI contact no -7905584694 Address -Plot no.- Ram nagar industrial area 226401 | 2023-09-25 | 2023-09-26 13:58 | No | Warranty | Subhas Plywood | Plot no 110 Ram nagar industrial area null | Lucknow | 226401 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Abhishek Patel Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found MCCB B pole heat & melt due to loose termination issue , this is not cover in under warranty so complaint was closed. | Repair |  | 8- Service Completed | 2023-09-26 14:04 |  |  | 40 | INR | 40 | ENM POWER PRODUCTS
WO-11221361 | 103817430 | 2023-09-06 13:04 | 2023-09-06 |  | 2023-09-06 12:48 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | C21746000206 | P:c217460600206---Fan issue Under AMC P:c21746000206---Fan issue S:AMC | 2023-09-06 | 2023-09-07 17:40 | No | Contract | Reliance Jio Infocomm Ltd | Nalhati Bus stand Birbhum | Birbhum | 742234 | West Bengal | India FS East Cooling CSP Snow Point Kolkata | Chandan Nandi_Snow Point Kolkata | Snow Point | HP ALARM.CONDENSER FAN FAULTY.CONDENSER FAN CHANGE.ALL PARAMETER CHECKED.MACHINE OK RUNNING. | Repair |  | 8- Service Completed | 2023-09-08 17:43 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 219 | INR | 219 | ENM SECURE POWER
WO-11305452 | 104236583 | 2023-09-25 17:49 | 2023-09-25 | NA | 2023-09-25 16:14 | MVS20N4NW6L | MVS20N4NW6L | MVS20N4NW6L | 10231210910 | New ACB lock stuck during racking out MVS20N4NW6L - 10231210910 rack in and rack out operation issue Site Address: Antony Lara Enviro Solution Pvt Ltd Integrated Municipal Solid waste Management Facility Project of MGCM Off Eastern Express Highway Kanamwar Nagar, Kanjoor Marg East Mumbai ? 400042 Mr.Ashwin Firke contact no ? 9860488298-M & 8850534873-M. | 2023-09-25 | 2023-09-26 15:42 | No | Warranty | Antony Lara Enviro Solutions | Eastern Express Highway, Near Kanamwar Nagar, Kanjoor Marg Integrated Municipal Solid Waste Management Facility,Project of MCGM,Off, Kanjurmarg | Mumbai | 400042 | Maharashtra | India FS ED&I CSP West Team East India Power Engineers Mumbai | Sandeep Ingavale East India Power engineers Mumbai | East India Power Engineers (5043) | Visited the site & checked the ACB with the chassis and found the breaker not getting the rack out. Opened the rack in/out mechanism front plate and then found the shutter safety lock got bogged in the mechanism due to the breaker not getting rak in / out. Removed the shutter safety lock from the mechanism and did the rack in/out operation found working ok. | Repair |  | 8- Service Completed | 2023-09-26 15:58 |  |  | 12 | INR | 12 | ENM POWER PRODUCTS
WO-11173360 | 103596158 | 2023-08-31 16:59 | 2023-08-28 |  | 2023-08-28 17:32 | METSEEM6438HCL10RS | METSEEM6438HCL10RS | METSEEM6438HCL10RS |  | As per the DOM, The Product is in Warranty. Kindly arrange the site visit. Issue: Display issue Address Modern Power System B-196, Sec-4,Bawana New Delhi 110039 Delhi India Contact person Details: - Mr.Chako 9818067269 | 2023-08-28 | 2023-08-31 17:02 | No | Warranty | Modern Power System | B-196, Sec-4,Bawana | New Delhi | 110039 | Delhi | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the meter found display not showing, Hence faulty replaced. METSEEM6438HCL10RS - 1 nos Email : mpsbawana@gmail.com | Repair |  | 9- Service Validated | 2023-09-01 11:30 |  |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11305457 | 104246266 | 2023-09-25 17:13 | 2023-09-25 | MCCB Tripping Problem | 2023-09-25 16:18 | LV563319 | LV563319 | LV563319 | TC-2023-W16-2 | LV429407 Coil is not operating properly As Per The serial number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Denfoss Technologies Pvt. Ltd. Building B7, Level 3, 4, 5 & Test Lab Magarpatta City SEZ, Magarpatta, Hadapsar Pune 411013 Maharashtra India Contact Person Details:- akshay Ji 9503647462 Product and Issue:- LV563319 MCCB LV429407 TC-2023-W16-2 Coil is not operating properly by giving supply | 2023-09-25 | 2023-09-26 15:47 | No | Warranty | Denfoss Technologies Pvt. Ltd. | Building B7, Level 3, 4, 5 & Test Lab Magarpatta City SEZ, Magarpatta, Hadapsar | Pune | 411013 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Amit Patil_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked MCCB Tripping Problem. removed front cover and observed coil holding knob found damaged bend due to coil miss operation. so as per customer we straight it . and fitted coil properly. and then taken on.off operation it's found ok. | Repair |  | 9- Service Validated | 2023-09-26 15:52 |  |  | 20 | INR | 20 | ENM POWER PRODUCTS
WO-11221434 | 103813327 | 2023-09-06 14:12 | 2023-09-06 |  | 2023-09-06 13:18 | APC Symmetra RM 4kVA Scalable to 6kVA N+1 220-240V | SYH4K6RMI | SYH4K6RMI | JD0844008838 | FW: IM02971025 WB-HGY-01 UPS Back up issue Site code: IM02971025 WB-HGY-01 UPS is not working Serial# JD0844008838 P: UPS Back up issue S: AMC | 2023-09-06 | 2023-09-12 12:05 | No | Contract | Central Board of Excise & Customs-CBEC | Congress Para | Balurghat | 733101 | West Bengal | India FS East HBN CSP SYSCOMP POWERSOL Sodepur | Prasenjit Mondal_SYSCOMP POWERSOL Sodepur | Syscomp Infotech Pvt Ltd - KOLKATA | Tested by one RIM, MIM, Power and battery module, but problem is not resolved. multiple fault is showing. rejected from APC due to Water damaged. | Repair |  | 10- Closed | 2023-09-12 18:08 |  |  | 55 | INR | 55 | ENM SECURE POWER
WO-11305528 | 104240926 | 2023-09-26 10:43 | 2023-09-25 |  | 2023-09-25 16:55 | LV525302 | LV525302 | LV525302 | 10-2022-W35-1-0699L1 | mccb not working LV525302 - 10-2022-W35-1-0699L1 pole continuity issue Site Address: Royal Maternity & Nursing Home House Number N - 6/20 - A-5, Karaudhi Road, Chitaipur Road-Sunderpur, Varanasi - 221005 (Near Pragati Public School) Contact person - Dr. Swati contact no. - 6388975678 | 2023-09-25 | 2023-09-26 16:08 | No | Warranty | Royal Maternity & Nursing Home | N - 6/20 - A-5, Karaudhi Road, Chitaipur Road-Sunderpur, Near Pragati Public School | Varanasi | 221005 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Aman Khare_Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found MCCB having tripping issue due to loose termination, now MCCB working fine. | Repair |  | 8- Service Completed | 2023-09-26 16:14 |  |  | 330 | INR | 330 | ENM POWER PRODUCTS
WO-11174061 |  | 2023-09-13 17:56 | 2023-09-30 |  | 2023-08-28 19:24 | Easy UPS 3S 40 kVA 400 V 3:3 UPS for external batteries | E3SUPS40KH | E3SUPS40KH | 9E1944T10695 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-08-28 | 2023-08-25 16:30 | No | Contract | Jane's Defense India LLP | 2nd and 3rd Floor, S.J.R iPark Tower No.1, Block Mobius EPIPZone1, White Field Road, Krishnarajapuram Hobli, | Bangalore | 560066 | Karnataka | India FS South1 HBN CSP UBM Autopower Pvt. Ltd Bangalore | Raghavendra UBM Autopower Pvt. Ltd Bangalore | Autopower systems and solutions | PM done, UPS working normal. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-13 17:58 |  |  | 0 | INR | 0 | ENM SECURE POWER
WO-11221467 | 103815623 | 2023-09-06 17:26 | 2023-09-06 |  | 2023-09-06 13:32 | APC Smart-UPS RC 6000VA 230V for India - No Batteries | SRC6KUXI | SRC6KUXI | B21446002568 | call id INC0004180749 1. Asset Code : 15A-AIR-H-00337 2. Serial No : B21446002568 3. Type : UPS / UPS - Battery : UPS 4. Make & Model : APC 6 KVA UPS (All in One Rack) 5. WSD : 03/09/2015 6. WED : 03/08/2016 7. Asset Status as per SCCD : Active 8. Nature | 2023-09-06 | 2023-09-08 13:08 | No | Contract | HDFC Bank Ltd | B1/13-B, VIPULKHAND, GOMTINAGAR, LUCKNOW, UTTAR PRADESH - 226010. | Lucknow | 226010 | Uttar Pradesh | India FS North2 HBN CSP BK Technologies Kanpur | Anand Gupta B.K. Technologies Lucknow | BK TECHNOLOGIES | UPS disconnected which has connected with battery and input power and output supply. UPS working ok on both mode. | Repair |  | 10- Closed | 2023-09-08 13:14 |  |  | 22 | INR | 22 | ENM SECURE POWER
WO-11305531 | 104239621 | 2023-09-25 17:14 | 2023-09-25 |  | 2023-09-25 16:58 | GCR_MVS | GCR_MVS | GCR_MVS | 44927 | Reg. Complaint for MVS ACB Checklist for complaint Registration 1 Name of Customer Yuvan Engineering 2 Site Address Waste management service in Rajoda, Madhya Pradesh, Address: VVX5+4PX, Rajoda, Madhya Pradesh 453771 3 Name of contact person at site Mr. Soham ji 4 Contact Phone / Mob. No: 8451003210 5 Defective products details MVS16N4MW6L 6 Product Make Schneider 7 Nature of Defect Tripping issue 8 Shutdown availability if applicable YES 9 Warranty status YES 10 Commissioned / Installed date NA 11 Serial No: or DOM of the product 12 Name & phone No: of person registering the complaint Devendra Mahajan ¦ 9131575424 Note : Point Nos: 1 to 9 are compulsory | 2023-09-25 | 2023-09-26 14:56 | No | Warranty | Yuvan Engineering | Near Sch-51 | Indore | Indore | Madhya Pradesh | India FS ED&I CSP West Team ABR Technical Service Indore | Chirag Jain_ABR Tecneical Services Indore | ABR Technical Services (9574) | Reached at site and found as per customer ACB tripping issue when they turn ON outgoing MCCB. Then we checked and found ACB working properly. By the time we reach site customer resolved tripping issue himself by changing ACB & MCCB setting. As ACB working properly so customer not allowed to stay in panel room, also customer not shared much details so we are unable to take more technical data. Currently ACB working properly so we are now closing this case. | Repair |  | 9- Service Validated | 2023-09-26 14:57 |  |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11174906 |  | 2023-09-12 16:22 | 2023-09-16 |  | 2023-08-28 19:40 | SUVTP40KHS | SUVTP40KHS | SUVTP40KHS | QS1645350590 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-08-28 | 2023-08-25 15:30 | No | Contract | STP Investment Services India Pvt Ltd | SJR Tech Park, Opp Sri Sai Baba Hospital, Whitefield null | Bangalore | 560066 | Karnataka | India FS South1 HBN CSP UBM Autopower Pvt. Ltd Bangalore | Raghavendra UBM Autopower Pvt. Ltd Bangalore | Autopower systems and solutions | PM done, UPS working normal. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-12 16:24 |  |  | 0 | INR | 0 | ENM SECURE POWER
WO-11175080 |  | 2023-09-12 17:24 | 2023-09-12 |  | 2023-08-28 19:54 | LEONARDO EV,DX,R22,EC FAN,( ZR68KC -COPELAND ), DOWNFLOW WITHOUT HEATER & HUMIDI | TDAV0511AN002 | TDAV0511AN002 | ZK1603011591 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-08-28 | 2023-09-12 21:30 | No | Contract | RELIANCE JIO INFOCOMM LIMITED | S/O Sh Durga Prasad Khatauni No 00234 Khasra No 1658 Vill Mau Pargana Mauranipur Tehsil Mauranipur Distt Jhansi | Jhansi | 284204 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Sunil Kumar Freezeotech Airconditioning & Refrigeration Lucknow | Freezeotech Airconditioning & Refrigeration Corporation | PM DONE CLEAN THE FILTER CONDENSORE COIL CHECK GAS PSI COMPRESSORE CHECK ALL PARAMETER UNIT IS WORKING OK | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-12 17:29 |  |  | 330 | INR | 330 | ENM SECURE POWER
WO-11221533 |  | 2023-09-06 16:07 | 2023-09-06 |  | 2023-09-06 13:49 | SURT10000XLINBQ | SURT10000XLINBQ | SURT10000XLINBQ | BQ1513001601 | Under AMC P: Battery Installation RBC44 4 Set S: Battery Installation RBC44 4 Set | 2023-09-06 | 2023-09-08 16:31 | No | Commercial Action - Sales | Reliance Retail | U C Plaza Near Moulana Hospital Ootty Road null | Perinthalmanna | 679322 | Kerala | India FS South2 HBN CSP APSMarketingCompany Calicut | PRAMEESH P.S APSMarketingCompany Calicut | APS Marketing Company | battery instalation done ups working fine 0M-1863C-NC * 4NOS 0A2334G05795 0A2334G05786 0A2334G05801 0A2334G05778 | Commissioning & Installation | Battery Installation | 10- Closed | 2023-09-08 16:46 |  |  | 75 | INR | 75 | ENM SECURE POWER
WO-11309614 | 104267046 | 2023-09-26 11:30 | 2023-09-26 |  | 2023-09-26 10:49 | METSEEM6438HCL10RS | METSEEM6438HCL10RS | METSEEM6438HCL10RS |  | DOP: 13/2/2023 METSEEM6438HCL10RS Qty:1 P: Meter not working Hallmark Sunnyside Manchirevula, Hyderabad, Telangana 500075 Sahith Reddy 9989444804 | 2023-09-26 | 2023-09-26 12:00 | No | Warranty | Hallmark Sunnyside | Manchirevula Rangareddy null | Hyderabad | 500075 | Telangana | India FS ED&I CSP South Team Sumanth Electrical Services Hyderabad | Basanth Reddy_SUMANTH ELECTRICAL SERVICES HYDERABAD | Sumanth Electrical Services | Visited the Site and Inspected the Schneider Electric-METSEEM6438HCL10RS-01 No's. Here in our observation we found that the as per customer requirement. Customer need to take the KW reading but the meters are seted to W/P PF. So, we have seted to KW and explained about the reading calculation all the meter are working properly. Note: In some meter programming has not done properly and to be done by panel builder. We didn't found any quality related problem in the meter and Complaint is closed. | Repair |  | 8- Service Completed | 2023-09-26 15:53 |  |  | 20 | INR | 20 | ENM POWER PRODUCTS
WO-11310196 | 104253365 | 2023-09-27 11:47 | 2023-09-26 |  | 2023-09-26 11:36 | INA_3P96280_20 | INA_3P96280_20 | INA_3P96280_20 |  | DELHIVERY DKT NO:251200725 DT 22.09.2023 NO OF LOT 02 CARTON RECEIVE OPEN AND DAMAGE CONDITION (INA_3P6280_20)PALLET | 2023-09-26 | 2023-09-27 17:44 | No | Warranty | Novatek Electro Engineers Pvt. Ltd. | 3440, Service Road, RPC Layout, W.C.Road, Vijayanagar, | Bangalore | 560040 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Swamy HJ_P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | Visited the site and inspected NS 800A 3 pole MCCB = 2 No's. 1) Both MCCB front cover corner side little damaged. 2) MCCB's master corton was damaged condition. product damaged status. Customer mentioned in POD copy. Hence we have taken all the photos and details and we will inform to Schneider's Electrics. After we will give the feed back ASAP. Material Received date: 25/09/2023 Invoice Date: 21/09/2023 S/N: 226035367 PO No:NE/B/0335/0923/S.G.K We sent all the transit damage details to Schneider Customer care. And we get the Ref: 104312159 from Schneider Customer Care. | Assessment/ Inspection | Data Collection | 8- Service Completed | 2023-09-27 17:45 |  |  | 5 | INR | 5 | ENM POWER PRODUCTS
WO-11310528 | 104247022 | 2023-09-27 08:03 | 2023-09-26 |  | 2023-09-26 13:00 | LC1E3210M7 | LC1E3210M7 | LC1E3210M7 |  | DOP: 13/9/2023 LC1E32 Qty:1 P: Screw issue Ragavendra controls Pvt. Ltd Vellanaipatti, Coimbatore ? 641 048, Tamil Nadu, India. E.MAIL :qc@rclindia.in 7397797109 Karthic raja.S | 2023-09-26 | 2023-09-27 17:25 | No | Warranty | RAGAVENDRA CONTROLS PRIVATE LIMITED | Site Address 6855\1A MOLAPALAYAM ROAD VELLANAIPATTI POST | COIMBATORE | 641048 | Tamil Nadu | India FS ED&I CSP South Team Power Pro Engineering Services Coimbatore | KV ARUNKUMAR_POWER PRO ENGINEERIG SERVICES COIMBATORE | Powerpro Engineering Services | WE HAVE VISITED THE SITE AND INSPECTED WE FOUND L1-TERMINAL SCREW NOT TIGHT DUE TO CONTACTOR HEAD SPOILED WE HAVE COLLECTED THE DETAILS FOR FURTHER ACTION AND ARRAGING FOR FREE REPLACEMENT FOR THIS | Repair |  | 8- Service Completed | 2023-09-28 14:03 |  |  | 21 | INR | 21 | ENM POWER PRODUCTS
WO-11221795 | 103818360 | 2023-09-06 17:45 | 2023-09-06 |  | 2023-09-06 15:04 | APC Symmetra LX 16kVA N,1 Ext. Run Tower Frame 220/230/240V or 380/400/415V | SYAF16KXR9I | SYAF16KXR9I | AD1705220381 | FW: IM02996067 RJ-GBP-01 UPS POWER MODULE ISSUE Site Code:IM01989087 RJ/GBP/01 Under AMC P:UPS one power module issue. S:AMC | 2023-09-06 | 2023-09-19 12:00 | No | Contract | CBEC | Gandhi Nagar Bhilwara Road Gulabpura Dist Bhilwara | Gulabpura | 311021 | Rajasthan | India FS North1 HBN CSP G NAGAR & ASSOCIATES Udaipur | Ambalal Menaria_G NAGAR & COMPANY Udaipur | G NAGAR & ASSOCIATES | I replace module SYPMA4KI ,now ups working fine check by costumer. | Repair |  | 10- Closed | 2023-09-19 12:01 |  |  | 250 | INR | 250 | ENM SECURE POWER
WO-11310569 | 104250338 | 2023-09-27 08:05 | 2023-09-26 |  | 2023-09-26 13:18 | LC1D65ABD | LC1D65ABD | LC1D65ABD | 8C23125 | capacitor duty contactor Checklist for the Registration of Service Request Sr. No Particulars Doc. Ref :- SE/CCC/003 1 Company Name & Complete Address with pin code - Where product is installed Roots Industries India private Limited SF NO:414/2,461/2-C & 462/3 Agharaharasamakulam Athipalayam, Coimbatore- 641110 2 Contact Person at Site : Name & Mobile No. Jeeva B 8608121975 Alternate Mobile No : 8667814299 3 Contact Person at Site - Email Address** hpedple@roots.co.in 4 Product Issue Type (Please select from drop down of column C-9) Hardware Issue 5 Are you ready to troubleshoot the issue remotely ? Yes/NO. If Yes, Our technical support engineer will call back to troubleshoot the issue remotely. No 6 Defective Product Model/Part No (Pls refer FAQ sheet ) LC1D65 M7 7 Nature of Defect* - Defects Video and Photographs Poll Open 8 Shutdown availability if applicable Yes 9 Photograph of product where Serial No/Batch Code or Date of Manufacturing printed - Please refer FAQ sheet to find the Batch code details on the products 8C23125 10 Proof Of Purchase - Pease attach SE*** Authorised Partner Invoice soft copy along with this check list SRI VISHNU ELECTRICALS 11 Name & phone No: of person registering the Service Request Jeeva B 8608121975 | 2023-09-26 | 2023-09-27 17:22 | No | Warranty | Roots Industries India Ltd | SF NO:414/2,461/2-C & 462/3 Agharaharasamakulam HPED unit 2 SF no 414 agrahara samanth null | COIMBATORE | 641110 | Tamil Nadu | India FS ED&I CSP South Team Power Pro Engineering Services Coimbatore | KV ARUNKUMAR_POWER PRO ENGINEERIG SERVICES COIMBATORE | Powerpro Engineering Services | WE HAVE VISITED THE SITE AND INSPECTE WE FOUND CAP-DUTY CONTACTOR Y-PH POLE OPEN CIRCUITED AND WE HAVE CHECKED THE TIGHTESS FOUND OK WE HAVE COLLECTED THE DETAILS FOR FURTHER ACTION AND ARRAGING FOR FREE REPALCEMENT FOR THIS | Repair |  | 8- Service Completed | 2023-09-30 22:01 |  |  | 31 | INR | 31 | ENM POWER PRODUCTS
WO-11310605 | 104272734 | 2023-09-28 15:24 | 2023-09-26 |  | 2023-09-26 13:33 | LV516303 | LV516303 | LV516303 | 10-2022-W25-6 | LV516303 MCCB Tripping Issue As Per The serial number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- RNT Metals Pvt. Ltd. E-44/E2-F7, RIICO Industrial Area, Khushkhera, Bhiwadi Alwar 301707 Rajasthan India Contact Person Details:- Shivdat Mishra 9214013925 Product and Issue:- LV516303 Serial number:- 10-2022-W25-6 MCCB is tripping frequently, rating is 160A, Ir rating plug is at 160, No burning sign at terminals side, Running load is 70A approx as per customer. | 2023-09-26 | 2023-09-28 15:26 | No | Warranty | RNT Metals Pvt. Ltd. | E-44/E2-F7, RIICO Industrial Area, Khushkhera, Bhiwadi null | Alwar | 301707 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mccb found overheating due to improper termination, Hence no replacement given to customer . Email : id not provided by customer . | Repair |  | 8- Service Completed | 2023-09-28 15:33 |  |  | 80 | INR | 80 | ENM POWER PRODUCTS
WO-11179178 | 103623180 | 2023-08-30 10:19 | 2023-08-29 | NA | 2023-08-29 17:42 | GCR_NSX | GCR_NSX | GCR_NSX |  | As per the invoice, The Product (Motor mechanism) is in Warranty. Kindly arrange the site visit. Issue: Motor mechanism is not working Address Prama Hikvision India Pvt. Ltd. Hira Industrial Estate Park, Off NH-8, Vasai Phata, Vasai (East), Palghar Thane 401208 Maharashtra India Contact person Details: - Mr.Ganesh 7506906111 | 2023-08-29 | 2023-08-30 17:43 | No | Warranty | Prama Hikvision India Pvt. Ltd. | Hira Industrial Estate Park, Off NH-8, Vasai Phata, Vasai (East), Palghar null | Thane | 401208 | Maharashtra | India FS ED&I CSP West Team East India Power Engineers Mumbai | Ratnesh Shigvan East India Power engineers Mumbai | East India Power Engineers (5043) | Visited the site & checked the motor mechanism with assembly An MCCB checked manual operation and found ok. Checked electrical auto mode operation and found spring charging not done in the mechanism. Checked the mechanism and found wiring is not done as per Schneider standards. Due to the mechanism getting failure. not use SDE contact. | Repair |  | 8- Service Completed | 2023-09-08 16:37 | =S= Consig Fill up 226017020 |  | 43 | INR | 43 | ENM POWER PRODUCTS
WO-11181292 | 103622867 | 2023-08-30 11:57 | 2023-08-30 |  | 2023-08-30 09:22 | METSEEM6436HCL10RS | METSEEM6436HCL10RS | METSEEM6436HCL10RS |  | complaint for EM6436 CL1.0 RS Company Name & Complete Address with pin code - Where product is installed VAIGHAI AGRO PRODUCTS LTD 350/1 NAGARI, SHOLAVANDAN ROAD, THANICHIYAM VILLAGE, VADIPATTI TK, MADURAI-625221 Contact Person at Site : Name & Mobile No. PUGAL ETHAN - 9976005416 Alternate Mobile No : 8344424446 Contact Person at Site - Email Address** mari.pkani@gmail.com Defective Product Model/Part No (Pls refer FAQ sheet ) METSEEM6436HCL10RS-4PCE Nature of Defect* - Defects Video and Photographs DISPLAY NOT WORKING WHEN GIVEN SUPPLY Shutdown availability if applicable yes POP - SE Authorised Partner Invoice soft copy se inv 9008253530 dt: 17-09-2023 Photograph of product where Serial No/Batch Code or Date of Manufacturing printed - Please refer FAQ sheet DOM: 060922 S/N: 540420187984 | 2023-08-30 | 2023-09-05 11:56 | No | Warranty | Vaighai Agro Products | RSS No:350, Cholavandan Road, Nagari | Madurai | 625221 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | George KJ_Omicon Engineering Madurai | Omicon Engineering | Inspected the site and checked the meter REF : METSEEM6436HCL10RS found Display not glowing . so given external supply and checked same issue observed . | Repair |  | 9- Service Validated | 2023-09-05 12:03 |  |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11311058 | 104276706 | 2023-09-27 10:36 | 2023-09-26 |  | 2023-09-26 16:28 | TeSys GV2-LV equipment - Low voltage circuit breaker | TeSys GV2-LV equipment - Low voltage circuit breaker |  | PK23053 | As Per The serial number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Reliable Electro Engineers FF-114, R.R. Auto industries Complex, Nr. Bank of Baroda, Makarpura, G.I.D.C Vadodara 390010 Gujarat India Contact Person Details:- Senta Jaydip 9327282941 Product and Issue:- GVAD1010 PK23053-- Contact Changeover Issues | 2023-09-26 | 2023-09-28 14:53 | No | Warranty | Reliable Electro Engineers | FF-114, R.R. Auto industries Complex, Nr. Bank of Baroda, Makarpura, G.I.D.C null | Vadodara | 390010 | Gujarat | India FS ED&I CSP West Team Jay Services Vadodara | Ghanshyam Kachiya_Jay Services Vadodara | Jay Services | we visited at site and checked that GVAD1010 -02 NOS Both are ok ,we mount with MPCB and tested working ok. , We also checked one MPCB GV2ME04 Observed ON-Off Operation found ok but B pole continuity open now we replaced from our distributor stock . | Repair |  | 8- Service Completed | 2023-09-29 11:05 | =S= Consig Fill up 226086497 |  | 6 | INR | 6 | ENM POWER PRODUCTS
WO-11311107 | 104268581 | 2023-09-27 14:53 | 2023-09-26 |  | 2023-09-26 16:49 | GCR_CVS_T1_19 | GCR_CVS_T1_19 | GCR_CVS_T1_19 |  | regarding faulty material R/Sir we received a complain against item MCCB LV580303 CUSTOMER NAME DAYA MANUFACTURERS & TRADERS JAGAN GOPALA INVOICE NO 796 DATED 05.08.2023 SITE AT :168C NEAR SONI PUBLIC SCHOOL FOCAL POINT CONTACT NO MR OM PARKASH /9417354574 BILL ALSO ATTACHED WITH MAIL Thanks and Regards VIKRAM GOEL (Marketing Manager) JAGAN GOPALA & CO. S.C.O. - 58, SECTOR - 26D MADHYA MARG CHANDIGARH-160019 | 2023-09-26 | 2023-09-27 17:24 | No | Warranty | Daya manufacturer and traders | 168C Near Focal Point Ekta Nagar | Patiala | 147003 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | checked the mccb found humming sound due to imput side terminals loose. Tighten the mccb terminals now mccb working fine, Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-27 17:27 |  |  | 120 | INR | 120 | ENM POWER PRODUCTS
WO-11175137 |  | 2023-09-16 18:05 | 2023-09-28 |  | 2023-08-28 20:01 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | JK1927000655 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-08-28 | 2023-09-28 21:30 | No | Contract | Reliance Jio Infocomm limited | MOHALLA- DARUD GIRA, TEHS- KAIMGANJ null | Farrukhabad | 209503 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Karuna Tripathi Freezeotech Airconditioning & Refrigeration Lucknow | Freezeotech Airconditioning & Refrigeration Corporation | pm done clean the filter condenser coil check all parameter unit is working ok | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-28 13:40 |  |  | 221 | INR | 221 | ENM SECURE POWER
WO-11221824 | 103822729 | 2023-09-07 10:26 | 2023-09-06 |  | 2023-09-06 15:17 | SURT6000XLI-CC_PUN018_CAP_Tils Systems and Software _1-Jan-19 | SURT6000XLI-CC | SURT6000XLI-CC | B21825009390 | Under AMC P:UPS not powering on C:server T:Customer request no problem found with input side and EPO switch S:AMC | 2023-09-06 | 2023-09-08 14:54 | No | Contract | McDonalds family restaurant | Unit no: F22, Seasons Mall, Magarpatta , Hadapsar, | Pune | 411028 | Maharashtra | India FS West1 HBN CSP_Modular Electronics Pvt Ltd Pune | Hanuman Patel_Modular Electronics Pvt Ltd Pune | Modular Electronics | UPS ok in technical points but physically front dust filter plate damaged | Repair |  | 8- Service Completed | 2023-09-08 15:03 |  |  | 15 | INR | 15 | ENM SECURE POWER
WO-11175235 |  | 2023-09-30 10:26 | 2023-09-30 |  | 2023-08-28 20:16 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | JK1933003913 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-08-28 | 2023-09-30 21:00 | No | Contract | Reliance Jio Infocomm Ltd | Mr. Hariram S/o Late Pudai, Vill Rahath PO Bikapur, Tehsil Bikapur null | Faizabad | 224204 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Karuna Tripathi Freezeotech Airconditioning & Refrigeration Lucknow | Freezeotech Airconditioning & Refrigeration Corporation | pm done clean the filter condenser unit with jet pump check all parameter unit is working ok | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-30 11:59 |  |  | 173 | INR | 173 | ENM SECURE POWER
WO-11221830 | 103822413 | 2023-09-06 17:00 | 2023-09-06 |  | 2023-09-06 15:19 | APC Smart-UPS RC 6000VA 230V for India - No Batteries | SRC6KUXI | SRC6KUXI | B21513001567 | FW: All in one Rack ups not working @4078_KPHB Colony - 6th Phase ¦¦ call id : INC0004352780 P:UPS not working S:AMC | 2023-09-06 | 2023-09-07 15:02 | No | Contract | HDFC Bank Ltd | HDFC Bank Branch Code 4078 Plot No 131 132 First Floor KPHB Colony 6th Phase Kukatpally Hyderabad | Hyderabad | 500085 | Telangana | India FS South3 HBN CSP CENTRALDATASYSTEMS HYDERABAD | Nagesh CENTRALDATASYSTEMS HYDERABAD | Central Data Systems Pvt Ltd | Checked ups on both mains and battery mode for 20 minutes with load 20% No issues found. | Repair |  | 10- Closed | 2023-09-07 15:07 |  |  | 12 | INR | 12 | ENM SECURE POWER
WO-11183118 | 103653583 | 2023-09-01 17:06 | 2023-08-30 |  | 2023-08-30 12:07 | LC1E18M7 | LC1E18M7 | LC1E18M7 | 1022343 | As per the Sr. no, The Product is in Warranty. Kindly arrange the site visit. Issue: Stucked in on position Address Tulip Institutional Service Pvt Ltd Plot 701 Pace City II Sector 37 Gurgaon 122004 Haryana India Contact person Details: - Mr.Dinbandu 8287524797 | 2023-08-30 | 2023-09-07 14:50 | No | Warranty | Tulip Institutional Service Pvt Ltd | Plot 701 Pace City II Sector 37 | Gurgaon | 122004 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the contactor found phase missing, Hence faulty replaced. LC1E1810M7 - 1 nos Email : nirala7765948720@gmail.com | Repair |  | 9- Service Validated | 2023-09-07 14:54 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11314806 | 104277385 | 2023-09-27 11:38 | 2023-09-27 | As per sr. no. product in warranty raise ZVO for replacement | 2023-09-27 10:34 | LC1DT32T7 | LC1DT32T7 | LC1DT32T7 |  | COMPLAIN ? LC1DT32 M7 - QTY - 01 (WINNER TECHNOLOGIES.) Checklist for Complaint Registration 1 Name of Customer M/S WINNER TECHNOLOGIES. 2 Site Address A-28, Patel Industrial Estate, Opp. Katargam Community Hall, Nr. Ganga H, Vasta-devdi Road, Katargam - 395004, SURAT Contact Phone / Mob. No: 9586261656 3 Name of contact person at site MR.UMESH BHAI 5 Defective product details LC1DT32 M7 - QTY - 01 6 Product Make SCHNEIDER-CONTACTOR 7 Nature of Defect NOT WORKING PROPERLY (1 POLE IS OPEN) 8 Shutdown availability if applicable 9 Warranty status UNDER WARRANTY 10 Commissioned / Installed date 11 Serial No: or DOM of the product BILL NO - : 1813/23-24 DATE - 25-05-2023 12 Name & phone No: of person registering the complaint JOHNSON- 8780431402 13 NOTE Note : Point Nos: 1 to 9 are compulsory | 2023-09-27 | 2023-09-27 21:30 | No | Warranty | Winner Technologies (Mudas Diamond) / Yogi Technologies | A-28, Patel Industrial Estate, Opp. Community Hall, Near Honda Showroom, Vastadevdi Road, Katargam | Surat | 395004 | Gujarat | India FS ED&I CSP West Team VARDHAMAN ELECTROSOFT Vadodara | MAHENDRA SINGH VARDHAMAN ELECTROSOFT Vadodara | VARDHAMAN ELECTROSOFT | we visited the site and check the contractor and found physically ok .open the contractor LCLDT32 and check we found grease on Au>. coil terminal A1 and A2 after that clean contractor working ok | Repair |  | 9- Service Validated | 2023-09-28 11:01 | =S= Consig Fill up 226085689 |  | 15 | INR | 15 | ENM POWER PRODUCTS
WO-11175192 |  | 2023-09-29 15:57 | 2023-09-29 |  | 2023-08-28 20:09 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | C21651000495 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-08-28 | 2023-09-29 21:30 | No | Contract | Reliance Jio Infocomm Ltd | Ward No.8 Mohalla-Kanoongo,Zamania Tehsil null | Gazipur | 232329 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Harinder Yadav Freezeotech Airconditioning & Refrigeration Lucknow | Freezeotech Airconditioning & Refrigeration Corporation | Pm done clean the filter and condensore coil clean and all parameter check unit is working ok | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-29 16:07 |  |  | 279 | INR | 279 | ENM SECURE POWER
WO-11221872 | 103823430 | 2023-09-06 17:01 | 2023-09-06 |  | 2023-09-06 15:39 | APC Smart-UPS RT 10000VA 230V Harsh Environment | SURT10000XLI-CC | SURT10000XLI-CC | B21516000371 | FW: RR : IM15438991 ¦ Store Code : 5844 ¦ SCHNEIDER ¦ TAMIL NADU -TRENDS Under AMC P: UPS output supply not coming S:AMC | 2023-09-06 | 2023-09-07 17:15 | No | Contract | Reliance Retail Ltd | RRL Trends Alpha Lotus Towers ,713/1, B1 Acadia, 60 Feet Raod Behind Muncipal Office, Avadi, Near Chennai | Chennai | 600056 | Tamil Nadu | India FS South2 HBN CSP_Soundry Power System Chennai | SaravananMano SoundryPowerSystems Chennai | Soundry Power Systems-Chennai | UPS WORKING NORMAL. | Repair |  | 10- Closed | 2023-09-07 17:21 |  |  | 20 | INR | 20 | ENM SECURE POWER
WO-11183218 | 103651043 | 2023-08-30 13:24 | 2023-08-30 | NA | 2023-08-30 12:47 | LRD07 | LRD07 | LRD07 |  | As per the invoice, The Product is in Warranty. Kindly arrange the site visit. Issue: Tripping issue in LRE07 Stuck issue in contactor Address Electrocare (India) Private Ltd(10809) Unit No.243, 2nd Floor, Plot No.Gen/2/1/C (Part), Raheja District-2, Edison Building No.1, Near Prabhat Diary & Thyrocare, TTC Industrial Area,Shiravane, Juinagar (East), Navi Mumbai 400705 Maharashtra India Contact person Details: - Mr.Vinod 9594940048 | 2023-08-30 | 2023-08-30 17:29 | No | Warranty | Electrocare (India) Private Ltd(10809) | Unit No.243, 2nd Floor, Plot No.Gen/2/1/C (Part), Raheja District-2, Edison Building No.1, Near Prabhat Diary & Thyrocare, TTC Industrial Area,Shiravane, Juinagar (East), Juinagar (East) | Navi Mumbai | 400705 | Maharashtra | India FS ED&I CSP West Team East India Power Engineers Mumbai | Sandeep Ingavale East India Power engineers Mumbai | East India Power Engineers (5043) | Visited the site & checked the LRD07 relay and found burnout condition it is not tripping overload protecting on load. Hence the relay needs to be replace with a new one. Also checked the Contactor and found the stuck condition need to be a replace with a new one. | Repair |  | 8- Service Completed | 2023-09-02 15:55 | =S= Consig Fill up 226010225 |  | 12 | INR | 12 | ENM POWER PRODUCTS
WO-11316336 | 104271396 | 2023-09-27 12:28 | 2023-09-27 |  | 2023-09-27 11:58 | LV429387 | GCR_NSX100_630 | GCR_NSX100_630 | TC-2022-W41-5 | Ref Part No: LV429387 MCCB:-1 NO was not working LV429387 - TC-2022-W41-5 operation issue Site Address: Visiontekniks Engineering & Automation # Plot No: 208/10 ¦ Phase-II, Sector-III, Lane-IV ¦ IDA Cherlapally, Hyderabad- 51 Phone: + 91 7013383897 ¦ Mobile: +91 9392424883 Contact Person Name:- Mr. Ayodhya , 85009 67383 | 2023-09-27 | 2023-09-28 12:00 | No | Warranty | VISION TEKNIKS | Plot No 208/10, St 4, Sector3, Phase-ii, Ida Cherlapallt | Hyderabad | 500005 | Andhra Pradesh | India FS ED&I CSP South Team Sumanth Electrical Services Hyderabad | Basanth Reddy_SUMANTH ELECTRICAL SERVICES HYDERABAD | Sumanth Electrical Services | Visited Site and inspected schneider electric MCCB and in our observation we found that MCCB is not closing after fitment of MN UVR Accessories and MCCB is not getting closing due to MCCB Trip Latch Pin mismatching and we have rectified the Pin Mismatching problem | Repair |  | 8- Service Completed | 2023-09-28 20:23 |  |  | 10 | INR | 10 | ENM POWER PRODUCTS
WO-11175198 |  | 2023-09-30 12:39 | 2023-09-30 |  | 2023-08-28 20:10 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | C21722001012 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-08-28 | 2023-09-30 21:30 | No | Contract | Reliance Jio Infocomm Ltd | T-Bindki, D-Fatehpur null | Fatehpur | 212625 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Karuna Tripathi Freezeotech Airconditioning & Refrigeration Lucknow | Freezeotech Airconditioning & Refrigeration Corporation | pm done clean the filter condenser unit with jet pump check all parameter unit is working ok | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-30 12:58 |  |  | 91 | INR | 91 | ENM SECURE POWER
WO-11316394 | 104280621 | 2023-09-27 19:23 | 2023-09-27 |  | 2023-09-27 12:18 | METSEEM6400NGRSCL1 | METSEEM6400NGRSCL1 | METSEEM6400NGRSCL1 | 44927 | Complaint -Reg Dear Sir/Madam, Greetings from GVK!! We GVK Power and engineering solutions had purchased 10 nos of Schneider make Schneider make Panel meters from your Authorized dealer named Lotus Controls located at Bangalore. There is a mismatch in the readings from one meter to another. Kindly depute your service representative to the address mentioned below. We are hereby attaching photographs of the few meters for kind need. Site Address: S S SUPER FOODS PVT LTD Sadali Hobli, S Gollahalli Village, Sidhlaghatta Taluk, Chikkaballapur - 562104 Contact Person Name:Mr. Venkatadri Contact No: 90364 99476/ 94482 72928 For GVK POWER & ENGINEERING SOLUTIONS #1138, 20th Cross, A" Block, Sahakaranagar, Bengaluru - 560092. | 2023-09-27 | 2023-09-28 13:01 | No | Warranty | S S SUPER FOODS PVT LTD | Plot No 03 Sadali Hobli S Gollahalli Village | Bengaluru | 562104 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | C Gunasekaran_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | We had visited the site and checked the customer reported meter.found getting reading wrong .Due to CT Direction reversed.so we inter changed ct link and checked kw and kwh getting positive.There is no issue with our meter. | Repair |  | 8- Service Completed | 2023-09-28 13:05 |  |  | 110 | INR | 110 | ENM POWER PRODUCTS
WO-11175211 |  | 2023-09-29 14:42 | 2023-09-29 |  | 2023-08-28 20:12 | EFC MONOBLOCK UNIT 1.3TR ( START RUN RELAY KIT, SEQUENCING , RS485 ) | WDF0181BN003 | WDF0181BN003 | C21850001101 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-08-28 | 2023-09-29 21:30 | No | Contract | Reliance Jio Infocomm Ltd | Village -Achhyawat, Mahrajganj null | Azamgarh | 276137 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Harinder Yadav Freezeotech Airconditioning & Refrigeration Lucknow | Freezeotech Airconditioning & Refrigeration Corporation | pm done of efc unit we clean filters and condenser coil check all parameter unit is working ok | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-29 14:52 |  |  | 279 | INR | 279 | ENM SECURE POWER
WO-11183465 |  | 2023-09-15 10:27 | 2023-08-30 |  | 2023-08-30 14:55 | LV438279 | LV438279 | LV438279 | TC-20417 | FSB _ WO _ For Orchid activity Kindly create 2 nos FSB WO for minitop hammer replacement PRB-233066 , Please refer attachment for Customer address. 12 nos for each day. Product : NSX630S DC, LV438279,TC20417. Contact Name : Pradeep, 07619122865. Regards, P.BALAKUMAR, Field Service Team, Schneider Electric , PH: 7428380635, Bangalore. | 2023-08-30 | 2023-09-22 10:31 | No | Pending Contract | Juniper Networks India Pvt Ltd | Prestige Tech Park Elnath-Exora Business Park Survey No.111/1 to 115/4 Wing A & B Amane Bellandur Khane Village Marathahalli Marathahalli - Sarjapur Outer Ring Road | Bangalore | 560103 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | C Gunasekaran_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | As per SE and customer request, we had visited the site and checked the customer installed MCCB.Found impacted date code .so we had replaced Hammer and checekd ON/OFF/TRIP working ok. | Field Service Bulletin | High - Immediate Action | 9- Service Validated | 2023-09-22 10:42 |  |  | 13 | INR | 13 | ENM POWER PRODUCTS
WO-11316443 | 104302887 | 2023-09-27 19:21 | 2023-09-27 |  | 2023-09-27 12:40 | LV432641 | LV432641 | LV432641 |  | As Per The serial number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Devi Electricals #10, 2nd cross, Naidu layout, Rajivgandhi road, J P Nagar, 6th phase, Bangalore Bangalore 560078 Karnataka India Contact Person Details:- 9741983851----Sasi Kumar 9986775768----Hari Product and Issue:- LV432641 Motor Mechanism is not getting spring charge in auto and manual mode. As per customer mounting is done properly | 2023-09-27 | 2023-09-29 12:23 | No | Warranty | Devi Electricals | #10, 2nd cross, Naidu layout, Rajivgandhi road, J P Nagar, 6th phase, Bangalore | Bangalore | 560078 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Rajalingam P SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported the MT 400/630A motor mechanism not getting spring charge in auto mode &manual mode due to main mechanism got failed the issue cannot repairable so we have replaced the new motor unit | Repair |  | 8- Service Completed | 2023-09-29 21:33 |  |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11175213 |  | 2023-09-16 15:53 | 2023-09-29 |  | 2023-08-28 20:12 | TDAVQ | TDAVQ | TDAVQ | JK2105005639 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-08-28 | 2023-09-29 20:30 | No | Contract | RELIANCE JIO INFOCOMM LIMITED | GHATA NO 662, SITUATED AT VILLAGE JAMAYATPUR, PARGANA KHAIRABAD null | SITAPUR | 261131 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Karuna Tripathi Freezeotech Airconditioning & Refrigeration Lucknow | Freezeotech Airconditioning & Refrigeration Corporation | pm done clean the filter condenser unit with jet pump check all parameter unit is working ok | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-29 11:14 |  |  | 88 | INR | 88 | ENM SECURE POWER
WO-11222036 | 103825698 | 2023-09-06 20:09 | 2023-09-06 |  | 2023-09-06 17:11 | APC Symmetra LX 16kVA N+1 Tower Frame, 220/230/240V or 380/400/415V | SYAF16KI | SYAF16KI | QD0802180381 | FW: IM02999392 MH-BOOM-10 RIM is Faulty Under AMC P: RIM is Faulty S:AMC | 2023-09-06 | 2023-09-13 16:30 | No | Contract | Central Board of Excise & Customs-CBEC | Ganges Ink Bldg., 110 1st floor, Opp.Cipla, L.B.S.Marg,Vikhroli(West) null | Mumbai | 400083 | Maharashtra | India FS West1 HBN CSP_Integriti Thane | Sushil Shede_Integriti Thane | INTEGRITI | Intelegent Module Replacement. Defective Material Details: Defective Model Number: - SYMIM5Q Defective Serial Number: - 5Q1702T75859 Defective Material Details: Defective Model Number: - SYMIM5Q Defective Serial Number: - 5Q1947T13710 | Repair |  | 8- Service Completed | 2023-09-13 17:25 |  |  | 12 | INR | 12 | ENM SECURE POWER
WO-11183692 | 103658467 | 2023-09-01 12:20 | 2023-08-30 |  | 2023-08-30 16:50 | LC1DMKM7 | LC1DMKM7 | LC1DMKM7 |  | As per the invoice, The Product is in Warranty. Kindly arrange the site visit. Issue: Contactor is not getting ON Address Annapurna Bakers Pvt. Ltd A3/3, MTC PANKI SITE - 3 Industrial Area kanpur 208022 Uttar Pradesh India Contact person Details: - Mr.Amar 9170108000 9335005027 | 2023-08-30 | 2023-09-07 16:12 | No | Warranty | Annapurna Bakers Pvt. Ltd | A3/3, MTC PANKI SITE - 3 Industrial Area null | kanpur | 208022 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Aman Khare_Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found contactor having coil issue so we replaced . | Repair |  | 9- Service Validated | 2023-09-07 16:14 |  |  | 115 | INR | 115 | ENM POWER PRODUCTS
WO-11175226 |  | 2023-09-30 12:03 | 2023-09-30 |  | 2023-08-28 20:14 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | C21723002127 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-08-28 | 2023-09-30 21:30 | No | Contract | Reliance Jio Infocomm Ltd | Baskhari Market null | Ambedkar Nagar | 224129 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Karuna Tripathi Freezeotech Airconditioning & Refrigeration Lucknow | Freezeotech Airconditioning & Refrigeration Corporation | pm done clean the filter condenser unit with jet pump check all parameter unit is working ok | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-30 12:15 |  |  | 215 | INR | 215 | ENM SECURE POWER
WO-11222100 | 103826618 | 2023-09-07 11:29 | 2023-09-07 |  | 2023-09-06 17:43 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | C21717000472 | P:c21717000472--Cooling issue Under AMC P:c21717000472--Cooling issue S:AMC | 2023-09-06 | 2023-09-07 18:22 | No | Contract | RELIANCE JIO INFOCOMM LIMITED | S/O Manish Opposite The Pani Taki Dalli Rajhara | Dalli Rajhara | 491228 | chhattisgarh | India FS East Cooling CSP Capital Refrigeration Raipur | Abdul Bari_Capital Refrigeration Raipur | Capital Refrigeration | REPLACED CONDENSER FAN AND TESTING | Repair |  | 10- Closed | 2023-09-07 18:23 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 130 | INR | 130 | ENM SECURE POWER
WO-11175229 |  | 2023-09-30 10:10 | 2023-09-30 |  | 2023-08-28 20:15 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | JK1918001001 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-08-28 | 2023-09-30 19:00 | No | Contract | Reliance Jio Infocomm Ltd | Arkhapur tanda ambedkar nagar null | Tanda | 224190 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Karuna Tripathi Freezeotech Airconditioning & Refrigeration Lucknow | Freezeotech Airconditioning & Refrigeration Corporation | pm done clean the filter condenser unit with jet pump check all parameter unit is working ok | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-30 10:25 |  |  | 206 | INR | 206 | ENM SECURE POWER
WO-11222114 | 103826880 | 2023-09-07 11:36 | 2023-09-06 |  | 2023-09-06 17:51 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | C21715000451 | P:C21715000451--Unit is dead Under AMC P:C21715000451--Unit is dead S:AMC | 2023-09-06 | 2023-09-07 12:48 | No | Contract | RELIANCE JIO INFOCOMM LIMITED | S/O Manish Opposite The Pani Taki Dalli Rajhara | Dalli Rajhara | 491228 | chhattisgarh | India FS East Cooling CSP Capital Refrigeration Raipur | Abdul Bari_Capital Refrigeration Raipur | Capital Refrigeration | SOLVE WIRING PROPERLY AND TESTING | Repair |  | 10- Closed | 2023-09-07 12:49 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 145 | INR | 145 | ENM SECURE POWER
WO-11185910 | 103681733 | 2023-08-31 10:44 | 2023-08-31 |  | 2023-08-31 09:16 | GCR_ASCO_S7000 | GCR_ASCO_S7000 | GCR_ASCO_S7000 |  | ASCO Complaint/Bangalore Pls create WO for the complaint. ATS Ref:- A7ACTM031200V5XC; Or pls use GCR_ASCO_S7000 SL no:- 2400618-003WE Under warranty:- Yes Problem:- Phase Sequence error in ATS Customer details:- Elins Switchboards Pvt Ltd; HP Site 65A-1, 3rd Cross, Bommasandra Industrial Area, Aneka Taluk, Bangalore-560099 Mr. Vishwanath/Mr. Abhinandan +91-8431525091 abhinandan@elinsswitchboards.com | 2023-08-31 | 2023-09-01 10:21 | No | Warranty | Elins Switchboards Pvt Ltd | 65A-1 3rd Cross Bommasandra Industrial Area Aneka Taluk | Bangalore | 560099 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Swamy HJ_P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | Visited the site and inspected the A7ACTM031200V5X5 ATS. In ths ATS normal side phase rotation showing ABC. At present condition we can't checked the control wiring due to from customer side shutdown not available | Repair |  | 9- Service Validated | 2023-09-01 10:23 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11316768 | 104307113 | 2023-09-27 17:11 | 2023-09-27 |  | 2023-09-27 14:48 | GCR_ASCO_MV_IEC_01 | GCR_ASCO_MV_IEC_01 | GCR_ASCO_MV_IEC_01 | 2382658-002WE | ASCO Complaint/Delhi Dear CCC Team, Please create WO for the complaint. ATS Ref:- GCR_ASCO_MV_IEC SL No:-2382658-002WE Under Warranty:- Yes Problem:- Few loads are tripping during retransfer Customer details:- YOTTA Infrastructure Solutions LLP Greater Noida West Link Rd, Tusiana Village, Knowledge Park V, Greater Noida, Uttar Pradesh 201306. Mr. Lavkanth lsrivastava@yotta.com 8470803769 | 2023-09-27 | 2023-09-27 17:47 | No | Warranty | YOTTA Infrastructure Solutions LLP | West Link Rd, Tusiana Village, Knowledge Park V | Greater Noida | 201306 | Uttar Pradesh | India FS ED&I CSP North Team Total Solution Services Delhi | Rahul Kumar Total Solution Services Delhi | Total Solution Services(500054203) | We have visit the Site and Checked the 01 NOS ATS. I Observed the ATS in Controlling Issue. | Repair |  | 8- Service Completed | 2023-09-27 18:03 |  |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11175230 |  | 2023-09-30 10:07 | 2023-09-30 |  | 2023-08-28 20:15 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | JK1918001002 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-08-28 | 2023-09-30 18:45 | No | Contract | Reliance Jio Infocomm Ltd | Arkhapur tanda ambedkar nagar null | Tanda | 224190 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Karuna Tripathi Freezeotech Airconditioning & Refrigeration Lucknow | Freezeotech Airconditioning & Refrigeration Corporation | pm done clean the filter condenser unit with jet pump check all parameter unit is working ok | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-30 10:20 |  |  | 206 | INR | 206 | ENM SECURE POWER
WO-11222216 |  | 2023-09-06 21:56 | 2023-09-06 |  | 2023-09-06 18:35 | SURT6000XLI-CC | SURT6000XLI-CC | SURT6000XLI-CC | B21930001607 | Pending Contract P: Battery Installation S: Battery Installation | 2023-09-06 | 2023-09-07 11:15 | No | Commercial Action - Sales | Reliance Trends | Adjacent to ICICI Bank , NH- 24 Faridpur null | Bareilly | 243503 | Uttar Pradesh | India FS North2 HBN CSP JDM Technologies Bareily | Raj kumar_JDM Technologies Pvt. Ltd Bareilly | JDM Technologies - Bareilly - Lucknow | Install battery now ups working ok on both mode. | Commissioning & Installation | Battery Installation | 10- Closed | 2023-09-08 12:40 |  |  | 29 | INR | 29 | ENM SECURE POWER
WO-11316953 | 104301180 | 2023-09-29 15:27 | 2023-09-27 |  | 2023-09-27 15:52 | LC1D65ABBE | LC1D65ABBE | LC1D65ABBE | AA3330120113 | COMPLAINT FOR LC1D65A Dear Sir Please log our complaint for the following and arrange a visit of service engineer . The details of the defective material are: Material Catalog No :LC1D65A Quantity :1 Defect :CONTACTOR NOT WORKING Invoice Number : AA3330120113 Invoice Date :18-8-2023 Customer Name : HPCL IRD MEERUT DEPOT V Address : ILLAGE PUTTA PARTAPUR MEERUT UTTAR PRADESH Contact Person :MR PANKAJ CHOUDHARY 7568150123 Kindly treat the matter as most urgent and awaiting your response. | 2023-09-27 | 2023-09-29 15:30 | No | Warranty | HPCL | Vedvyas Puri Village Poota Partapur Indl Area | Meerut | 250103 | Uttar Pradesh | India FS ED&I CSP North Team Sharma Electric Works Delhi | Pradeep Sharma_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the contactor found coil burnt due wrong supply , Hence no relpacement given to customer. Email : id not provided by customer . | Repair |  | 8- Service Completed | 2023-09-30 12:29 |  |  | 120 | INR | 120 | ENM POWER PRODUCTS
WO-11175260 |  | 2023-09-30 12:42 | 2023-09-30 |  | 2023-08-28 20:19 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | JK1927000797 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-08-28 | 2023-09-30 21:30 | No | Contract | Reliance Jio Infocomm Ltd | Village Sivili Post Shivgarh Tahsil- Maharajganj Dist-Raibarely null | Mahrajganj | 229306 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Karuna Tripathi Freezeotech Airconditioning & Refrigeration Lucknow | Freezeotech Airconditioning & Refrigeration Corporation | pm done clean the filter condenser unit with jet pump check all parameter unit is working ok | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-30 13:06 |  |  | 148 | INR | 148 | ENM SECURE POWER
WO-11222225 | 103828756 | 2023-09-07 12:15 | 2023-09-06 |  | 2023-09-06 18:42 | APC Smart-UPS RT 10000VA 230V Harsh Environment | SURT10000XLI | SURT10000XLI | B21510000490 | FW: RR : IM15443142 ¦ Store Code : 1924 ¦ SCHNEIDER ¦ TELANGANA -TRENDS Under AMC P: UPS BACKUP Issue S:AMC | 2023-09-06 | 2023-09-07 18:04 | No | Contract | Reliance Retail Ltd | Reliance Retail Near Pillar No 118 & 119 MCUBE MALL Attapur Rajendra Nagar | Hyderabad | 500048 | Telangana | India FS South3 HBN CSP CENTRALDATASYSTEMS HYDERABAD | B Ramakrishna CENTRALDATASYSTEMS HYDERABAD | Central Data Systems Pvt Ltd | Checked ups on battery and mains mode no issues found ups All voltages are normal ups working fine | Repair |  | 10- Closed | 2023-09-07 18:06 |  |  | 15 | INR | 15 | ENM SECURE POWER
WO-11187619 | 103685466 | 2023-08-31 12:03 | 2023-08-31 |  | 2023-08-31 11:27 | LC1D32 | LC1D32 | LC1D32 | 1023113 | As per the Sr. no, The Product is in Warranty. Kindly arrange the site visit. Issue: Contactor pole open issue Address Premier concreate pvt ltd plot no 41, pali crusher zone Fridabad 121004 Haryana India Contact person Details: - Mr.Rajnath 9555270602 | 2023-08-31 | 2023-09-01 16:37 | No | Warranty | Premier concreate pvt ltd | plot no 41, pali crusher zone null | Fridabad | 121004 | Haryana | India FS ED&I CSP North Team S D Electric Delhi | Ashish Pokhriyal_S D Electric Delhi | S D Electric (500017662) | We visited the site and checked the 1." LC1D32M7" , 2311 Physical Observation no dust, no damage, no liquid Action taken check one contractor and fault found phase fault Final comment replacement deny due to contractor working ok on customer site Email id - rajnath9555@gmail.com | Repair |  | 9- Service Validated | 2023-09-01 16:50 |  |  | 40 | INR | 40 | ENM POWER PRODUCTS
WO-11222248 | 103829164 | 2023-09-06 21:39 | 2023-09-06 |  | 2023-09-06 18:52 | APC Smart-UPS RT 6000VA 230V No Batteries | SURT6000UXI | SURT6000UXI | IS1142004331 | FW: INC0004316112 // 2505 / BANKURA HDFC Bank P: Chargeable basis case logged for 1time UPS checking (mention serial number of AC/UPS) No Spares support APC will Pay the charges S: Chargeable basis case logged for 1time UPS checking : (mention serial number of AC/UPS) | 2023-09-06 | 2023-09-07 16:09 | No | Commercial Action - Sales | HDFC Bank Ltd | HDFC Bank Kajuri Danga Near Electicity Sub Station PO Kendutihi Bankura | Bankura | 722102 | West Bengal | India FS East HBN CSP Computer Care Asansol | Sanjay Prasad_Computer Care Asansol | COMPUTER CARE | UPS not checked as all batteries are deep discharged.Advice to replace all batteries first. | Repair |  | 10- Closed | 2023-09-07 16:14 |  | service for 1 time visit | 105 | INR | 105 | ENM SECURE POWER
WO-11322039 | 104307912 | 2023-09-28 15:12 | 2023-09-28 |  | 2023-09-28 12:49 | LRE08 | LRE08 | LRE08 |  | Plz Book Complaint Rema Engineers As Per The Invoice The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- REMA ENGINEERS Plot No.5221, Phase -4, Vatva GIDC,Ramol Char Rasta,Vatva Ahmedabad 382445 Gujarat India Contact Person Details:- Contact person Name :- Suresh Thakor Contact Person Mobile No :- +91 9904041116 Product and Issue:- MODEL ? LC1E0901M7 :- 1 NOS LRE08 :- 1 NOS Problem Observed :- Phase Problems | 2023-09-28 | 2023-09-30 10:43 | No | Warranty | REMA ENGINEERS | Plot No.5221, Phase -4, Vatva GIDC,Ramol Char Rasta,Vatva | Ahmedabad | 382445 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Nijesh Patel_Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked product found physically observed ok. LRE08 SR NO : 8C23044 But nc no not working. underwarranty status so free replacemnet. LC1E0901M7 SR NO : 1023323 ok but l1 pole open . underwarranty status free replacment. | Repair |  | 8- Service Completed | 2023-09-30 10:43 | =S= Consig Fill up 226097877 |  | 10 | INR | 10 | ENM POWER PRODUCTS
WO-11322089 | 104302862 | 2023-09-29 14:54 | 2023-09-28 | ACB Rack in & Rack out issue | 2023-09-28 13:08 | MVS10N4NW6L | MVS10N4NW6L | MVS10N4NW6L |  | ACB complaint. MVS10N4EW6L rack in and rack out operation issue Site Address: Control Tech Gat. No. 803 -804, At Post Velu, Tal Bhor, Dist. Pune.- PIN : 412205, India. Contact person: Mr.Girish (9011032104) | 2023-09-28 | 2023-09-30 15:34 | No | Warranty | CONTROL TECH | Gat No. 803 & 804, At-Post Velu, Tal-Bhor | Pune | 412205 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Samadhan S_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the ACB Rack in & Rack out issue. right side rail not getting comes out, then we make rail grove make a problem to rail for out. main shaft from dislocated so we make it proper and put the block on rail and then taken operation of ACB found ok., after making shaft proper problem is resolved. | Repair |  | 8- Service Completed | 2023-09-30 15:40 |  |  | 60 | INR | 60 | ENM POWER PRODUCTS
WO-11224431 | 103847888 | 2023-09-07 12:03 | 2023-09-07 |  | 2023-09-07 11:32 | SURTD5000XLI-CC | SURTD5000XLI-CC | SURTD5000XLI-CC | B22125041586 | FW: RR : IM15433547 ¦ Store Code : TJW9 ¦ SCHNEIDER ¦ DELHI -DIGITAL In-warranty P: UPS not working S:Onsite | 2023-09-07 | 2023-09-07 14:00 | No | Warranty | CDIT Reliance Limited | D11, NDSE Part 11,South Ex, | New Delhi | 110049 | Delhi | India FS North1 HBN CSP HITEK BUSINESS SYSTEMS PVT LTD Delhi | Brajesh B_Hitek Business Systems New Delhi | Hitek Business Systems Pvt Ltd | Engineer this site visit UPS check found UPS working ok input wiring fault | Repair |  | 10- Closed | 2023-09-08 16:01 |  |  | 15 | INR | 15 | ENM SECURE POWER
WO-11224465 |  | 2023-09-07 12:56 | 2023-09-07 |  | 2023-09-07 11:50 | SURT6000XLI-CC | SURT6000XLI-CC | SURT6000XLI-CC | B21943005475 | FW: RR : IM15230699¦ Store Code:TBA9 ¦ SCHNEIDER ¦ KERALA ¦ TRENDS under amc P: Battery Installation S:Battery Installation | 2023-09-07 | 2023-09-08 17:27 | No | Commercial Action - Sales | Reliance Retail Limited | RRL TST Kanjirapally, NEAR TO AKKARAPPALLY, K E Rd KANJIRAPPALLY null | KANJIRAPPALLY | 686507 | Kerala | India FS South2 HBN CSP AutopowerSystems&Solutions Kochi | NISHANTH GOPI AutopowerSystems&Solutions Kochi | AUTOPOWER SYSTEMS & SERVICES | battery replacement done | Commissioning & Installation | Battery Installation | 10- Closed | 2023-09-08 17:37 |  |  | 86 | INR | 86 | ENM SECURE POWER
WO-11327101 | 104358294 | 2023-09-29 12:45 | 2023-09-29 | NA | 2023-09-29 12:10 | LV563650 | LV563650 | LV563650 |  | CVS MCCB Nuisance Tripping at M/s. Power & Protection As Per The Invoice copy The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Power & Protection Santragachi, Brojonath Lahiri Lane Howrah 711104 West Bengal India Contact Person Details:- Contact Person: Mr. Subrata Das (+91 9231627155) Product and Issue:- LV563650 CVS MCCB (Reference: LV563650 ? Qty. 1 no.) is having nuisance tripping issue. | 2023-09-29 | 2023-09-30 16:30 | No | Warranty | Power & Protection | Santragachi, Brojonath Lahiri Lane null | Howrah | 711104 | West Bengal | India FS ED&I CSP East Team B.D Electroservices Kolkata | RAHUL RAY_B.D Electroservices Kolkata | B.D Electroservices(500017330) | Visited site and we fitted 1 no motor mechanism and checked its working properly. | Repair |  | 8- Service Completed | 2023-09-30 11:58 |  |  | 24 | INR | 24 | ENM POWER PRODUCTS
WO-11224508 | 103849182 | 2023-09-07 18:35 | 2023-09-07 |  | 2023-09-07 12:14 | SURT6000XLI-CC | SURT6000XLI-CC | SURT6000XLI-CC | B21628000070 | FW: RR : IM15444848 ¦ Store Code : 2991 ¦ SCHNEIDER ¦ ODISHA -FRESH Under AMC P: UPS not working S:AMC | 2023-09-07 | 2023-09-07 17:40 | No | Contract | Reliance Fresh Ltd | Plot 756 Khata 344, Mouza - Cuttack Sahar Unit No.28, P.S Chauliaganj Nayabazar | Cuttack | 753004 | Odisha | India FS East HBN CSP Disha Computers Bhubneshwar | TARUN PARIDA_Disha Computers Bhubneshwar | Disha Computers-Bhubaneshwar | Checked the UPS found the dedicated earth not connected in isolation transformer so the N-E High voltage in UPS out put, after connecting earth UPS showing proper voltage | Repair |  | 10- Closed | 2023-09-08 08:44 |  |  | 30 | INR | 30 | ENM SECURE POWER
WO-11188065 | 103689971 | 2023-08-31 15:30 | 2023-08-31 | NA | 2023-08-31 14:39 | LC1D25M7 | LC1D25M7 | LC1D25M7 |  | COMPLAINT - SR INDUSTRIES--31.08.2023 Name of Customer S R INDUSTRIES Site Address Unit No 215/203/204,Globe Estate,Plot No C-9,Vikas Naka,New kalyan Road,near Tata Power,Dombivli MIDC phase 1,Dombivli east Thane 421203. EMAIL ID srindustries77@rediffmail.com Contact Phone / Mob. No: Sunil Naravade / 9004960595 Defective product details & Invoice details LC1D25M7 LC1D09M7 LC1D09F7 LC1D18F7 LC1D09F7 LC1D12F7 LC1D18M7 LC1D12F7 LC1D12M7 Nature of Defect SCROW PROBLEM SCROW PROBLEM COIL PROBLEM COIL PROBLEM NC CONTACT PROBLEM SCROW PROBLEM NO CONTACT PROBLEM COIL PROBLEM NO CONTACT PROBLEM Shutdown availability if applicable Applicable Warranty status YES Commissioned / Installed date Invoice no 9008598262 Dtd.12.06.2023 9008616503 Dtd.24.06.2023 9008598256 Dtd.12.06.2023 9008596974 Dtd 10.09.2023 | 2023-08-31 | 2023-09-01 13:34 | No | Warranty | SR Industries | Unit No 215,Globe Estate near Vikas Naka,Dombivli MIDC Phase 1,Dombivli East | Thane | 421203 | Maharashtra | India FS ED&I CSP West Team East India Power Engineers Mumbai | Sandeep Ingavale East India Power engineers Mumbai | East India Power Engineers (5043) | Visited the site and checked the Contactor by giving supply found ok. Checked the 03 nos contactor coil burnout condition. Hence the 03 nos Contactor not converted in warranty. Checked the 03 nos contactor terminal screw faulty. Hence the 03 nos contactor needs to be replace with new one | Repair |  | 8- Service Completed | 2023-09-05 14:32 | =S= Consig Fill up 226018556 |  | 22 | INR | 22 | ENM POWER PRODUCTS
WO-11327370 | 104358947 | 2023-09-29 16:29 | 2023-09-29 |  | 2023-09-29 14:08 | CAE40M5 | CAE40M5 | CAE40M5 | XA2EVM6LC | Company name - Richa Processing Mill Pvt. Ltd. Address - I-16, Phase 1, DLF Industrial Area, Faridabad-121003, Haryana Contact person - Ajay Contact No. 8810950646 Product - CAE40M5 Invoice no - 9008593260 Qty - 1 Issue - Not Working Product - XA2EVM6LC Invoice no - 9008654654 | 2023-09-29 | 2023-09-29 18:42 | No | Warranty | Richa Processing Mill Pvt Ltd | 16, DLF Industrial Area,, Phase-I,, Faridabad, Haryana | Faridabad | 121003 | Haryana | India FS ED&I CSP North Team S D Electric Delhi | Arif Raza S D Electric Delhi | S D Electric (500017662) | We visited the site and checked the 1.CAE40M5 , 1223215 Physical Observation no dust, no damage, no liquid Action taken check one contractor and fault found Coil bunrt Final comment replacement rejected due to coil burnt. Email id -safiboy6797@gmail.com | Repair |  | 8- Service Completed | 2023-09-29 18:47 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11188203 | 103594842 | 2023-08-31 17:04 | 2023-08-31 |  | 2023-08-31 15:50 | GCR_NSX | GCR_NSX | GCR_NSX |  | As per the invoice, The Product(MOtor mechanism) is in Warranty. Kindly arrange the site visit. Issue: MOtor mechanism is not working Address Akshaya Aura #6, kalidasa Marg (1st Main road) Gandhi Nagar Bangalore 560009 Karnataka India Contact person Details: - Mr.Aaradhya 9620146434 | 2023-08-31 | 2023-09-01 16:57 | No | Warranty | Akshaya Aura | #6, kalidasa Marg (1st Main road) Gandhi Nagar null | Bangalore | 560009 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Nagaraja G_P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | Visited the site and inspected the MT 400/630 motor mechanism. Along with motor mechanism MCCB not getting On. Due to motor mechanism storage spring was opened. Hence same rectified the problem and tested MCCB with motor mechanism working found ok. | Repair |  | 9- Service Validated | 2023-09-01 16:59 |  |  | 9 | INR | 9 | ENM POWER PRODUCTS
WO-11188453 | 103687266 | 2023-09-01 09:59 | 2023-08-31 |  | 2023-08-31 17:37 | MS13AC12N5 | MS13AC12N5 | MS13AC12N5 |  | As per the invoice, The Product(MOtor mechanism) is in Warranty. Kindly arrange the site visit. Issue:startor is not working Address Residence 4-29,Ravada Village perika veedhi Street bhogapuram mandal vizianagaram VISAKHAPATNAM 531162 Andhra Pradesh India Contact person Details: - Mr.Mahesh 9398325811 | 2023-08-31 | 2023-09-08 14:46 | No | Warranty | Residence | 4-29,Ravada Village perika veedhi Street bhogapuram mandal vizianagaram null | VISAKHAPATNAM | 531162 | Andhra Pradesh | India FS ED&I CSP South Team Voltamp Electrical Works Visakhapatnam | Vydha Venkatesh_VOLT AMP ELECTRICAL WORKS Visakhapatnam | Voltamp Electrical Works | as per the complaint visited the site chicking 415V DOL starter is not working so we are observed the problem dol starter mechanical on/off problem so we are observed RM22TR33 3 Phase Voltage control relay is not working so we are zvo material replaced so testing ok closed the issue | Repair |  | 9- Service Validated | 2023-09-08 14:48 |  |  | 60 | INR | 60 | ENM POWER PRODUCTS
WO-11332697 | 104368236 | 2023-09-30 11:10 | 2023-09-30 |  | 2023-09-30 10:56 | LC1D32M7 | LC1D32M7 | LC1D32M7 | 8B2312 | contactor problem LC1D32M7 - 8B2312 pole continuity issue Site Address: bajrang electric house . Lalitpur road jhansi up. Pin code - 284403 contact person - Mr. Anubhav singh contact no . - 8896447899 | 2023-09-30 | 2023-09-30 12:40 | No | Warranty | BAJRANG ELECTRIC HOUSE | 497\1, Rawatyana, Jhansi null | Lalitpur | 284403 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Abhishek Patel Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found contactor having pole open issue. | Repair |  | 8- Service Completed | 2023-09-30 12:43 |  |  | 430 | INR | 430 | ENM POWER PRODUCTS
WO-11191449 | 103693700 | 2023-09-01 12:30 | 2023-09-01 |  | 2023-09-01 10:16 | LC1D09BD | LC1D09BD | LC1D09BD | 1023231 | As per the Sr. no, The Product is in Warranty. Kindly arrange the site visit. Issue: Contactor pole open issue Address Jay Khodiyar Control System Sukhsagar Complex 102,First Floor Nehrunagar,Main Road 80 Feet Road Rajkot 360002 Gujarat India Contact person Details: - Mr.jitinder 9227551251 | 2023-09-01 | 2023-09-02 16:45 | No | Warranty | Jay Khodiyar Control System | Sukhsagar Complex 102,First Floor Nehrunagar,Main Road 80 Feet Road | Rajkot | 360002 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | RAHUL PARMAR JKS Rajkot | JKS Engineering Co. | We visited at site check LA1E0910 contactor terminals and body side not any damages check contactor coil open found 1nos coil replacement check LC1D09BDL contactor on/off not working 24v supply but contactor not working in side check diode side problem 1nos diode replacement | Repair |  | 9- Service Validated | 2023-09-02 17:30 | =S= Consig Fill up 226014277 |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11224643 | 103850767 | 2023-09-07 14:02 | 2023-09-07 |  | 2023-09-07 12:56 | Leonardo EV,DX,R22,EC Fan,TDAV0811A,Downflow Without Heater & Humidifier | TDAV0811AN001 | TDAV0811AN001 | ZK1330020317 | P:zk1330020317---LP Alarm Under AMC P:LP Alarm S:AMC | 2023-09-07 | 2023-09-08 17:18 | No | Contract | Reliance Jio Infocomm Ltd. | Reliance Jio Infocomm Ltd 17,18 Plot No 5 Block DP Tower II Godrej Waterside Sector V P S Electronics Complex Salt lake City | Kolkata | 700091 | West Bengal | India FS East Cooling CSP Snow Point Kolkata | Laxmikant Dhang_Snow Point Kolkata | Snow Point | OIL SEPARATER EQUILIZER PIPE LEAKAGE.OIL SEPARATER EQUILIZER PIPE LEAKAGE REPAIRING DONE.VACUUM.12KG R22 GAS CHARGE.ALL PARAMETER CHECKED.MACHINE OK RUNNING. | Repair |  | 10- Closed | 2023-09-08 17:25 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 30 | INR | 30 | ENM SECURE POWER
WO-11333495 | 104383038 | 2023-09-30 17:57 | 2023-09-30 |  | 2023-09-30 17:23 | GCR_ASCO_S7000 | GCR_ASCO_S7000 | GCR_ASCO_S7000 | 2506276-004RE | Dear CCC Team, Please create the WO for the complaint. ATS Ref:- J7ACTSB30150K500; Pls use GCR_ASCO_S7000 if part ref not available. SL No:- 2506276-004RE Under warranty:- Yes Problem:- ATS inhibit error in Controller display. Customer details:- Switchgear & Control Technics Private Limited Bommasandra Industrial Area, Hosur Road, Anekal Taluk, Bengaluru, Karnataka-560099 Akash - +91 8892424628 akashsimpi@switchgear.in | 2023-09-30 | 2023-09-30 18:46 | No | Warranty | Switchgear and Control Technics Pvt.Ltd. | 152, Bommasandra Ind Area, Hosur Road, Anekal Taluk, | Bangalore | 560099 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Swamy HJ_P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | Visited the site and inspected the J7ACTSB30150K500 ATS. And this ATS not getting transfer and also in controller display showing is XFER TO NORMAL INHIBIT. Due to DOC control wiring connection was wrong. Hence same as rectified the problem and explain to customer how to connect the connection and tested ATS transfer and re-transfer working found normal. | Repair |  | 8- Service Completed | 2023-09-30 18:47 |  |  | 45 | INR | 45 | ENM POWER PRODUCTS
WO-11224679 | 103851522 | 2023-09-07 14:36 | 2023-09-07 |  | 2023-09-07 13:17 | APC Easy UPS Online 6000VA Indian Outlet Rackmount 230V India | SRV6KL-IN | SRV6KL-IN | 9S2023A67858 | FW: [External]RE: RR : IM15444391 ¦ Store Code : U549 ¦ SCHNEIDER ¦ KARNATAKA -SMART POINT IN-WARRANTY P: UPS not working S:Onsite | 2023-09-07 | 2023-09-07 18:25 | No | Warranty | Reliance Retail Limited | Mariyappanapalya Bangalore,Gf 202 F J Complex St James Church R,Oad Mariyappanapalya,H A Farms Post null | Bangalore | 560024 | Karnataka | India FS South1 HBN CSP UBM Autopower Pvt. Ltd Bangalore | Praveen Kumar UBM Autopower Pvt. Ltd Bangalore | Autopower systems and solutions | We received call on Thu - 7th Sep, 1:17 PM only, Onsite Date: 7th Sep. Checked the ups found in bypass mode switch to online mode & all parameters working fine, UPS working normal. | Repair |  | 10- Closed | 2023-09-08 12:01 |  |  | 10 | INR | 10 | ENM SECURE POWER
WO-11195105 | 103720397 | 2023-09-02 11:45 | 2023-09-02 |  | 2023-09-01 16:05 | METSEEM6436HCL10RS | METSEEM6436HCL10RS | METSEEM6436HCL10RS |  | As per the invoice, The Product is in Warranty. Kindly arrange the site visit. Issue: One phase sensing issue Address UNIVERSAL POWER EQUIPMENT PVT LTD Plot No:18,Industrial Area , CMDA Industrial Complex Maraimalai Nagar Chennai 603209 Tamil Nadu India Contact person Details: - Mr.Ashraf 8056010612 | 2023-09-01 | 2023-09-05 18:00 | No | Warranty | UNIVERSAL POWER EQUIPMENT PVT LTD | Plot No:18,Industrial Area , CMDA Industrial Complex Maraimalai Nagar null | Chennai | 603209 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Site Visit Done | Repair |  | 9- Service Validated | 2023-09-06 13:36 | Hi Team, Material booked zfre Zvo : 226007651 |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11178264 |  | 2023-09-30 13:10 | 2023-09-30 |  | 2023-08-29 11:36 | EFC 0.8TR, Downflow, Bottom Discharge | WDF0101BN001 | WDF0101BN001 | JK1341002970 | Preventive Maintenance/Regular Preventive Maintenance | 2023-08-29 | 2023-09-30 21:30 | No | Contract | Reliance Corporate It Park Limited | S/O Sh Thakur Prasad null | Hassanganj | 754250 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Karuna Tripathi Freezeotech Airconditioning & Refrigeration Lucknow | Freezeotech Airconditioning & Refrigeration Corporation | pm done clean the filter condenser unit with jet pump check all parameter unit is working ok | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-30 13:17 |  |  | 148 | INR | 148 | ENM SECURE POWER
WO-11195130 | 103726803 | 2023-09-04 14:12 | 2023-09-01 |  | 2023-09-01 16:27 | LC1E0910M7 | LC1E0910M7 | LC1E0910M7 | 1022162 | As per the Sr. no, The Product is in Warranty. Kindly arrange the site visit. Issue: contactor stuck issue Address DR Control Systems 33 Feet Road Faridabad Sector 23 Faridabad 121005 Haryana India Contact person Details: - Mr.Nazin 8882759688 | 2023-09-01 | 2023-09-11 15:48 | No | Warranty | DR Control Systems | 33 Feet Road Faridabad Sector 23 | Faridabad | 121005 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | checked the contactor found out put not showing and mcb found dolly free. Hence faulty, replaced. LC1E1810M7 - 1 Nos. A9N3P40C - 1 Nos. Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-12 13:51 |  |  | 45 | INR | 45 | ENM POWER PRODUCTS
WO-11195203 | 103726898 | 2023-09-01 17:23 | 2023-09-01 | MCCB Damaged & Shunt coil not operating | 2023-09-01 16:56 | EZC100H4100 | EZC100H4100 | EZC100H4100 |  | Pl issue complaint no. Name of Customer: Datson electronics Pvt. Ltd. 2. Site Address: - Gat No. 30, Sinhagad Road, Gorhe Budruk, Tal- Haveli Next to Savali Resort Pune 411025. 3. Name of contact person at site :-Patil Sir 4. Contact Phone / Mob. No: - 9922950382 5. Defective product details:-,Ref no- EZC100H4100 6. Product Make:-Schneider Electric 7. Nature of Defect: MCCB Damaged & Shunt coil not operating 8. Shutdown availability if applicable :nil 9. Serial No: or DOM of the product- TH-2022-W07-2 | 2023-09-01 | 2023-09-01 17:26 | No | Warranty | Datsons Electronics Pvt Ltd | Gat No 30 Sinhagad Road Gorhe Budruk, Tal Haveli | Pune | 411025 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Amit Patil_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the MCCB Damaged & Shunt coil not operating. observed neutral pole damaged . so we reject the warranty. also checked shunt coil found that the metal part of coil operating mechanism is damaged. Due to damaged of product warranty is avoided. | Repair |  | 9- Service Validated | 2023-09-01 17:34 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11224818 |  | 2023-09-12 13:23 | 2023-09-12 |  | 2023-09-07 14:22 | HXCVQ | HXCVQ | HXCVQ | JK2246000878 | pm | 2023-09-07 | 2023-09-21 09:49 | No | Commercial Action - Service Ops | Yotta Infrastructure | PLOT NO 7, SECTOR KNOWLEDGE PARK V Tusiana Village, Gautam Buddha Nagar null | Greater Noida | 201301 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Bilal Mansuri Freezeotech Airconditioning & Refrigeration GZB | Freezeotech Airconditioning & Refrigeration Corporation | PREVENTIVE MAINTENANCE DONE. CLEAN FILTERS,EVAPORATING & CONDESING COILS, WATER TRAY, DRAIN PIPE. CHECK ALL PARAMETRE UNIT IS WORKING OK. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-22 15:25 |  |  | 28 | INR | 28 | ENM SECURE POWER
WO-11195276 | 103723941 | 2023-09-02 10:40 | 2023-09-01 |  | 2023-09-01 17:42 | CA2KN22M7 | CA2KN22M7 | CA2KN22M7 |  | As per the invoice, The Product is in Warranty. Kindly arrange the site visit. Issue: contactor is not getting on Address POWERGRID CORPORATION OF INDIA LIMITED 765/400kV GIS SS MITTAPALLY VIL, DICHPALLY MANDAL. NIZAMABAD 503001 Telangana India Contact person Details: - Mr. Udaysai 6361217245 | 2023-09-01 | 2023-09-05 12:00 | No | Warranty | POWERGRID CORPORATION OF INDIA LIMITED | 765/400kV GIS SS MITTAPALLY VIL, DICHPALLY MANDAL. null | NIZAMABAD | 503001 | Telangana | India FS ED&I CSP South Team Sumanth Electrical Services Hyderabad | Basanth Reddy_SUMANTH ELECTRICAL SERVICES HYDERABAD | Sumanth Electrical Services | Self Visited PGCIL Site and Inspected Schneider Electric CA2KN22M7 Auxiliary Contactor we have replaced with new CA2KN22M7 and faulty collected back to ASC For RTS and complaint is closed | Repair |  | 9- Service Validated | 2023-09-05 15:27 |  |  | 160 | INR | 160 | ENM POWER PRODUCTS
WO-11178426 |  | 2023-09-15 11:12 | 2023-09-02 |  | 2023-08-29 12:33 | TDAVQ | TDAVQ | TDAVQ | C21923003658 | PM | 2023-08-29 | 2023-08-28 17:24 | No | Contract | Army commanding Office | Army commanding Office Signal null | KARGIL | 194102 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-18 17:33 |  |  | 430 | INR | 430 | ENM SECURE POWER
WO-11224819 |  | 2023-09-12 13:24 | 2023-09-12 |  | 2023-09-07 14:23 | HXCVQ | HXCVQ | HXCVQ | JK2246002310 | pm | 2023-09-07 | 2023-09-21 15:26 | No | Commercial Action - Service Ops | Yotta Infrastructure | PLOT NO 7, SECTOR KNOWLEDGE PARK V Tusiana Village, Gautam Buddha Nagar null | Greater Noida | 201301 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Bilal Mansuri Freezeotech Airconditioning & Refrigeration GZB | Freezeotech Airconditioning & Refrigeration Corporation | PREVENTIVE MAINTENANCE DONE. CLEAN FILTERS,EVAPORATING & CONDESING COILS, WATER TRAY, DRAIN PIPE. CHECK ALL PARAMETRE UNIT IS WORKING OK. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-22 15:31 |  |  | 28 | INR | 28 | ENM SECURE POWER
WO-11178428 |  | 2023-09-15 11:14 | 2023-09-02 |  | 2023-08-29 12:33 | TDAVQ | TDAVQ | TDAVQ | C21923003451 | PM | 2023-08-29 | 2023-09-08 17:55 | No | Contract | Army commanding Office | Army commanding Office Signal null | KARGIL | 194102 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-21 17:58 |  |  | 860 | INR | 860 | ENM SECURE POWER
WO-11224826 |  | 2023-09-12 13:29 | 2023-09-12 |  | 2023-09-07 14:23 | HXCVQ | HXCVQ | HXCVQ | JK2245010334 | pm | 2023-09-07 | 2023-09-22 18:16 | No | Commercial Action - Service Ops | Yotta Infrastructure | PLOT NO 7, SECTOR KNOWLEDGE PARK V Tusiana Village, Gautam Buddha Nagar null | Greater Noida | 201301 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Bilal Mansuri Freezeotech Airconditioning & Refrigeration GZB | Freezeotech Airconditioning & Refrigeration Corporation | PREVENTIVE MAINTENANCE DONE. CLEAN FILTERS,EVAPORATING & CONDESING COILS, WATER TRAY, DRAIN PIPE. CHECK ALL PARAMETRE UNIT IS WORKING OK. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-22 18:21 |  |  | 28 | INR | 28 | ENM SECURE POWER
WO-11199062 | 103720442 | 2023-09-02 11:20 | 2023-09-02 |  | 2023-09-02 09:47 | C25N3MA220 | C25N3MA220 | C25N3MA220 |  | As per the invoice, The Product is in Warranty. Kindly arrange the site visit. Issue: pole open issue Address PATEL AGRI INDUSTRIES PVT LTD VILLAGE ARAWAN, BLOCK BEN, DIST. NALANDA, NALANDA 803114 Bihar India Contact person Details: - Mr. Himanshu 9118553846 | 2023-09-02 | 2023-09-11 19:24 | No | Warranty | M/s PATEL AGRI INDUSTRIES PVT LTD | VILLAGE ARAWAN, BLOCK BEN, DIST. NALANDA, null | NALANDA | 803114 | Bihar | India FS ED&I CSP East Team Vidya Enterprises Lucknow | Rana Ranjan_Vidya Enterprises Lucknow | Vidya Enterprises | As per customer complaint visited the site and check the MCCB found R Phase pole open. Replace the C25N3MA220 MCCB from Schneider service stock. MCCB replace in panel by customer at the time of shutdown. Engineer handover the material to customer and faulty material is collected. faulty material serial no. 2KCD0091166 and new Serial no. 7DHS0154521 | Repair |  | 9- Service Validated | 2023-09-11 19:24 | =S= Consig Fill up226025316 ( Two work order WO-11199062 number having same OA # 226025316 ) =S= Free Order 226025179 has been saved |  | 60 | INR | 60 | ENM POWER PRODUCTS
WO-11178439 |  | 2023-09-15 11:54 | 2023-09-02 |  | 2023-08-29 12:34 | TDAVQ | TDAVQ | TDAVQ | C21935000947 | PM | 2023-08-29 | 2023-08-31 16:11 | No | Contract | Army commanding Office | Army commanding Office Signal null | LEH | 194101 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-20 13:14 |  |  | 870 | INR | 870 | ENM SECURE POWER
WO-11224821 |  | 2023-09-12 13:25 | 2023-09-12 |  | 2023-09-07 14:23 | PRODUCT UNIFLAIR LEONARDO CHW DOWNFLOW HXCV6200A WITHOUT H VER WITH DUAL SPLY AN | HXCVQ | HXCVQ | JK2243003718 | pm | 2023-09-07 | 2023-09-22 17:58 | No | Commercial Action - Service Ops | Yotta Infrastructure | PLOT NO 7, SECTOR KNOWLEDGE PARK V Tusiana Village, Gautam Buddha Nagar null | Greater Noida | 201301 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Bilal Mansuri Freezeotech Airconditioning & Refrigeration GZB | Freezeotech Airconditioning & Refrigeration Corporation | PREVENTIVE MAINTENANCE DONE. CLEAN FILTERS,EVAPORATING & CONDESING COILS, WATER TRAY, DRAIN PIPE. CHECK ALL PARAMETRE UNIT IS WORKING OK. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-22 18:03 |  |  | 28 | INR | 28 | ENM SECURE POWER
WO-11199073 | 103740758 | 2023-09-02 11:10 | 2023-09-02 |  | 2023-09-02 10:00 | LC1E0910M7 | LC1E0910M7 | LC1E0910M7 |  | LC1E0910M7 09 Amps Sr No. 10-23017 , Jan 23 Problem: Not getting ON / Coil Open LC1E0910M7 09 Amps Sr No. 10-23017 , Jan 23 Problem: Not getting ON / Coil Open Bala Shree Industries E-607-608, E.P.I.P. BORANADA,JODHPUR 342004 Mr. RAM 7888606910 saielecthouse@gmail.com | 2023-09-02 | 2023-09-02 11:19 | No | Warranty | Bala Shree Industries | E-607-608, E.P.I.P. BORANADA | JODHPUR | 342004 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Amarjeet Singh Sharma Electric Jaipur | Sharma Electric Works | Checked the contactor found phase missing and mccb found phase missing, Hence faulty replaced. LC1E0910M7 - 1 nos EZC630H4600N - 1 nos Email : saielecthouse@gmail.com | Repair |  | 9- Service Validated | 2023-09-02 13:13 |  |  | 338 | INR | 338 | ENM POWER PRODUCTS
WO-11178427 |  | 2023-09-15 11:13 | 2023-09-02 |  | 2023-08-29 12:33 | TDAVQ | TDAVQ | TDAVQ | C21923003659 | PM | 2023-08-29 | 2023-08-28 17:37 | No | Contract | Army commanding Office | Army commanding Office Signal null | KARGIL | 194102 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-18 17:40 |  |  | 430 | INR | 430 | ENM SECURE POWER
WO-11224822 |  | 2023-09-12 13:27 | 2023-09-12 |  | 2023-09-07 14:23 | PRODUCT UNIFLAIR LEONARDO CHW DOWNFLOW HXCV6200A WITHOUT H VER WITH DUAL SPLY AN | HXCVQ | HXCVQ | JK2243004770 | pm | 2023-09-07 | 2023-09-22 18:04 | No | Commercial Action - Service Ops | Yotta Infrastructure | PLOT NO 7, SECTOR KNOWLEDGE PARK V Tusiana Village, Gautam Buddha Nagar null | Greater Noida | 201301 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Bilal Mansuri Freezeotech Airconditioning & Refrigeration GZB | Freezeotech Airconditioning & Refrigeration Corporation | PREVENTIVE MAINTENANCE DONE. CLEAN FILTERS,EVAPORATING & CONDESING COILS, WATER TRAY, DRAIN PIPE. CHECK ALL PARAMETRE UNIT IS WORKING OK. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-22 18:08 |  |  | 28 | INR | 28 | ENM SECURE POWER
WO-11199074 | 103740696 | 2023-09-02 11:07 | 2023-09-02 |  | 2023-09-02 10:01 | INA_NWDOU4 | INA_NWDOU4 | INA_NWDOU4 |  | 1 Company Name & Complete Address with pin code - Where product is installed TN India pvt. Ltd. 92/2,87/2, 90/2/1, Sr. no. 87,1 90/1/1, 90/2/2, 90/3.Near ITI Bhilad - 396105 2 Contact Person at Site : Name & Mobile No. Mr. Sandip bhandari Alternate Mobile No : 9824470821 3 Contact Person at Site - Email Address** pcvapi@gmail.com 4 Defective Product Model/Part No (Pls refer FAQ sheet ) INA_NWD0U4 5 Nature of Defect* - Defects Video and Photographs ATS mcb tripping 6 Shutdown availability if applicable Yes 7 POP - SE Authorised Partner Invoice soft copy na 8 Photograph of product where Serial No/Batch Code or Date of Manufacturing printed - Please refer FAQ sheet 3N-2023-W04-4 230440086 | 2023-09-02 | 2023-09-08 13:01 | No | Warranty | TN India pvt. Ltd | 92/2,87/2, 90/2/1, Sr. no. 87,1 90/1/1, 90/2/2, 90/3.Near ITI Bhilad null | Valsad | 396105 | Gujarat | India FS ED&I CSP West Team SHIV SAI ELECTRICALS Vapi | SHIVAM LAD SHIV SAI ELECTRICALS VAPI | shivsai electricals | WE FOUND REPORTED ATS ACP PLATE LIVE MODULE IS PHYSICALLY OK ON VISUAL INSPECTION.IT IS USED IN 4000A MVS 4PEDO PANEL FOR CHANGEOVER OF SOURCE WE EVEN SEPRATE MOTOR SUPPLY & COIL SUPPLY BUT ISSUE NOT RESOLVED.TAKE ALL PHOTOS OF INSTALLATION &WE WILL ESCALATE THE CASE TO EXPORT. | Repair |  | 9- Service Validated | 2023-09-17 07:57 |  |  | 13 | INR | 13 | ENM POWER PRODUCTS
WO-11178430 |  | 2023-09-15 11:18 | 2023-09-02 |  | 2023-08-29 12:33 | TDAVQ | TDAVQ | TDAVQ | C21922004238 | PM | 2023-08-29 | 2023-09-07 16:14 | No | Contract | Army commanding Office | Army commanding Office Signal null | LEH | 194101 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-20 14:22 |  |  | 710 | INR | 710 | ENM SECURE POWER
WO-11178433 |  | 2023-09-15 11:23 | 2023-09-02 |  | 2023-08-29 12:33 | TDAVQ | TDAVQ | TDAVQ | C21922009711 | PM | 2023-08-29 | 2023-09-07 13:04 | No | Contract | Army commanding Office | Army commanding Office Signal null | KHALSI | 190004 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-20 14:07 |  |  | 640 | INR | 640 | ENM SECURE POWER
WO-11200654 | 103741654 | 2023-09-02 15:27 | 2023-09-02 | Contactor not working | 2023-09-02 14:08 | LC1E40004M5WB | LC1E40004M5WB | LC1E40004M5WB |  | Pl issue complaint no 1. Name of Customer: Sonigara Landmark 2. Site Address: - Sonigara Landmark, Office 313, 3rd Floor Near, Chatrapati Chowk Rd, Wakad, Pune, Maharashtra 411057 3. Name of contact person at site :- Mr.DNYANESHWAR AHER 4. Contact Phone / Mob. No: -70305 61807 5. Defective product details:- LC1E40004M5 6. Product Make:-Schneider Electric 7. Nature of Defect: VDP not showing indication 8. Shutdown availability if applicable :nil 9. Serial No: or DOM of - 8C22045 | 2023-09-02 | 2023-09-02 16:05 | No | Warranty | Sonigara Landmark | Office 313, 3rd Floor Near, Chatrapati Chowk Rd, Wakad, | Pune | 411057 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Amit Patil_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the Contactor not working. we installed the contactor after installing DG contactor not on mseb fail. we observed their old contactor. so we old contactor normally free & operate in some operation. and also shown customer new and old contactor are found ok. | Repair |  | 9- Service Validated | 2023-09-02 16:19 |  |  | 45 | INR | 45 | ENM POWER PRODUCTS
WO-11178437 |  | 2023-09-15 11:51 | 2023-09-02 |  | 2023-08-29 12:34 | TDAVQ | TDAVQ | TDAVQ | C21926003958 | PM | 2023-08-29 | 2023-08-29 17:49 | No | Contract | Army commanding Office | Army commanding Office Signal null | KARGIL | 194103 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-18 17:52 |  |  | 490 | INR | 490 | ENM SECURE POWER
WO-11224871 | 103853691 | 2023-09-07 15:43 | 2023-09-07 |  | 2023-09-07 14:37 | LEONARDO EV,DX,R22,EC FAN,( HCM109-DANFOSS ), DOWNFLOW WITHOUT HEATER & HUMIDIFI | TDAV0811AN005 | TDAV0811AN005 | ZK1603000105 | RE: Leakage issue found at PAC11 (8Tr) at Asansol SAG2 Under AMC P:refrigerant leakage issue at PAC-11 oil separator joint. S:AMC | 2023-09-07 | 2023-09-07 19:08 | No | Contract | Reliance Jio Infocomm Limited | SURVEY PLOT NO-COM/G/01 MOUJA-SITLA, | ASANSOL | 713302 | West Bengal | India FS East Cooling CSP Snow Point Kolkata | Laxmikant Dhang_Snow Point Kolkata | Snow Point | OIL SIGN.OIL SEPARATOR LTO LEAKAGE.REFRIGERANT PUMP DOWN.LEAKAGE REPAIRING.VACCUM. 4.8KG R22 GAS TOPUP.ALL PARAMETER CHECKED.MACHINE OK RUNNING. | Repair |  | 10- Closed | 2023-09-08 07:18 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 200 | INR | 200 | ENM SECURE POWER
WO-11208879 | 103747528 | 2023-09-04 10:51 | 2023-09-04 |  | 2023-09-04 10:18 | 30002459 | 30002459 | 30002459 | 54232040094 | As per the Sr. no, The Product is in Warranty. Kindly arrange the site visit. Issue: meter continously showing current without inputs Address Schneider Electric Infra. Ltd. 328/23-24 Rasulabad Road,Village Jarod Taluka- Waghodia Vadodara 391510 Gujarat India Contact person Details: - Mr.Vineet 8882478125 | 2023-09-04 | 2023-09-05 12:38 | No | Warranty | Schneider Electric Infra. Ltd. | IN16,328/23-24 Rasulabad Road,Village Jarod Taluka- Waghodia | Vadodara | 391510 | Gujarat | India FS ED&I CSP West Team Jay Services Vadodara | Ghanshyam Kachiya_Jay Services Vadodara | Jay Services | We visited at site & checekd that Meter SR 54232040094- test by Aux supply found meter display ON but some current value Display Continur . We set CTR only 1 & observed display value 0.046 Amp meter faulty. Need to be replace. Meter SR 54231860273- test by Aux supply Found display ON but some value display without load also found set Button not working. meter faulty need to be replace. Meter- 54231860327 - observed meter display scratches . now we replace display from other def meter & test working ok. checked CAD32U7- found 43-44 contact continuity open. we open & observed that moving contact strip out of space . now rectify & tested ok. only two ammeter need to be replace. | Repair |  | 9- Service Validated | 2023-09-05 12:38 |  |  | 26 | INR | 26 | ENM POWER PRODUCTS
WO-11178429 |  | 2023-09-15 11:16 | 2023-09-02 |  | 2023-08-29 12:33 | TDAVQ | TDAVQ | TDAVQ | C21923003452 | PM | 2023-08-29 | 2023-09-08 17:49 | No | Contract | Army commanding Office | Army commanding Office Signal null | KARGIL | 194102 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-21 17:53 |  |  | 860 | INR | 860 | ENM SECURE POWER
WO-11178435 |  | 2023-09-15 11:43 | 2023-09-02 |  | 2023-08-29 12:34 | PRODUCT UNIFLAIR LEONARDO DX EV TDAV1822A R407C EC FAN DOWNFLOW WITH HEATER AND | TDAVQ | TDAVQ | C21922003069 | PM | 2023-08-29 | 2023-09-02 13:32 | No | Contract | Army commanding Office | Army commanding Office Signal null | LEH | 194101 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-19 13:35 |  |  | 740 | INR | 740 | ENM SECURE POWER
WO-11210557 | 103755183 | 2023-09-04 12:30 | 2023-09-04 |  | 2023-09-04 11:18 | METSEEM6459HCL10NC | METSEEM6459HCL10NC | METSEEM6459HCL10NC |  | XB5AA42N & METSEEM6459HCL10NC-Not Working. Please see below details of Part References which has found in faulty condition. So, take action for repair/replacement urgently.. 1) PART NO: METSEEM6459HCL10NC PART NO : METSEEM6459HCL10NC QTY. : 1 NO. ISSUE : Display not working. Invoice No. : 9008399843 - Copy Attached. 2) PART NO: XB5AA42N PART NO : XB5AA42N QTY. : 1 NO. ISSUE : It's nor release back and stuck in press position. Invoice No. : - Copy Attached. # Location and contact details. Location : Survey No. 248-250, First Floor Sardar Patel Ring Road, Nana Chiloda, Gandhinagar - 382330 Contact person : Nilesh Jansari Contact No. : +91 97253 85545 | 2023-09-04 | 2023-09-04 17:17 | No | Warranty | Lubi Electronics Pvt. Ltd. | Survey No. 248-250, Sardar Patel Ring Road, Nana Chiloda, Basement & 1st Floor, Gandhinagar, | Ahmedabad | 380025 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Mistri Anik Engineering Ahmedabad | Anik Engineering (554) | Visited site and checked the product found physically observed ok. METSEEM6436HCL10NC SR NO : 160123 observed as per customer meter display problem. so we give the supply but no display observed . so may be its internal problem for replacement. XB3AA42N SR NO : 102308 observed push button mechanism problem. | Repair |  | 9- Service Validated | 2023-09-04 17:18 | =S= Consig Fill up 226014278 |  | 15 | INR | 15 | ENM POWER PRODUCTS
WO-11210573 | 103755091 | 2023-09-04 11:47 | 2023-09-04 |  | 2023-09-04 11:28 | GCR_MTZ2_CB | GCR_MTZ2_CB | GCR_MTZ2_CB |  | RE: LTX2292-MTZ ACB Release cover damage Dear CC Team, We observe during the internal Testing that one of ACB from facia Release cover was broken. Photo is attached for ACB Detail reference. Please depute service engineer and resolve the issue on priority our customer inspection is held up. Product Details: Photo Attached Site Address : SCHNEIDER ELECTRIC INFRASTRUCRE LTD . (LV FAT ) Mile Stone -87 , Village , Kotambi, Vadodara ? Halol Highway, Post ? Jarod , Vadodara Gujrat -391510, India Contact Person : Mr. Vineet Kushwaha Mo No: 8882478124 Mr. Amit Parida Mo No: 8249545477 | 2023-09-04 | 2023-09-05 13:17 | No | Warranty | M/s Schneider Electric Infrastructure Ltd. ( LV FAT) | Milestone 87,Village: Kotambi Vadodara-Halol Highway Post : Jarod, Dist. : Vadodara Vadodara, Gujarat - 391510 | VADODARA | 391510 | Gujarat | India FS ED&I CSP West Team Jay Services Vadodara | Ghanshyam Kachiya_Jay Services Vadodara | Jay Services | We visited at site & checekd that ACB ON-OFF operation found ok. Checked release working satisfactory. We observed that release front glass cover missing. It is breakagte from release top side resting point breakage so glass cover not fitted. We attached photographs & video for reference. we submit all details to schneider further action taken by SEIL. Micrologic X transparent cover Ref LV850053SP. | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-05 13:18 |  |  | 26 | INR | 26 | ENM POWER PRODUCTS
WO-11178431 |  | 2023-09-15 11:19 | 2023-09-02 |  | 2023-08-29 12:33 | TDAVQ | TDAVQ | TDAVQ | C21922004239 | PM | 2023-08-29 | 2023-09-07 16:10 | No | Contract | Army commanding Office | Army commanding Office Signal null | LEH | 194101 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-20 14:13 |  |  | 710 | INR | 710 | ENM SECURE POWER
WO-11210616 | 103756977 | 2023-09-05 13:28 | 2023-09-04 |  | 2023-09-04 11:46 | LC1D32M7 | LC1D32M7 | LC1D32M7 | 1022086 | As per the Sr. no(1022085), The Product is in Warranty. Kindly arrange the site visit. Issue: pole open issue Address Chicago piza 4A/17 old rajinder nagar, New delhi 110060 Delhi India Contact person Details: - Mr.Mohd Anas 7428316150 | 2023-09-04 | 2023-09-05 13:31 | No | Warranty | Chicago piza | 4A/17 old rajinder nagar, null | New delhi | 110060 | Delhi | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the contactor found output not showing due termination burnt, Hence no replacement given to customer. Email : id not provided by customer. | Repair |  | 9- Service Validated | 2023-09-05 14:44 |  |  | 20 | INR | 20 | ENM POWER PRODUCTS
WO-11178432 |  | 2023-09-15 11:21 | 2023-09-02 |  | 2023-08-29 12:33 | PRODUCT UNIFLAIR LEONARDO DX EV TDAV1021A R407C DOWNFLOW WITH HEATER AND HUM WIT | TDAVQ | TDAVQ | C21923000672 | PM | 2023-08-29 | 2023-09-07 13:23 | No | Contract | Army commanding Office | Army commanding Office Signal null | KHALSI | 190004 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-20 13:26 |  |  | 640 | INR | 640 | ENM SECURE POWER
WO-11225070 | 103857771 | 2023-09-07 15:59 | 2023-09-07 |  | 2023-09-07 15:47 | LEONARDO EV,DX,R22,EC FAN,( HCM109-DANFOSS ), DOWNFLOW WITHOUT HEATER & HUMIDIFI | TDAV0811AN005 | TDAV0811AN005 | C21611000764 | Outdoor Fan Faulty- C21611000764 Under AMC P:Outdoor Unit fan issue--c21611000764 S:AMC | 2023-09-07 | 2023-09-07 18:32 | No | Contract | RELIANCE JIO INFOCOMM LIMITED | 6th. Floor, Ashoka Millenium,Ring Road No-1, New Rajendra Nagar | Raipur | 492001 | chhattisgarh | India FS East Cooling CSP Capital Refrigeration Raipur | Abdul Bari_Capital Refrigeration Raipur | Capital Refrigeration | REPLACED CONDENSER FAN AND TESTING | Repair |  | 10- Closed | 2023-09-08 09:19 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 10 | INR | 10 | ENM SECURE POWER
WO-11210758 | 103758349 | 2023-09-04 12:55 | 2023-09-04 | NA | 2023-09-04 12:29 | LV525333 | LV525333 | LV525333 | 10-2023-w04-2 | As per the Sr. no(10-2023-w04-2), The Product is in Warranty. Kindly arrange the site visit. Issue: tripping issue Address Fashion group industrial solution pvt ltd Uhde house, opp. Sipla research centre, Vikhroli Mumbai 400083 Maharashtra India Contact person Details: - Mr.Ram kumar 9702304017 | 2023-09-04 | 2023-09-05 14:23 | No | Warranty | Fashion group industrial solution pvt ltd | Uhde house, opp. Sipla research centre, Vikhroli null | Mumbai | 400083 | Maharashtra | India FS ED&I CSP West Team East India Power Engineers Mumbai | Sandeep Ingavale East India Power engineers Mumbai | East India Power Engineers (5043) | Visited the site & checked the MCCB and found that CVS250 TMD type MCCB uses motor load. As per Schneider Standard, this MCCB is not suitable for motor load. Hence the complaint is not covered under warranty. | Repair |  | 8- Service Completed | 2023-09-05 14:31 |  |  | 12 | INR | 12 | ENM POWER PRODUCTS
WO-11178434 |  | 2023-09-15 11:28 | 2023-09-02 |  | 2023-08-29 12:34 | TDAVQ | TDAVQ | TDAVQ | C21922003072 | PM | 2023-08-29 | 2023-09-02 13:37 | No | Contract | Army commanding Office | Army commanding Office Signal null | LEH | 194101 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-19 13:41 |  |  | 740 | INR | 740 | ENM SECURE POWER
WO-11225363 | 103862282 | 2023-09-08 10:30 | 2023-09-07 |  | 2023-09-07 17:57 | APC Smart-UPS RT 10000VA 230V Harsh Environment | SURT10000XLI-CC | SURT10000XLI-CC | B21235001803 | FW: RR : IM15443274 ¦ Store Code : 8012 ¦ SCHNEIDER ¦ ANDHRA PRADESH -TRENDS Under AMC P: UPS BACKUP Issue S:AMC | 2023-09-07 | 2023-09-11 10:57 | No | Contract | Reliance Digital Retail Ltd | Multi Functional Complex, Alcot Gardens | Rajahmundry | 533102 | Andhra Pradesh | India FS South3 HBN CSP SatyaveniS LaserComputers Kakinada | Venkat Sastry SatyaveniS LaserComputers Kakinada | Laser Computers-Kakinada- Hyderabad | visit the site checked the ups ups bottons or not working ups batterey each 6 sv droped infrom the customer not the charge on 1863b8 no ups working fine | Repair |  | 10- Closed | 2023-09-11 11:02 |  |  | 65 | INR | 65 | ENM SECURE POWER
WO-11211098 | 103756081 | 2023-09-05 17:07 | 2023-09-04 | NA | 2023-09-04 14:01 | PM5000 series-PM5320-Relay, Control & Measurement - measuring, monitoring device | PM5000 series-PM5320-Relay, Control & Measurement - measuring, monitoring device |  |  | Person Assistance Required-Very very urgent-NCF for POR: AEB23240011 AA PANEL Name of Customer M/s Arrow Electricals India Pvt Ltd. Vasai (E) 2 Site Address M/s Arrow Electricals India Pvt Ltd. Vasai (E) 3 Name of contact person at site Ajay Yadav 4 Contact Phone / Mob. No: 8296588418 5 Defective product details PM5320CL0.5SRS485+BACNET LOAD MANAGER PM5320 CLASS 0.5S, RS485 PORT, BACNET PROTOCOL, 31ST HARMONIC, 2 DI, 2 DO, 35 ALARMS, DATA LOGGING, 64SAMPLES/CYCLE. 6 Product Make SCHNEIDER 7 Nature of Defect DISPLAY NOT SHOWING ANY READING 8 Shutdown availability if applicable open 9 Warranty status yes 10 Commissioned / Installed date 11 Serial No: or DOM of the product 0 12 Name & phone No: of person registering the complaint JAYESH MHATRE Executive-Purchase & store 08237393903 13 Channel (Distributor) Invoice Details Challan No:1359/23-24 Challan Dt.:03.Jul.2023 CENTRAL ELECTRICALS & ELECTRONICS PVT LTD. | 2023-09-04 | 2023-09-09 10:35 | No | Warranty | Arrow Electricals India Pvt. Ltd. | Arrow House (11A/11B), K.T. Industrial Park, Goraipada,, Vasai E, Dist. Palghar | Vasai | 401208 | Maharashtra | India FS ED&I CSP West Team Kanekar Consulting Engineers Pvt Ltd Thane | Nitin Arote_Kanekar Consulting Mumbai | Kanekar Consulting Engineers Pvt. Ltd. | Check both meter found display digit not showing only backlight show need to be replaced the meters | Repair |  | 9- Service Validated | 2023-09-09 16:46 | =S= Consig Fill up 226034250 |  | 27 | INR | 27 | ENM POWER PRODUCTS
WO-11178436 |  | 2023-09-15 11:49 | 2023-09-02 |  | 2023-08-29 12:34 | TDAVQ | TDAVQ | TDAVQ | C21926008911 | PM | 2023-08-29 | 2023-08-29 17:42 | No | Contract | Army commanding Office | Army commanding Office Signal null | KARGIL | 194103 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-18 17:45 |  |  | 490 | INR | 490 | ENM SECURE POWER
WO-11225406 | 103863063 | 2023-09-08 09:57 | 2023-09-08 |  | 2023-09-07 18:14 | SRC10KUXI | SRC10KUXI | SRC10KUXI | B22002014641 | FW: RR : IM15446029 ¦ Store Code : TFY1 ¦ SCHNEIDER ¦ HARYANA -SMART IN-warranty P: UPS BACKUP Issue S:Onsite | 2023-09-07 | 2023-09-08 13:38 | No | Contract | Reliance Retail Limited | RRL TFY1 SMART, GROUND & FIRST FLOOR MILAN PALACE, KHEWAT NO 714, KHASRA NO 461, AMBALA RD | KAITHAL | 136027 | Haryana | India FS North2 HBN CSP Green IT Solutions Chandigarh | Deepak Green IT Solutions Chandigarh | Green IT Solutions | Checked and found that ups ok and battery bank faulty need to be replace. So recommend to customer replace the battery bank | Repair |  | 10- Closed | 2023-09-08 13:45 |  |  | 135 | INR | 135 | ENM SECURE POWER
WO-11211216 | 103741278 | 2023-09-05 15:02 | 2023-09-04 | NA | 2023-09-04 14:44 | LC1D18M7 | LC1D18M7 | LC1D18M7 |  | As per the invoice, The Product is in Warranty. Kindly arrange the site visit. Issue: pole open issue Address SHRAM SHRADDHA NAGARI SAH.PATSANSTHA LTD OPP.STATE BANK OF INDIA, SALAVI STOP, NACHANE ROAD, Ratnagiri 415612 Maharashtra India Contact person Details: - Mr.Rajesh 8208960534 | 2023-09-04 | 2023-09-05 17:50 | No | Warranty | SHRAM SHRADDHA NAGARI SAH.PATSANSTHA LTD | OPP.STATE BANK OF INDIA, SALAVI STOP, NACHANE ROAD, null | Ratnagiri | 415612 | Maharashtra | India FS ED&I CSP West Team East India Power Engineers Mumbai | Abhishek Parab_East India Power engineers Mumbai | East India Power Engineers (5043) | As per discussion with Mr. Nitin sir, he said please book the material directly. | Repair |  | 8- Service Completed | 2023-09-08 16:41 | =S= Consig Fill up 226031653 |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11178438 |  | 2023-09-15 11:52 | 2023-09-02 |  | 2023-08-29 12:34 | TDAVQ | TDAVQ | TDAVQ | C21935000946 | PM | 2023-08-29 | 2023-08-31 16:53 | No | Contract | Army commanding Office | Army commanding Office Signal null | LEH | 194101 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-20 12:55 |  |  | 0 | INR | 0 | ENM SECURE POWER
WO-11225464 | 103862334 | 2023-09-08 10:46 | 2023-09-07 |  | 2023-09-07 18:34 | EFC Monoblock unit 1.3TER, downflow with start run relay kit | WDF0181BN002 | WDF0181BN002 | ZK1538005297 | RE: I-KA-BLGI-ILA-0001 PAC Issue - Bijapur CMP Under AMC P:Cooling Issue S:AMC | 2023-09-07 | 2023-09-08 17:00 | No | Contract | RELIANCE JIO INFOCOMM LIMITED | No-361/9,RS No-187/192, Situated At Girisagar layout Badagundi Village,Biligi Taluk Bagalkot Dist | Bagalkot | 587101 | Karnataka | India FS South3 Cooling CSP Fresco solutions Bangalore | FAIYAZ F_Fresco solutions Bangalore | Fresco solutions | Relay Cable wire got burned rectified the issue | Repair |  | 8- Service Completed | 2023-09-08 17:38 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 350 | INR | 350 | ENM SECURE POWER
WO-11211282 | 103764556 | 2023-09-06 12:34 | 2023-09-04 |  | 2023-09-04 15:19 | LC1D25M7 | LC1D25M7 | LC1D25M7 | 102312 1 | As per the Sr. no, The Product is in Warranty. Kindly arrange the site visit. Issue: pole open issue Address Indian plastic footware Plot no 88, sector 16 BAHADURGARH 124507 Haryana India Contact person Details: - Mr. Ashmeet 7496965002 | 2023-09-04 | 2023-09-11 13:20 | No | Warranty | Indian plastic footware | Plot no 88, sector 16 null | BAHADURGARH | 124507 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | checked the contactor found coils faulty, replaced LXD1B7 - 1 Nos. LXD1M7 - 1 Nos. Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-12 13:28 |  |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11178440 |  | 2023-09-15 11:55 | 2023-09-02 |  | 2023-08-29 12:34 | TDAVQ | TDAVQ | TDAVQ | C21931007248 | PM | 2023-08-29 | 2023-08-31 13:48 | No | Contract | Army commanding Office | Army commanding Office Signal null | KHALSAR | 180011 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-20 12:51 |  |  | 645 | INR | 645 | ENM SECURE POWER
WO-11226069 | 103864472 | 2023-09-07 18:50 | 2023-09-07 |  | 2023-09-07 18:48 | APC Smart-UPS VT 30kVA 400V, Internal Maintenance Bypass | SUVT30KH | SUVT30KH | PS0543345808 | FW: UPS backup not happening @361_Basaveshwar Nagar HDFC Bank Under AMC P: UPS backup not happening S:AMC | 2023-09-07 | 2023-09-08 15:45 | No | Contract | HDFC Bank Ltd | NO. 321, 3RD STAGE, 4TH BLOCK, NEAR 8TH MAIN, CLOSE TO AIRTEL SHOWROOM, BANGALORE, KARNATAKA | BANGALORE | 560079 | Karnataka | India FS South1 HBN CSP UBM Autopower Pvt. Ltd Bangalore | Robert UBM Autopower Pvt. Ltd Bangalore | Autopower systems and solutions | We received call on Fri - 8th Sep. 10:11 AM only, Onsite Date: 8th Sep. Checked the ups Found NPF, High voltage informed Customer need to resolved the Electric issue, UPS working fine. | Repair |  | 10- Closed | 2023-09-09 13:53 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 9 | INR | 9 | ENM SECURE POWER
WO-11211394 | 103763630 | 2023-09-04 16:48 | 2023-09-04 | Meter not power on | 2023-09-04 16:05 | METSEEM6436HCL10RS | METSEEM6436HCL10RS | METSEEM6436HCL10RS |  | Meter complaint Name of Customer NAVASASYAM DANDEKAR PVT LTD Site Address GAT NO. 108, VILLAGE, KHALUMBRE TALUKA-KHED NEAR KSH CHOWK, BEHIND YAP COMPANY PUNE-410501 Name of contact person at site Atul K. Shinde. Contact Phone / Mob. No: 9673540064 Defective product details METSEEM6436HCL10RS Product Make SCHNEIDER Nature of Defect Not working Shutdown availability if applicable Yes Serial Num Number of the product: 540420171341 Warranty status In Warranty Commissioned / Installed date 9/1/2023 Invoice Number 8/31/2023 Serial No: or DOM of the product 540420171341 | 2023-09-04 | 2023-09-04 17:47 | No | Warranty | Navasasyam Dandekar Pvt Ltd | Gat No.108, Village, Khalumbre, Near KSH Chowk, Behind YAPP Taluka Khed | Pune | 410501 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Amit Patil_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the Meter not power on. they use 1A Glass fuse for control Supply to meter. we given supply to meter but it's not getting power on. So problem observed in Meter., meter needs to be replaced. Required Material : METSEEM6436HCL10RS - 01 nos | Repair |  | 9- Service Validated | 2023-09-05 11:11 | =S= Consig Fill up 226030331 |  | 65 | INR | 65 | ENM POWER PRODUCTS
WO-11178441 |  | 2023-09-15 11:57 | 2023-09-02 |  | 2023-08-29 12:34 | TDAVQ | TDAVQ | TDAVQ | C21931010877 | PM | 2023-08-29 | 2023-08-31 13:42 | No | Contract | Army commanding Office | Army commanding Office Signal null | KHALSAR | 180011 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-20 12:46 |  |  | 645 | INR | 645 | ENM SECURE POWER
WO-11228394 | 103878842 | 2023-09-08 12:36 | 2023-09-08 |  | 2023-09-08 10:09 | APC Smart-UPS RT 2000VA 230V No Batteries | SURT2000UXI | SURT2000UXI | JS0750009538 | FW: INC0004408547//S1ANHY36//Jubilee Hills Offsite//UPS BATTERIES BACK UP NIL : Chargeable basis case logged for 1time UPS checking (mention serial number of JS0750009538) No Spares support APC will Pay the charges S: Chargeable basis case logged for 1time UPS checking : (mention serial number of JS0750009538) | 2023-09-08 | 2023-09-08 12:41 | No | Commercial Action - Sales | HDFC Bank Ltd | HDFC ATM S1ANHY36 Jubilee Hills Club Offsite Hyderabad | Hyderabad | 500033 | Telangana | India FS South3 HBN CSP CENTRALDATASYSTEMS HYDERABAD | Nagesh CENTRALDATASYSTEMS HYDERABAD | Central Data Systems Pvt Ltd | Visited site and found battery issue also ups input power disconnected condition | Repair |  | 10- Closed | 2023-09-08 12:45 |  |  | 8 | INR | 8 | ENM SECURE POWER
WO-11211533 | 103746915 | 2023-09-04 18:09 | 2023-09-04 |  | 2023-09-04 16:24 | LC1D09BD | LC1D09BD | LC1D09BD | 1023324 | As per the Sr. no, The Product is in Warranty. Kindly arrange the site visit. Issue: pole open issue Address GLOBAL CNC PVT LTD Plot No.G-2617/19, Gate No.1,GIDC Metoda Rajkot 360021 Gujarat India Contact person Details: - Mr. Ajay 8849044149 | 2023-09-04 | 2023-09-05 16:03 | No | Warranty | GLOBAL CNC PVT LTD | Plot No.G-2617/19, Gate No.1,GIDC Metoda null | Rajkot | 360021 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | Jayesh J_JKS Rajkot | JKS Engineering Co. | Visited site and observation check contactor all terminal found check with external 24v dc with coil not working then open and check coil found not damage but its terminal side wire broken due to this issue we have consider in warranty and give 1nos replacement. | Repair |  | 9- Service Validated | 2023-09-05 16:03 | =S= Consig Fill up 226031334 |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11228404 | 103878999 | 2023-09-11 14:41 | 2023-09-08 |  | 2023-09-08 10:18 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | C21708001059 | P:Damper Motor fault---C21708001059 Under AMC P:Damper Motor fault---C21708001059 S:AMC | 2023-09-08 | 2023-09-12 12:00 | No | Contract | Reliance Jio Infocomm Ltd | Mr.Gireesh Babu, Palattuparambath House, Panamaram Post, Wayanad | WAYANAD | 670721 | Kerala | India FS South2 Cooling CSP Evergreen Thiruvananthapuram | Anwar_Evergreen Thiruvananthapuram | Evergreen | D amber Motor Fault | Repair |  | 8- Service Completed | 2023-09-12 09:29 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 180 | INR | 180 | ENM SECURE POWER
WO-11211547 | 103765918 | 2023-09-04 16:50 | 2023-09-04 |  | 2023-09-04 16:31 | NA06304V | NA06304V | NA06304V | WG22452390057 | ASCO Complaint / Pune Please create WO for complaint. ATS Ref:- NA06304V SL No:- WG22452390057 Under warranty:- Yes Problem:- Manual handle lock issue Customer details:- Vertiv Energy Private Limited Plot No A-78, VIII, ESR Pune Industrial Park Pvt Ltd Wasuli, Tal Khed, MIDC Phase II, Chakan, Pune 410501 Mr. Prasad ? 7400173092 prasad.yadav@vartiv.com | 2023-09-04 | 2023-09-04 22:37 | No | Warranty | Vertiv Energy Private Limited | Plot No A-78, VIII, ESR Pune Industrial Park Pvt Ltd Wasuli, Tal Khed, MIDC Phase II, Chakan null | Pune | 410501 | Maharashtra | India FS ED&I CSP West Team R P Electrical Mumbai | Shridhar Dongare R P Electrical Mumbai | R P Electrical | Checked ATS found ATS baned guards head damaged 02 Nos. | Repair |  | 9- Service Validated | 2023-09-04 22:43 |  |  | 51 | INR | 51 | ENM POWER PRODUCTS
WO-11229114 | 103879650 | 2023-09-08 18:15 | 2023-09-08 |  | 2023-09-08 10:49 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | JK1928005838 | Water leakage Serial# JK1928005838 P: Water leakage S: AMC | 2023-09-08 | 2023-09-09 09:25 | No | Contract | Reliance Jio Incocom Ltd | Ward No.5,Rongmongve, Near Diphu Law College, Thana Road,Diphu | KARBI ANGLONG | 782460 | Assam | India FS East Cooling CSP SYSCOMP POWERSOL Guwahati | SHUBHAM PATHAK SYSCOMP POWERSOL Guwahati | SYSCOMP POWERSOL - GUWAHATI | Found water leakage issue, maintenance done ok, now working properly | Repair |  | 10- Closed | 2023-09-11 01:27 |  |  | 300 | INR | 300 | ENM SECURE POWER
WO-11229237 |  | 2023-09-29 21:33 | 2023-09-20 |  | 2023-09-08 11:56 | EFC MONOBLOCK 1.3TR R410A START KIT RS485 SEQ CONTROL | WDF0181BN040-1 | WDF0181BN040-1 | JK2044000331 | pm | 2023-09-08 | 2023-09-20 18:00 | No | Contract | Reliance Jio Info comm | Open Plot of Patel Mukundbhai Kanchanbhai,Survey No 66, Village Jambudi Tehsil Halol, Dist Panchmahal null | Panchmahal | 389350 | Gujarat | India FS West2 Cooling CSP Comfort HVAC Solutions Ahd | Avesh Memon Comfort HVAC Solutions Ahd | Comfort HVAC Solutions | Preventive Maintenance done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-29 21:36 |  |  | 155 | INR | 155 | ENM SECURE POWER
WO-11229238 | 90708921 | 2023-09-29 21:55 | 2023-09-21 |  | 2023-09-08 11:56 | WDF0181BN040-1 | WDF0181BN040-1 | WDF0181BN040-1 | JK22046000846 | PM | 2023-09-08 | 2023-09-21 18:00 | No | Contract | Reliance Jio Infocomm Ltd | RCom tower, Behind Naswadi Chowkdi,Avayraj Society null | VADODARA | 391170 | Gujarat | India FS West2 Cooling CSP Comfort HVAC Solutions Ahd | Avesh Memon Comfort HVAC Solutions Ahd | Comfort HVAC Solutions | Preventive Maintenance done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-29 21:58 |  |  | 100 | INR | 100 | ENM SECURE POWER
WO-10996971 | 102486283 | 2023-09-15 11:19 | 2023-07-15 |  | 2023-07-15 10:13 | SRV15KUXI-IN | SRV15KUXI-IN | SRV15KUXI-IN | 9S2308A04504 | DOP : 4 JUL 2023 P : Installation C : NA T : NA S : Installation | 2023-07-15 | 2023-09-15 11:21 | No | Commercial Action - Sales | Observabt Soft Services Pvt Ltd | Unit No 608 Jain Sadguru Image Capital Park 6rd Floor Madhapur null | Hyderabad | 500081 | Telangana | India FS South3 HBN CSP CENTRALDATASYSTEMS HYDERABAD | B Ramakrishna CENTRALDATASYSTEMS HYDERABAD | Central Data Systems Pvt Ltd | ups installation done ups working fine | Commissioning & Installation | Start-up | 8- Service Completed | 2023-09-15 11:24 |  |  | 15 | INR | 15 | ENM SECURE POWER
WO-11229239 |  | 2023-09-29 21:43 | 2023-09-21 |  | 2023-09-08 11:56 | EFC MONOBLOCK 1.3TR R410A START KIT RS485 SEQ CONTROL | WDF0181BN040-1 | WDF0181BN040-1 | JK2040002069 | PM | 2023-09-08 | 2023-09-21 18:00 | No | Contract | Reliance Jio Infocomm Ltd | Behind swamynarayan mandir Dabhoi null | Vadodara | 391110 | Gujarat | India FS West2 Cooling CSP Comfort HVAC Solutions Ahd | Avesh Memon Comfort HVAC Solutions Ahd | Comfort HVAC Solutions | Preventive Maintenance done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-29 21:45 |  |  | 220 | INR | 220 | ENM SECURE POWER
WO-11229240 | 98967679 | 2023-09-29 21:38 | 2023-09-19 |  | 2023-09-08 11:56 | EFC MONOBLOCK 1.3TR R410A START KIT RS485 SEQ CONTROL | WDF0181BN040-1 | WDF0181BN040-1 | JK2046002182 | PM | 2023-09-08 | 2023-09-19 18:00 | No | Contract | Reliance Jio Infocomm Ltd | Block Survey No. 123, Khata N0. 182, Mouje:- Vijyakhunt, Mahisagar null | Dahod | 389260 | Gujarat | India FS West2 Cooling CSP Comfort HVAC Solutions Ahd | Avesh Memon Comfort HVAC Solutions Ahd | Comfort HVAC Solutions | Preventive Maintenance done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-29 21:41 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 220 | INR | 220 | ENM SECURE POWER
WO-11221327 | 103813724 | 2023-09-06 13:38 | 2023-09-06 |  | 2023-09-06 12:36 | LV525333 | LV525333 | LV525333 | 10 2022 W18 4 | Fwd: Case : 103728156 dt. 2.9.23 Vinayak Granite pvt ltd H 163, Rupanghar, kishangarh Ajmer Rajasthan Mr.Sita ram 7780554315 Product : LV525333 Serial Number : 10 2022 W18 4 tripping issue | 2023-09-06 | 2023-09-06 13:42 | No | Warranty | Vinayak Granite pvt ltd | H 163, Rupanghar, kishanghar | Ajmer | 305814 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Sunny Sharma Sharma Electric Jaipur | Sharma Electric Works | Checked the mccb found working ok. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-07 15:33 |  |  | 135 | INR | 135 | ENM POWER PRODUCTS
WO-11178552 |  | 2023-09-15 11:59 | 2023-09-02 |  | 2023-08-29 13:13 | TDAVQ | TDAVQ | TDAVQ | C21934000963 | PM | 2023-08-29 | 2023-09-02 15:48 | No | Contract | Army commanding Office | Army commanding Office Signal null | LEH | 194101 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-19 13:50 |  |  | 780 | INR | 780 | ENM SECURE POWER
WO-11229241 |  | 2023-09-25 18:37 | 2023-09-09 |  | 2023-09-08 11:56 | PRODUCT UNIFLAIR LEONARDO DX IDAV0811 DOWNFLOW R410A DBL SKN WITHOUT HTR AND HUM | TDAVQ | TDAVQ | JK2206024855 | PM | 2023-09-08 | 2023-09-09 18:00 | No | Commercial Action - Sales | RIL JIO INFOCOMM LTD | Opp Sudamanagar Society,Nr.balaji Steel Traders,Raliyati Road null | Dahod | 389151 | Gujarat | India FS West2 Cooling CSP Comfort HVAC Solutions Ahd | Avesh Memon Comfort HVAC Solutions Ahd | Comfort HVAC Solutions | Preventive Maintenance done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-25 18:40 |  |  | 220 | INR | 220 | ENM SECURE POWER
WO-11221520 | 103816408 | 2023-09-06 16:19 | 2023-09-06 |  | 2023-09-06 13:46 | DM3110 | DM3110 | DM3110 |  | Regarding Faulty Ammeter Sr. No. MATERIAL DESCRIPTION NATURE OF THE COMPLAINT 1 AMMETER DM3110 DISPLAY PROBLEM (DISPLAY NOT SHOWING) (S/N 54233110193) THE ADDRESS AND CONTACT IS AS UNDER: Shivalic Power Control Private Limited Global Manufacturer of LT & HT Panels Plot No-72, Sector-68, IMT Faridabad-121004, India | 2023-09-06 | 2023-09-12 16:16 | No | Warranty | Shivalic Power Control Private Limited | Plot No.- 72, Sector- 68, IMT | Faridabad | 121004 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the meter found display not showing. Hence faulty replaced. 30002461 - 1 Nos. email : id not provided by customer . | Repair |  | 9- Service Validated | 2023-09-12 16:19 |  |  | 52 | INR | 52 | ENM POWER PRODUCTS
WO-11178556 |  | 2023-09-15 12:04 | 2023-09-02 |  | 2023-08-29 13:13 | TDAVQ | TDAVQ | TDAVQ | C21930012884 | PM | 2023-08-29 | 2023-09-01 13:21 | No | Contract | Army commanding Office | Army commanding Office Signal null | BASECAMP | 181124 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-20 16:24 |  |  | 750 | INR | 750 | ENM SECURE POWER
WO-11229242 |  | 2023-09-25 18:33 | 2023-09-09 |  | 2023-09-08 11:56 | PRODUCT UNIFLAIR LEONARDO DX IDAV0811 DOWNFLOW R410A DBL SKN WITHOUT HTR AND HUM | TDAVQ | TDAVQ | JK2224020476 | PM | 2023-09-08 | 2023-09-09 18:00 | No | Commercial Action - Sales | RIL JIO INFOCOMM LTD | Opp Sudamanagar Society,Nr.balaji Steel Traders,Raliyati Road null | Dahod | 389151 | Gujarat | India FS West2 Cooling CSP Comfort HVAC Solutions Ahd | Avesh Memon Comfort HVAC Solutions Ahd | Comfort HVAC Solutions | Preventive Maintenance done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-25 18:35 |  |  | 220 | INR | 220 | ENM SECURE POWER
WO-11178572 |  | 2023-09-15 12:13 | 2023-09-02 |  | 2023-08-29 13:13 | TDAVQ | TDAVQ | TDAVQ | C21935000945 | PM | 2023-08-29 | 2023-08-29 18:03 | No | Contract | Army commanding Office | Army commanding Office Signal null | P GALI | 192301 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-18 18:07 |  |  | 895 | INR | 895 | ENM SECURE POWER
WO-11229243 |  | 2023-09-18 09:38 | 2023-09-11 |  | 2023-09-08 11:56 | InRow RD, 300mm, Air Cooled, 220-240V, 50Hz | ACRD101 | ACRD101 | UK1130112043 | PM | 2023-09-08 | 2023-09-11 18:00 | No | Contract | Siemens Limited | Maneja Near Makarpura Railway Station Near Makarpura Railway Stn | Vadodara | 390013 | Gujarat | India FS West2 Cooling CSP Comfort HVAC Solutions Ahd | Avesh Memon Comfort HVAC Solutions Ahd | Comfort HVAC Solutions | Preventive Maintenance done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-18 09:41 |  |  | 130 | INR | 130 | ENM SECURE POWER
WO-11222028 | 103825406 | 2023-09-07 15:03 | 2023-09-06 |  | 2023-09-06 17:05 | NR06304 | NR06304 | NR06304 | WG22233390060 | ASCO Complaint/Goa Please create WO for the complaint. ATS ref:- NR06304 SL No:- WG22233390060 Under warranty:- Yes Problem:- Remote transfer option not working. Customer details:- Electro Controls Sancoale, Zuari Nagar, Goa ? 403726 Mr. Akshay Stores.electrocontrols@gmail.com 9325949662 | 2023-09-06 | 2023-09-07 11:11 | No | Warranty | Electro Controls(17996) | D3/14, Sancoale Industrial Estate, | South Goa | 403726 | Goa | India FS ED&I CSP West Team R P Electrical Mumbai | Ramaji Desai R P Electrical Mumbai | R P Electrical | Visited the site and found ATS / RTS in de-energized condition. Checked the RTS and observed the R type controller of RTS. Observed R1 & R0-No, R3 and R0-NO But R2 and R0 was continuously NC. Removed the harness from controller and checked the harness from controller and checked the harness coming from PLC to RTS. The Harness continuously NC. The controller again done the lugging and re-installed the harness and now all the contacts are NO. We had short R1 & R0, R2 & RO & R3 RO. Transfer to source I, source II and off normal. We had short the PLC contacts and found normal operation of RTS / ATS. The customer will check with the PLC. ATS is working manually and electrically Ok. | Repair |  | 9- Service Validated | 2023-09-08 11:23 |  |  | 52 | INR | 52 | ENM POWER PRODUCTS
WO-11178553 |  | 2023-09-19 14:03 | 2023-09-02 |  | 2023-08-29 13:13 | PRODUCT UNIFLAIR LEONARDO DX EV TDAV1822A R407C DOWNFLOW WITH HEATER AND HUM WIT | TDAVQ | TDAVQ | C21934001252 | PM | 2023-08-29 | 2023-09-02 15:05 | No | Contract | Army commanding Office | Army commanding Office Signal | LEH | 194101 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-19 14:08 |  |  | 780 | INR | 780 | ENM SECURE POWER
WO-11229244 |  | 2023-09-18 09:46 | 2023-09-11 |  | 2023-09-08 11:56 | InRow RD, 300mm, Air Cooled, 220-240V, 50Hz | ACRD101 | ACRD101 | UK1130112041 | PM | 2023-09-08 | 2023-09-11 18:00 | No | Contract | Siemens Limited | Maneja Near Makarpura Railway Station Near Makarpura Railway Stn | Vadodara | 390013 | Gujarat | India FS West2 Cooling CSP Comfort HVAC Solutions Ahd | Avesh Memon Comfort HVAC Solutions Ahd | Comfort HVAC Solutions | Preventive Maintenance done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-18 09:48 |  |  | 130 | INR | 130 | ENM SECURE POWER
WO-11229115 | 103879636 | 2023-09-08 11:44 | 2023-09-08 |  | 2023-09-08 10:50 | 30002385 | 30002385 | 30002385 |  | Meter DM3110, 30002385 Srn 54-223110665 DOM July 2022 Fault : Not powering ON Meter DM3110, 30002385 Srn 54-223110665 DOM July 2022 Fault : Not powering ON Display unit Fail Shree ji Marbles NH-8 Riico industrial area, Gunjol, Nathdwara, Rajsamand, Rajasthan 313301 Mr. Balak Kumar 9540904757 | 2023-09-08 | 2023-09-08 11:47 | No | Warranty | Shree ji marble | NH-8 riico industrial area, Gunjol, Nathdwara, Rajsamand, | Udaipur | 313301 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Sunny Sharma Sharma Electric Jaipur | Sharma Electric Works | Checked the meter found not power up and coil found internally short, Hence faulty replaced. 30002385 - 1 nos 30002055 - 1 nos LX1FL415 - 1 nos Email : bkv.rjs@rediffmail.com | Repair |  | 9- Service Validated | 2023-09-08 15:28 |  |  | 355 | INR | 355 | ENM POWER PRODUCTS
WO-11178554 |  | 2023-09-19 14:12 | 2023-09-02 |  | 2023-08-29 13:13 | TDAVQ | TDAVQ | TDAVQ | C21929011524 | PM | 2023-08-29 | 2023-09-07 17:03 | No | Contract | Army commanding Office | Army commanding Office Signal | KAIRI | 194201 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-21 17:07 |  |  | 845 | INR | 845 | ENM SECURE POWER
WO-11229245 |  | 2023-09-25 18:29 | 2023-09-09 |  | 2023-09-08 11:56 | PRODUCT UNIFLAIR LEONARDO DX IDAV0811 DOWNFLOW R410A DBL SKN WITHOUT HTR AND HUM | TDAVQ | TDAVQ | JK2224000830 | PM | 2023-09-08 | 2023-09-09 18:00 | No | Commercial Action - Sales | RIL JIO INFOCOMM LTD | Opp Sudamanagar Society,Nr.balaji Steel Traders,Raliyati Road null | Dahod | 389151 | Gujarat | India FS West2 Cooling CSP Comfort HVAC Solutions Ahd | Avesh Memon Comfort HVAC Solutions Ahd | Comfort HVAC Solutions | Preventive Maintenance done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-25 18:32 |  |  | 220 | INR | 220 | ENM SECURE POWER
WO-11178574 |  | 2023-09-15 12:16 | 2023-09-02 |  | 2023-08-29 13:13 | TDAVQ | TDAVQ | TDAVQ | C21935002109 | PM | 2023-08-29 | 2023-09-01 16:33 | No | Contract | Army commanding Office | Army commanding Office Signal null | LEH | 194101 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-20 16:43 |  |  | 865 | INR | 865 | ENM SECURE POWER
WO-11229299 | 103880666 | 2023-09-08 12:33 | 2023-09-07 |  | 2023-09-08 12:20 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | C21802000008 | RE: Create case-ID- low cooling issue Under AMC P:Low cooling issue S:AMC | 2023-09-08 | 2023-09-07 16:36 | No | Contract | Reliance Jio Infocomm Ltd | Near Buddha temple,Pudhu | Gummidipoondi | 601201 | Tamil Nadu | India FS South4 Cooling CSP Unity Air conditioning Engineers Chennai | V Ramkumar_ Unity Air conditioning Engineers Chennai | UNITY AIRCONDITIONING ENGINEERS | L.P Alarm: Now we checked and found R22 gas is fully vapor. Now we release the old gas in the unit and vacuumizing, recommissioning in the unit, all parameters working normal. | Repair |  | 10- Closed | 2023-09-08 16:50 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 66 | INR | 66 | ENM SECURE POWER
WO-11229439 | 103882063 | 2023-09-08 14:14 | 2023-09-08 |  | 2023-09-08 13:14 | GCR_NW_CB | GCR_NW_CB | GCR_NW_CB | 10220350109 | FW: Boeing B1 - Two number Source A and Source B of 1000A ACB Spring charge Issue and Breaker Draw out issue NW10H14PMD02.0A 10220350109 1000A Spring Charge Issue | 2023-09-08 | 2023-09-08 16:09 | No | Warranty | M/S. Boeing India PVT LTD | BIETCampus-PH-1A-B1 & Security Plaza Interior GCPlOT NO:-55-B56,57&59, HI- Tech, Defense aerospace Park ( Aerospace Sector) Devanhalli Village, Jala Hobli, Yelahanka Taluk | Bangalore | 562110 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Santhosh DP_P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | Inspected and found 1)NW16HA4PMDO S/N: 10220350003,ACB Breaker Rack out issue, because of (fully tight)over Rack in fromm customer side. So we have same as rectified the problem, and same as explaine to customer. After tested ACB Rack in & Rack out operation working found ok. *Customer complaint ACB not closing, because of breaker in side UV coil fixed. But UV coil wiring is not done by customer. Kindly discuss your panel builder. *As per customer request we removed UV coil after teste ACB breaker ON/OFF tested working found ok. *There is no problem in our products | Repair |  | 8- Service Completed | 2023-09-08 16:10 |  |  | 43 | INR | 43 | ENM POWER PRODUCTS
WO-11178555 |  | 2023-09-19 14:14 | 2023-09-02 |  | 2023-08-29 13:13 | TDAVQ | TDAVQ | TDAVQ | C21931013821 | PM | 2023-08-29 | 2023-09-07 16:47 | No | Contract | Army commanding Office | Army commanding Office Signal | KAIRI | 194201 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-21 16:51 |  |  | 845 | INR | 845 | ENM SECURE POWER
WO-11229568 | 103850990 | 2023-09-08 15:31 | 2023-09-08 | NA | 2023-09-08 13:57 | LV540309 | LV540309 | LV540309 |  | As per the invoice, The Product is in Warranty. Kindly arrange the site visit. Issue: pole open issue Address APJ ENGINEERS PVT LTD PLOT NO333. PELHAR VIL NALASUPARA HIGHWAY ROAD BEHIND SKYWAY HOTEL Thane 401208 Maharashtra India Contact person Details: - Mr.Mukhatar 9819084048 | 2023-09-08 | 2023-09-11 17:36 | No | Warranty | APJ Engineers Pvt. Ltd. | PLOT NO333. PELHAR VIL NALASUPARA HIGHWAY ROAD BEHIND SKYWAY HOTEL null | Thane | 401208 | Maharashtra | India FS ED&I CSP West Team East India Power Engineers Mumbai | Sandeep Ingavale East India Power engineers Mumbai | East India Power Engineers (5043) | Visited the site & checked MCCB continuity in ON condition and found all four poles okay. Also applied 3ph supply on MCCB input side & checked the output side voltage found incoming voltage value match with outgoing voltage value. Hence the MCCB all poles ok & working found ok. | Repair |  | 8- Service Completed | 2023-09-12 08:31 |  |  | 41 | INR | 41 | ENM POWER PRODUCTS
WO-11178618 |  | 2023-09-15 12:44 | 2023-09-02 |  | 2023-08-29 13:29 | TDAVQ | TDAVQ | TDAVQ | C21930006599 | PM | 2023-08-29 | 2023-09-06 16:38 | No | Contract | Army commanding Office | Army commanding Office Signal null | DAYALACHAK | 180001 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-21 16:44 |  |  | 745 | INR | 745 | ENM SECURE POWER
WO-11178557 |  | 2023-09-15 12:05 | 2023-09-02 |  | 2023-08-29 13:13 | TDAVQ | TDAVQ | TDAVQ | C21930012890 | PM | 2023-08-29 | 2023-09-01 13:39 | No | Contract | Army commanding Office | Army commanding Office Signal null | BASECAMP | 181124 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-20 16:19 |  |  | 750 | INR | 750 | ENM SECURE POWER
WO-11229846 | 103888671 | 2023-09-08 16:50 | 2023-09-08 |  | 2023-09-08 15:49 | J07ATSC30400K500 | J07ATSC30400K500 | J07ATSC30400K500 |  | FW: One Pallet received in Wet & packing damage condition MUM-31521 .( HAWB # MFE0028573 ) 59 packages. PO 1104964495 Please create WO for the complaint under Inspection and Assessment. ATS Ref:- J07ATSC30400K500; Or pls use GCR_ASCO_S7000 Under warranty:- Yes, just landed in MDC Problem:- Damaged, need to inspect for conclusion SrNo Material Description PO no PO line Inbound Qty 1 J07ATSC30400K500 836530,7000 SERIES J FRAME OLN 400A 1104964495 10 1 Customer details:- Mumbai DC SCHNEIDER ELECTRIC INDIA PRIVATE LIMITED Phone: 336-731-5000 BLDG NO 3 BGR WAREHOUSING COMPLEX BEHIND HP PETROL PUMP MUMBAI NASHIK HIGHWAY VILLAGE VAHULI TAI BHIWANDI THANE Sold To MAHARASHTRA INDIA 421302 Hitesh - +91967006956 Hitesh.Kamte@non.se.com | 2023-09-08 | 2023-09-09 10:44 | No | Warranty | Schneider Electric India Pvt. Ltd. Mumbai DCcu | BGR Warehousing Complex,Building No. 3, Building No. 3,Near Shiv Sagar Hotel, Behind HP Petrol Pump, Mumbai Nashik Highway, Bhiwandi, Thane - | Mumbai | 421302 | Maharashtra | India FS ED&I CSP West Team R P Electrical Mumbai | Sunil Jadhav R P Electrical Mumbai | R P Electrical | Checked the ATS, controller and switch has water entry indications and unable declare it is healthy without testing the complete ATS. Hence its required testing, informed to MDC. | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-12 10:49 |  |  | 53 | INR | 53 | ENM POWER PRODUCTS
WO-11178573 |  | 2023-09-15 12:14 | 2023-09-02 |  | 2023-08-29 13:13 | TDAVQ | TDAVQ | TDAVQ | C21935001084 | PM | 2023-08-29 | 2023-09-01 16:26 | No | Contract | Army commanding Office | Army commanding Office Signal null | LEH | 194101 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-20 16:29 |  |  | 865 | INR | 865 | ENM SECURE POWER
WO-11229988 | 103890862 | 2023-09-11 13:11 | 2023-09-08 |  | 2023-09-08 16:40 | LC1D09 | LC1D09 | LC1D09 |  | LC1D09--2 no ,63amp 4P--2 no , 32amp 3P--1 no, 32amp 4P--1 no MCB's Aug 2023--Samta Electric LC1D09--2 no ,63amp 4P--2 no , 32amp 3P--1 no, 32amp 4P--1 no Aug 2023--Samta Electric Nuisance Tripping Site : 1234/5, Bada Jain Temple, Sonipat, Harayana Mr.Rahul : 7027933093 | 2023-09-08 | 2023-09-14 16:24 | No | Warranty | Mr. Rahul | 1234/5, Bada Jain Temple | Sonipat | 131001 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mcb found dolly free and contactor found not working due to coil issue, Hence faulty replaced. A9N4P63C - 1 nos A9N3P32C - 1 nos LXD1M7 - 1 nos Email : id not provided by customer . | Repair |  | 9- Service Validated | 2023-09-14 16:27 |  |  | 65 | INR | 65 | ENM POWER PRODUCTS
WO-11178568 |  | 2023-09-15 12:07 | 2023-09-02 |  | 2023-08-29 13:13 | TDAVQ | TDAVQ | TDAVQ | C21934001268 | PM | 2023-08-29 | 2023-08-30 18:39 | No | Contract | Army commanding Office | Army commanding Office Signal null | POHRUPET | 181221 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-18 18:44 |  |  | 730 | INR | 730 | ENM SECURE POWER
WO-11229308 | 103882351 | 2023-09-08 14:15 | 2023-09-08 |  | 2023-09-08 12:24 | Leonardo EV,DX,R22,EC Fan,TDAV0811A,Downflow Without Heater & Humidifier | TDAV0811AN001 | TDAV0811AN001 | C21613002542 | Low cooling issue Serial# C21613002542 P:Low cooling issue S:AMC | 2023-09-08 | 2023-09-10 13:53 | No | Contract | Reliance Jio Infocomm Ltd. | AG1 Metro Chinna Chowk | Kadapa | 516001 | Andhra Pradesh | India FS South1 Cooling CSP RK Cooling Enterprises Hyderabad | Kalakoti Manik_RK Cooling Enterprises Hyderabad | RK Cooling Enterprises | site observed cooling not coming replaced new filter drier n2 test done ok vacuumed and r22 gas charged 12 kgs now unit working fine | Repair |  | 8- Service Completed | 2023-09-11 13:59 |  |  | 300 | INR | 300 | ENM SECURE POWER
WO-11230212 | 103892066 | 2023-09-08 19:09 | 2023-09-08 |  | 2023-09-08 17:57 | GCR_NW_CB | GCR_NW_CB | GCR_NW_CB |  | Request to Visit Sch Engineer for inspection support. Please refer trail mail for approval and share WO number under inspection category. Product : NW63H14PEDO6.0H, SL:10231830799, Issue : Installation support . Customer : Power control Equipment Address: Address: 40A, Vaddarapalya, Jigani, Karnataka 562106 Contact Person: Mr.Srikanth, 9008987510, purchase@powercontrol.in | 2023-09-08 | 2023-09-15 07:57 | No | Warranty | Power Control Equipments Unit - 2 | Plot 40-A, 57 Vaddarapalya 1st Phase, 3rd Road, Jigani Industrial Area, | Bangalore | 562106 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Rajalingam P SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | As per customer request , we had visited and supported customer we observed micrologic and arc chutes found no trace of water, carried out secondary current injection also passed. contact resistance found ok. so we explained to customer to use breaker,there is no issues with our breaker. | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-15 07:59 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11178570 |  | 2023-09-15 12:10 | 2023-09-02 |  | 2023-08-29 13:13 | TDAVQ | TDAVQ | TDAVQ | C21934001269 | PM | 2023-08-29 | 2023-08-30 18:33 | No | Contract | Army commanding Office | Army commanding Office Signal null | POHRUPET | 181221 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-18 18:36 |  |  | 730 | INR | 730 | ENM SECURE POWER
WO-11229328 | 103882728 | 2023-09-08 13:47 | 2023-09-08 |  | 2023-09-08 12:35 | EFC 0.8TR, Downflow, Bottom Discharge | WDF0101BN001 | WDF0101BN001 | JK1341002970 | controller faulty Serial# JK1341002970 P:Controller faulty S:AMC | 2023-09-08 | 2023-09-09 04:00 | No | Contract | Reliance Corporate It Park Limited | S/O Sh Thakur Prasad | Hassanganj | 754250 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Karuna Tripathi Freezeotech Airconditioning & Refrigeration Lucknow | Freezeotech Airconditioning & Refrigeration Corporation | site visit found the running capacitor faulty now change the part unit is working ok | Repair |  | 10- Closed | 2023-09-11 11:18 |  |  | 40 | INR | 40 | ENM SECURE POWER
WO-11178619 |  | 2023-09-15 12:40 | 2023-09-02 |  | 2023-08-29 13:29 | TDAVQ | TDAVQ | TDAVQ | C21931007247 | PM | 2023-08-29 | 2023-09-05 17:49 | No | Contract | Army Commanding Office | Army Commanding Office signal null | Srinagar | 194104 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-20 17:54 |  |  | 780 | INR | 780 | ENM SECURE POWER
WO-11229329 | 103881203 | 2023-09-11 10:24 | 2023-09-08 |  | 2023-09-08 12:36 | WDF0181BN040-1 | WDF0181BN040-1 | WDF0181BN040-1 | JK2041002127 | Request for log of repair call Reliance Jio, Pipalwada Under AMC P: Temp sensor faulty. S:AMC | 2023-09-08 | 2023-09-09 12:00 | No | Contract | Reliance Jio Infocomm Ltd | Block/Revenue Survey No. 0 Gamtal/2, Khata No. 104, Mouje - Pipalwada, Taluka - Dolvan | Tapi | 394635 | Gujarat | India FS West2 Cooling CSP DECENT HVAC SYSTEM Gandhinagar | Mickey Kabrawala DECENT HVAC SYSTEM Gandhinagar | DECENT HVAC SYSTEM | Complaint attend, Temp. sensor and capacitor replaced. (> 240 Km) | Repair |  | 8- Service Completed | 2023-09-11 10:42 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 360 | INR | 360 | ENM SECURE POWER
WO-11178571 |  | 2023-09-15 12:11 | 2023-09-02 |  | 2023-08-29 13:13 | TDAVQ | TDAVQ | TDAVQ | C21935000944 | PM | 2023-08-29 | 2023-08-29 17:58 | No | Contract | Army commanding Office | Army commanding Office Signal null | P GALI | 192301 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-18 18:00 |  |  | 895 | INR | 895 | ENM SECURE POWER
WO-11234292 | 103823890 | 2023-09-09 14:04 | 2023-09-09 |  | 2023-09-09 12:45 | LC1F330 | LC1F330 | LC1F330 |  | As per the invoice, The Product(LX9FH2202) is in Warranty. Kindly arrange the site visit. Issue: Coil issue Address Power controls and switch gear pvt ltd Near OBC Bank Ambala Chandigarh road, Zirakpur Mohali 140603 Punjab India Contact person Details: - Mr.MD Amir 9872434088 | 2023-09-09 | 2023-09-09 15:56 | No | Warranty | Power controls and switch gear pvt ltd | Near OBC Bank Ambala Chandigarh road, Zirakpur null | Mohali | 140603 | Punjab | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Karnail Singh Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the coil found card burnt faulty ,but out of warranty from serial number. hence no replacement given to customer. Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-11 16:09 |  |  | 25 | INR | 25 | ENM POWER PRODUCTS
WO-11178576 |  | 2023-09-15 12:20 | 2023-09-02 |  | 2023-08-29 13:14 | PRODUCT UNIFLAIR LEONARDO DX EV TDAV0511A R407C DOWNFLOW WITH HEATER AND HUM WIT | TDAVQ | TDAVQ | C21934000827 | PM | 2023-08-29 | 2023-08-30 18:27 | No | Commercial Action - Sales | Army commanding Office | Army commanding Office Signal null | KARGIL | 194103 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-18 18:30 |  |  | 570 | INR | 570 | ENM SECURE POWER
WO-11234304 | 103881556 | 2023-09-09 14:38 | 2023-09-09 |  | 2023-09-09 12:59 | LC1D18M7 | LC1D18M7 | LC1D18M7 |  | As per the invoice, The Product is in Warranty. Kindly arrange the site visit. Issue: pole open issue Address Nahal Steeling Mills Nahar Complex Chandigarh Ambala Road Village Lehali Dappar Post Office Mohali 140103 Punjab India Contact person Details: - Mr.Sanjay sharma 9855128701 | 2023-09-09 | 2023-09-11 17:01 | No | Warranty | Nahal Steeling Mills Pvt | Nahar Complex Chandigarh Ambala Road Village Lehali Dappar Post Office | Mohali | 140103 | Punjab | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Karnail Singh Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the contactor found working ok. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-11 17:50 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11178578 |  | 2023-09-15 12:38 | 2023-09-02 |  | 2023-08-29 13:14 | TDAVQ | TDAVQ | TDAVQ | C21935001269 | PM | 2023-08-29 | 2023-09-03 17:41 | No | Contract | Army commanding Office | Army commanding Office Signal null | LEH | 194101 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-20 17:44 |  |  | 940 | INR | 940 | ENM SECURE POWER
WO-11178575 |  | 2023-09-15 12:18 | 2023-09-02 |  | 2023-08-29 13:14 | TDAVQ | TDAVQ | TDAVQ | C21934000826 | PM | 2023-08-29 | 2023-08-30 18:21 | No | Contract | Army commanding Office | Army commanding Office Signal null | KARGIL | 194103 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-18 18:25 |  |  | 570 | INR | 570 | ENM SECURE POWER
WO-11229451 | 103884392 | 2023-09-08 17:22 | 2023-09-08 |  | 2023-09-08 13:20 | SURT6000XLI-CC | SURT6000XLI-CC | SURT6000XLI-CC | B21831002349 | FW: RR : IM15446659 ¦ Store Code : TR09 ¦ SCHNEIDER ¦ TELANGANA -TRENDS Under AMC P: UPS BACKUP Issue S:AMC | 2023-09-08 | 2023-09-09 15:55 | No | Contract | Reliance Retail Limited | RRL TST Vikarabad, Alampally Road, Alampally | Vikarabad | 501102 | Telangana | India FS South3 HBN CSP CENTRALDATASYSTEMS HYDERABAD | B Ramakrishna CENTRALDATASYSTEMS HYDERABAD | Central Data Systems Pvt Ltd | Visited site and found battery issue informed to customer to replace battery | Repair |  | 10- Closed | 2023-09-09 16:18 |  |  | 85 | INR | 85 | ENM SECURE POWER
WO-11234331 | 103909527 | 2023-09-09 17:01 | 2023-09-09 | Product found in transit Damaged | 2023-09-09 13:44 | LDF36400U33X | LDF36400U33X | LDF36400U33X |  | MCCB FOUND DAMAGE - LDF36400U33XAAUNM (refer attached image) We received Damage MCCB from your side in last supply For the details please see the attachment Found Acrlic cover fiting element damage | 2023-09-09 | 2023-09-09 17:09 | No | Warranty | UNI-TECH AUTOMATION PRIVATE LIMITED | S No 79/2 Plot No 7 Shiva | Pune | 411021 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Samadhan S_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the MCCB with coupled Motor mechanism found in transit Damaged. checked motor mechanism upper acrylic holding knob found damaged in transit. this problem is not repairable. So it's needs to be replaced. Required Material : Motor Mechanism ( Power pact Square D) | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-12 11:51 |  |  | 65 | INR | 65 | ENM POWER PRODUCTS
WO-11178577 |  | 2023-09-15 12:24 | 2023-09-02 |  | 2023-08-29 13:14 | TDAVQ | TDAVQ | TDAVQ | C21934001250 | PM | 2023-08-29 | 2023-09-03 17:30 | No | Contract | Army commanding Office | Army commanding Office Signal null | LEH | 194101 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-20 17:33 |  |  | 940 | INR | 940 | ENM SECURE POWER
WO-11229488 | 103884892 | 2023-09-08 13:40 | 2023-09-08 |  | 2023-09-08 13:35 | APC SYMMETRA RM 6KVA N+1 FRAME 220-240V EXCLUDING RAIL KIT | SYHF6KI-D | SYHF6KI-D | JD0828002226 | FW: OR-ANG-01 Back up issue Site code: OR-ANG-01 Back up issue Serial# JD0828002226 P: Back up issue S:AMC | 2023-09-08 | 2023-09-13 10:51 | No | Contract | Central Board of Excise & Customs-CBEC | Beside BSNL Office Nalco Nagar Office of the superintendent , GST Tax Angul 4&5 range FCI Chowk Nalconagar | Angul | 759125 | Odisha | India FS East HBN CSP Disha Computers Bhubneshwar | TARUN PARIDA_Disha Computers Bhubneshwar | Disha Computers-Bhubaneshwar | REPLACED BATTERY MODULE NOW UPS OK & WORKING SYBT2 5D2324T15459/5D2324T15467 | Repair |  | 10- Closed | 2023-09-14 09:54 |  |  | 150 | INR | 150 | ENM SECURE POWER
WO-11178617 |  | 2023-09-15 12:42 | 2023-09-02 |  | 2023-08-29 13:29 | TDAVQ | TDAVQ | TDAVQ | C21931010873 | PM | 2023-08-29 | 2023-09-05 17:57 | No | Contract | Army Commanding Office | Army Commanding Office signal null | Srinagar | 194104 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-20 18:01 |  |  | 780 | INR | 780 | ENM SECURE POWER
WO-11229608 | 103885808 | 2023-09-12 23:04 | 2023-09-08 |  | 2023-09-08 14:11 | WDF0181BN003 | WDF0181BN003 | WDF0181BN003 | C21716001241 | FW: Capacitor and Damper Motor faulty 2nd PAC of NLD AG1 HTKL-ENB-9012 Under AMC P:Damper Motor issue--C21716001241 S:AMC | 2023-09-08 | 2023-09-12 23:08 | No | Contract | Reliance jio infocomm Ltd | MR.BHIMRAO KERBA PATKURE PAWAR,GAT NO-536,OPP.LOKMAT OFFICE,AT/POST-TOP,TAL-HATKANANGALE | Kolhapur | 416122 | Maharashtra | India FS West2 Cooling CSP Unitec Engineers Pune | Onkar Deshmukh Unitec Engineers Pune | Unitec Engineers | Damper motor replacement done. | Repair |  | 8- Service Completed | 2023-09-12 23:08 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 45 | INR | 45 | ENM SECURE POWER
WO-11234374 | 103830198 | 2023-09-10 17:35 | 2023-09-11 |  | 2023-09-09 15:16 | LC1E65M7 | LC1E65M7 | LC1E65M7 |  | As per the invoice, The Product is in Warranty. Kindly arrange the site visit. Issue: pole open issue Address KVR Industries SY No 103/D/7/3/2,Muthagudem to Lanka Sagar Chinthagudem Penuballi Mandal Khammam 507302 Telangana India Contact person Details: - Mr.Anil 8309519529 | 2023-09-09 | 2023-09-13 12:00 | No | Warranty | KVR Industries | SY No 103/D/7/3/2,Muthagudem to Lanka Sagar Chinthagudem Penuballi Mandal null | Khammam | 507302 | Telangana | India FS ED&I CSP South Team Sumanth Electrical Services Hyderabad | Basanth Reddy_SUMANTH ELECTRICAL SERVICES HYDERABAD | Sumanth Electrical Services | Visited KVR Industries Rice Mills Site at Khammam Dist and inspected Schneider Electric LC1E80M7 and LC1E50M7 and LC1E40M7 and LAETSD Power Contactors are Damaged and Melted at L1 L2 L3 Termination Point Terminal Got Burnt Out we have replaced with new contactors and we have replaced as a special case and complaint is closed we have collected faulty contactors for RTS to ASC CSP | Repair |  | 9- Service Validated | 2023-09-13 16:32 |  |  | 250 | INR | 250 | ENM POWER PRODUCTS
WO-11178620 |  | 2023-09-15 12:45 | 2023-09-02 |  | 2023-08-29 13:29 | TDAVQ | TDAVQ | TDAVQ | C21931010878 | PM | 2023-08-29 | 2023-09-06 16:31 | No | Contract | Army commanding Office | Army commanding Office Signal null | DAYALACHAK | 180001 | Jammu and Kashmir | India FS North2 Cooling CSP S & S Computers_Jammu | Baitulah Ahmad_S & S Computers_Jammu | S & S Computer Services | PM Done Clean air filter indoor and outdoor units then checked all electrical connections and parameters properly, tested ok. PAC working fine. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-21 16:35 |  |  | 745 | INR | 745 | ENM SECURE POWER
WO-11234438 | 103910976 | 2023-09-11 11:17 | 2023-09-11 |  | 2023-09-09 17:49 | LC1G265KUEN | LC1G265KUEN | LC1G265KUEN | LJ22222700100073 | As per the Sr no, The Product is in Warranty. Kindly arrange the site visit. Issue: Coil issue Address PCBL (TN) Limited (Chennai _ EPC) No A-7, SIPCOT Industrial Park, Thervoy Kandigai, Gummidipoondi Taluk, Tiruvallur 601202 Tamil Nadu India Contact person Details: - Mr.Satyendra 8980041962 | 2023-09-09 | 2023-09-15 17:00 | No | Warranty | PCBL (TN) Limited (Chennai _ EPC) | No A-7, SIPCOT Industrial Park, Thervoy Kandigai, Gummidipoondi Taluk, | Tiruvallur | 601202 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Visited Done | Repair |  | 9- Service Validated | 2023-09-15 17:25 |  |  | 65 | INR | 65 | ENM POWER PRODUCTS
WO-11229648 | 103886931 | 2023-09-08 15:38 | 2023-09-08 |  | 2023-09-08 14:30 | LEONARDO EV,DX,R22,EC FAN,( HCM109-DANFOSS ), DOWNFLOW WITHOUT HEATER & HUMIDIFI | TDAV0811AN005 | TDAV0811AN005 | ZK1602019894 | Under AMC P:Compressor issue--zk1602019894 S:AMC | 2023-09-08 | 2023-09-10 06:30 | No | Contract | RELIANCE JIO INFOCOMM LIMITED | Shashi Jaiswal, S A 15/12E | Varanasi | 221001 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Harinder Yadav Freezeotech Airconditioning & Refrigeration Lucknow | Freezeotech Airconditioning & Refrigeration Corporation | compressor faulty now change the compressor n2 testing and vacuumed R-22 gas 14 kg charge unit is working ok | Repair |  | 10- Closed | 2023-09-14 23:14 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 313 | INR | 313 | ENM SECURE POWER
WO-11239958 | 103909533 | 2023-09-11 16:05 | 2023-09-11 |  | 2023-09-11 09:30 | NA04004V | NA04004V | NA04004V |  | Service form no 31 AARAV FRAGRANCES AND FLAVORS PVT. LTD C 61, TTC Industrial Area, MIDC , Road No. RC1, Thane Belapur road, Vill.: Pawane, Post : Turbhe, Navi Mumbai, Maharashtra 400705 Prashant Patil 8879524085 WATSN 400A ATS MSEB INPUT SUPPLY LED Is continuously blinking And the operation of ATS is happening in AUTO Mode 23184390050 DIPSY TRADERS DISTRIBUTOR SEI--11/7/2023 NA04004V | 2023-09-11 | 2023-09-13 11:07 | No | Warranty | AARAV FRAGRANCES & FIAVOURS LTD. | PLOT NO. C-61, TTC, MIDC AREA, RC-1,,THANE BELAPUR ROAD, PAWANE null | Navi Mumbai | 400705 | Maharashtra | India FS ED&I CSP West Team R P Electrical Mumbai | Sunil Jadhav R P Electrical Mumbai | R P Electrical | Checked 400A WATSN ATS found physically in good condition. ATS S1 over voltage 280V setting set. ATS Electrical Operation not checked found shut down is not given. Customer ATS is installed upside down. | Repair |  | 9- Service Validated | 2023-09-14 11:15 |  |  | 44 | INR | 44 | ENM POWER PRODUCTS
WO-11229845 | 103888943 | 2023-09-08 17:24 | 2023-09-08 |  | 2023-09-08 15:47 | XRAF6422A | XRAF6422A | XRAF6422A | SRF032906 | FW: Chiller-4 HP Alarm P:Chiller HP Alarm S:AMC | 2023-09-08 | 2023-09-09 04:30 | No | Contract | Yotta Infrastructure | PLOT NO 7, SECTOR KNOWLEDGE PARK V Tusiana Village, Gautam Buddha Nagar | Greater Noida | 201301 | Uttar Pradesh | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Mohd. Shadab Freezeotech Airconditioning & Refrigeration GZB | Freezeotech Airconditioning & Refrigeration Corporation | high condenser pressure alarm found the sensore we have reconnect check all parameter unit is working ok | Repair |  | 10- Closed | 2023-09-08 21:25 |  |  | 28 | INR | 28 | ENM SECURE POWER
WO-11241347 | 103879633 | 2023-09-11 17:55 | 2023-09-12 |  | 2023-09-11 12:12 | GCR_LV_APFC | GCR_LV_APFC | GCR_LV_APFC |  | As per the invoice, The Product is in Warranty. Kindly arrange the site visit. Issue: Fan defect alram Address MRF ARAKONAM Arakonam, Thirittani road, Ichiputhur VELLORE 631003 Tamil Nadu India Contact person Details: - Mr.Sunil 7502775939 | 2023-09-11 | 2023-09-12 18:30 | No | Warranty | MRF ARAKONAM | Arakonam, Thirittani road, Ichiputhur null | VELLORE | 631003 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Site Visit Done | Repair |  | 9- Service Validated | 2023-09-12 20:34 |  |  | 85 | INR | 85 | ENM POWER PRODUCTS
WO-11229902 | 103889164 | 2023-09-09 10:32 | 2023-09-11 |  | 2023-09-08 16:12 | APC SYMMETRA RM 6KVA N+1 FRAME 220-240V EXCLUDING RAIL KIT | SYHF6KI-D | SYHF6KI-D | JD0925008159 | RE: breakdown call required WO11095683 Under AMC P:MIMs Not working S:AMC | 2023-09-08 | 2023-09-11 15:39 | No | Contract | Central Board of Excise & Customs-CBEC | Mid Town Chamber Club Road | Ranchi | 834001 | Jharkhand | India FS East HBN CSP Power Solution Ranchi | KAMRANUL HAQUE_Power Solution Ranchi | Power Solution-Ranchi | SYRIM SYMIM AND SYPM2KU REPLACED UNIT IS WORKING OK CALL HAS BEEN CLOSED | Repair |  | 10- Closed | 2023-09-11 16:47 |  |  | 5 | INR | 5 | ENM SECURE POWER
WO-11229931 | 103890303 | 2023-09-08 16:48 | 2023-09-08 |  | 2023-09-08 16:20 | SURT6000XLI-CC | SURT6000XLI-CC | SURT6000XLI-CC | B21930001584 | FW: RR : IM15448383 ¦ Store Code : TH76 ¦ SCHNEIDER ¦ UTTAR PRADESH -JEWELLERY Under AMC P: UPS BACKUP Issue S:AMC | 2023-09-08 | 2023-09-09 14:09 | No | Contract | Reliance Retail Ltd(JEWELLERY) | Reliance Jewels 97/18A, Elite Allahabad Bank Road | Jhansi | 284001 | Uttar Pradesh | India FS North2 HBN CSP MUKUL COMPUTERS Agra | Faizan F_Mukul Computers Agra | MUKUL COMPUTERS - AGRA - LUCKNOW | battery faulty cx side ups working in mains mode . | Repair |  | 10- Closed | 2023-09-11 18:29 |  |  | 250 | INR | 250 | ENM SECURE POWER
WO-11241631 | 103921478 | 2023-09-11 16:19 | 2023-09-11 | NA | 2023-09-11 14:04 | MVS32N4NW6L | MVS32N4NW6L | MVS32N4NW6L | 10221640004 | Please give the complaint no Customer - Croda India Company Pvt. Ltd Address - TTC Industrial Area, Kopar khairane, Navi Mumbai - 400705 Contact Person - Sanjay Chikhalikar Contact No. - 9867223848 Equipment Details -MVS32N4NW6L Equipment Sr. No. - 10221640004 Problem Reported - ACB MVS32N4NW6L is overheated on a 50% load | 2023-09-11 | 2023-09-11 16:28 | No | Warranty | Croda India Company | Plot No 1/1 Part, TTC Industrial Area, Thane Belapur Road Koper Khairne | Navi Mumbai | 400710 | Maharashtra | India FS ED&I CSP West Team East India Power Engineers Mumbai | Sandeep Ingavale East India Power engineers Mumbai | East India Power Engineers (5043) | Visited the site & checked the breaker & main arcing contact and found ok. Checked the cluster contact & breaker terminal contact found ok. The heating cause is obtained due to not standard nut bolt issue in the busbar fittin on the chassis. | Repair |  | 8- Service Completed | 2023-09-14 16:12 | =S= Consig Fill up 226042685 |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11229971 | 103890498 | 2023-09-08 17:55 | 2023-09-08 |  | 2023-09-08 16:32 | APC Easy UPS Online 6000VA Indian Outlet Rackmount 230V India | SRV6KL-IN | SRV6KL-IN | 9S2148A00196 | FW: RR : IM15403902 ¦ Store Code :TDT0 ¦ SCHNEIDER ¦ PUNJAB -TRENDS Under AMC P: UPS BACKUP Issue S:AMC | 2023-09-08 | 2023-09-09 08:34 | No | Contract | Reliance Retail Limited | SCO-1 & 2, PWD Rest House Market, Tehsil Khanna | Ludhiana | 141401 | Punjab | India FS North2 HBN CSP Essar Engineers Chandigarh | Vishal Chauhan Essar Engineers Chandigarh | Essar Engineers | Checked the UPS SRV5KL-IN , 9S2326A0198N and found UPS working normal .Now UPS tested on load its working normal . | Repair |  | 10- Closed | 2023-09-09 08:44 |  |  | 110 | INR | 110 | ENM SECURE POWER
WO-11241643 | 103921751 | 2023-09-11 15:37 | 2023-09-11 |  | 2023-09-11 14:11 | METSEEM6436HCL10RS | METSEEM6436HCL10RS | METSEEM6436HCL10RS |  | Name of Customer A.T.E. ENTERPRISES PRIVATE LIMITED Site Address Survey No: 251,Village - Sari Sarkhej Bavla Highway (NH No: 8A), "Taluka: Sanand Ahmedabad, 382220" Name of contact person at site:-Yagnik Contact Phone / Mob. No:-7227899615.00 Defective product details:-XB7EV08BP(1 QTY),GVAED101(1 QTY),METSEEM6436HL05RS(1 QTY) Invoice no.:-PSI/23000950(24/04/2023) Nature of Defect:-Not getting on, NO NC not working | 2023-09-11 | 2023-09-18 13:03 | No | Warranty | ATE Enterprise Pvt Ltd | Near Sari Gam Opp Gallops Industrial Park Ahmedabad Bavla Highway Ahmedabad 251 252 | Ahmedabad | 382220 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Mistri Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physically observed ok. METSEEM6436HCL05RS SR NO : 010623 observed ok. according to customer rs485 communication not working so we carry for further action at our asc. RXM2LB2P7 SR NO : 8A 2022 W16 6J X 230 vac observed physcially ok but no nc not getting changed. so give free replacement. XB5AS542N 102147 04 Nos observed ok but push button not working so free replacement. GVAE11 SR NO : PK22513B obsreved ok but nc no not working so free replacemnet. ZBV M3N SR NO : 1022417 02 Nos ok but not wokring so free replacemnt. ZBR102N SR NO :102248 - 02 obsreved ok but not working found so give free replacement. XB7 EV048BPN SR NO : 102249 03 Nos observed physically observed ok but not woring so free replacemnet | Repair |  | 9- Service Validated | 2023-09-18 13:04 | =S= Consig Fill up 226060589 |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11242007 | 103924918 | 2023-09-11 18:18 | 2023-09-11 |  | 2023-09-11 16:54 | LV540308 | LV540308 | LV540308 |  | As per the invoice, The Product is in Warranty. Kindly arrange the site visit. Issue: Hardware issue Address TSRTC Cantonment Bus Depot Gandhi Nagar, Nehru Nagar Colony, West Marredpally Secunderabad 500026 Telangana India Contact person Details: - Mr.Siva 9573875706 | 2023-09-11 | 2023-09-12 12:00 | No | Warranty | TSRTC Cantonment Bus Depot | Gandhi Nagar, Nehru Nagar Colony, West Marredpally | Secunderabad | 500026 | Telangana | India FS ED&I CSP South Team Sumanth Electrical Services Hyderabad | Venkata Prasad_SUMANTH ELECTRICAL SERVICES HYDERABAD | Sumanth Electrical Services | We have visited TSRTC Cantonment Bus Depot Mega Engg Site and we have inspected Schneider Electric LV540308 MCCB and in our observation we found MX Trip Coil to Main Mechanism Miss match and we have rectified the problem and complaint is closed | Repair |  | 9- Service Validated | 2023-09-12 19:17 |  |  | 10 | INR | 10 | ENM POWER PRODUCTS
WO-11229994 | 103890859 | 2023-09-08 18:41 | 2023-09-08 |  | 2023-09-08 16:41 | APC Symmetra RM 4kVA Scalable to 6kVA N+1 220-240V | SYH4K6RMI | SYH4K6RMI | JD0831011166 | FW: WO-11095713 CBEC BR/DAL/ 01 PM Under AMC P: ups is dead S:AMC | 2023-09-08 | 2023-09-12 13:38 | No | Contract | Central Board of Excise & Customs-CBEC | 3rd Floor, Shri Balajee Complex, Near Raj Colony, Old GT Road, Sasaram | Rohtas | 821115 | Bihar | India FS East HBN CSP Ascent Technology Patna | Md Kalam_Ascent Technology Patna | Ascent Technology - PATNA-KOLKATA | pcb and battery replaced ups is working fine 0J-0P8843/0J-0P8842/RBC44-IN "570944AD23794825/5788429916953818/B22305020840 B22305020839" | Repair |  | 10- Closed | 2023-09-12 13:40 |  |  | 232 | INR | 232 | ENM SECURE POWER
WO-11245363 | 103952591 | 2023-09-12 11:42 | 2023-09-12 |  | 2023-09-12 10:26 | LC1E50M7 | LC1E50M7 | LC1E50M7 |  | LC1E50M7 , Coil LAEX3M7 Sr No : WH2241 Coil Not working Biswas Trading Co. 125/42, Near Sunview Hotel Mahatma Gandhi Road Dalhousie Himachal Pradesh PIN 176304 Mr Jatin Sharma 8360194147 LC1E50M7 , Coil LAEX3M7 Sr No : WH2241 Coil Not working | 2023-09-12 | 2023-09-12 11:45 | No | Warranty | Biswas Trading Co | 125/42, Near Sunview Hotel Mahatma Gandhi Road | Dalhousie | 176304 | Himachal Pradesh | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Rakesh Kumar Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the contactor found coil burnt and mcb found MCB found phase missing & dolly free. Hence faulty replaced. LAEX3M7 - 1 Nos. LX1FH2202 - 1 Nos. EZ9F21263 - 2 Nos. email : jatsharma1@rediffmail.com | Repair |  | 9- Service Validated | 2023-09-12 13:45 |  |  | 315 | INR | 315 | ENM POWER PRODUCTS
WO-11230033 | 103891157 | 2023-09-08 17:24 | 2023-09-08 |  | 2023-09-08 16:51 | APC Smart-UPS RT 10000VA 230V Harsh Environment | SURT10000XLI | SURT10000XLI | B21510000490 | FW: RR : IM15443142 ¦ Store Code : 1924 ¦ SCHNEIDER ¦ TELANGANA -TRENDS Under AMC P: UPS not powering on S:AMC | 2023-09-08 | 2023-09-11 18:58 | No | Contract | Reliance Retail Ltd | L&T Mall Punjagutta, Sy No:1/1, Ward No: 89, Block E, Khairthabad Village | Hyderabad | 500082 | Telangana | India FS South3 HBN CSP CENTRALDATASYSTEMS HYDERABAD | Nagesh CENTRALDATASYSTEMS HYDERABAD | Central Data Systems Pvt Ltd | Fan replacement done ups working normal | Repair |  | 10- Closed | 2023-09-11 19:08 |  |  | 13 | INR | 13 | ENM SECURE POWER
WO-11245888 | 103952749 | 2023-09-12 10:51 | 2023-09-12 |  | 2023-09-12 10:46 | MEHVCHDY250A44PB | MEHVCHDY250A44PB | MEHVCHDY250A44PB |  | Re: WO-11093865 from Schneider Electric Model : MEHVCHDY250A44PB--10-15 nos ME-N0273813 No supply Site : New Standard Electrical, Plot No 192, Opp Reliance Petrol Pump, Meghtar, Anjar, Kutch 370110 Mr.Parth : 9510154300 | 2023-09-12 | 2023-09-12 14:37 | No | Warranty | New standard electrical | Plot no 192 opposit reliance petrol pump Meghpar anjar | kutch | 370110 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | Jayesh J_JKS Rajkot | JKS Engineering Co. | check cap 8 nos cap psd open so as per marketing approval giving replacement 8 nos | Repair |  | 9- Service Validated | 2023-09-12 20:27 | =S= Consig Fill up 226023088 |  | 220 | INR | 220 | ENM POWER PRODUCTS
WO-11230060 | 103891384 | 2023-09-08 17:50 | 2023-09-08 |  | 2023-09-08 16:59 | SURT6000XLI-CC | SURT6000XLI-CC | SURT6000XLI-CC | B21747025141 | FW: RR : IM15385943 ¦ Store Code :TI57 ¦ SCHNEIDER ¦ TAMIL NADU -FRESH Under AMC P: UPS BACKUP Issue S:AMC | 2023-09-08 | 2023-09-11 12:01 | No | Contract | RRL Fresh Ltd | No.HIG 42 & 43, Maraimalainagar NH 1 GST Road | Chennai | 603209 | Tamil Nadu | India FS South2 HBN CSP_Soundry Power System Chennai | SaravananMano SoundryPowerSystems Chennai | Soundry Power Systems-Chennai | BATTERY ISSUES. | Repair |  | 10- Closed | 2023-09-11 12:06 |  |  | 40 | INR | 40 | ENM SECURE POWER
WO-11246913 | 103954345 | 2023-09-12 12:27 | 2023-09-12 | coil Suppressor Module Installed on Contactor coil | 2023-09-12 12:03 | LC1D1506M7 | LC1D1506M7 | LC1D1506M7 |  | Please Issue Complaint No . Name of Customer: CRAFTSMAN AUTOMATION LTD PUNE UNIT 4 2. Site Address: - GAT No. / Hissa No. 137/2, 138/2 & 136/1 Sanaswadi Village, Shirur Taluka 412208 PUNE 3. Name of contact person at site :-Mr. Naren Magar 4. Contact Phone / Mob No. : 8308471217 5. Defective product details:- LC1D1506M7 6. Product Make:-Schneider Electric 7. Nature of Defect: Contactor Not Switching 8. Shutdown availability if applicable :nil 9. Serial No: or DOM of the product- PK23035 | 2023-09-12 | 2023-09-12 12:32 | No | Warranty | Craftsman Automation Pvt. Ltd.-UNIT-2 | GAT No.-137, Hissa No.-2, Sanaswadi Village, Shirur Taluk, | Pune | 412208 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Sachin Jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked and we installed the coil Suppressor Module Installed on Contactor coil machine no - 133, 197, 178, H500. We make connection of coil Suppressor Properly & then we Switching Operation found ok. | Repair |  | 9- Service Validated | 2023-09-12 12:49 |  |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11230614 | 103894708 | 2023-09-08 19:30 | 2023-09-08 |  | 2023-09-08 18:44 | WDF0181BN040-1 | WDF0181BN040-1 | WDF0181BN040-1 | JK21052002144 | IN-Warranty P:Low cooling S:Onsite | 2023-09-08 | 2023-09-09 19:50 | No | Warranty | Reliance JIO Info COMM | Block Development Office, Pandabeswar Development Block,near DVC More,PO Pandabeswar | Bardhaman | 713346 | West Bengal | India FS East Cooling CSP Snow Point Kolkata | Laxmikant Dhang_Snow Point Kolkata | Snow Point | OVER VOLTAGE ISSUE AT SITE.CONDENSER COILAND FILTER DIRTY.CONDENSER COIL AND FULTER.CLEAN.ALL PARAMETER CHECKED.MACHINE OK RUNNING. | Repair |  | 10- Closed | 2023-09-10 07:59 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 190 | INR | 190 | ENM SECURE POWER
WO-11247922 | 103955907 | 2023-09-15 17:28 | 2023-09-12 |  | 2023-09-12 16:25 | LC1D65F7 | LC1D65F7 | LC1D65F7 | 8B23184 | As per the Sr. no, The Product is in Warranty. Kindly arrange the site visit. Issue: pole open issue Address OVT India Private Ltd C-45, Sector 57 Rd, Block C, Sector 57, Noida GAUTAM BUDDHA NAGAR 201301 Uttar Pradesh India Contact person Details: - Mr.Amit 8010678453 | 2023-09-12 | 2023-09-14 17:29 | No | Warranty | OVT India Private Ltd | C-45, Sector 57 Rd, Block C, Sector 57, Noida | GAUTAM BUDDHA NAGAR | 201301 | Uttar Pradesh | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the contactor found coil burnt due to abnormal , Hence no replacement. Email : id not provided by customer. | Repair |  | 9- Service Validated | 2023-09-15 17:33 |  |  | 65 | INR | 65 | ENM POWER PRODUCTS
WO-11230978 | 103894890 | 2023-09-08 19:14 | 2023-09-08 |  | 2023-09-08 18:51 | APC Smart-UPS RT 10000VA 230V Harsh Environment | SURT10000XLI-CC | SURT10000XLI-CC | B21511001908 | FW: Ups not working_B21511001908_IM13384018_JC_MTRI_01 Under AMC P: Ups not working S:AMC | 2023-09-08 | 2023-09-11 14:19 | No | Contract | Reliance Corporate It Park Limited | Asha Complex, SH 54 Mathiyadih Dhaka Road | Motihari | 845401 | Bihar | India FS East HBN CSP Aman International Muzaffarpur | Shubham_Aman International Muzaffarpur | Aman International-Muzaffarpur | UPS Working good ON mains Problem in battery RBC44-IN 3 set | Repair |  | 10- Closed | 2023-09-11 14:37 |  |  | 89 | INR | 89 | ENM SECURE POWER
WO-11248098 | 103967204 | 2023-09-14 12:18 | 2023-09-12 |  | 2023-09-12 17:32 | GCR_NSX | GCR_NSX | GCR_NSX |  | As per the invoice, The Product(Motor Mechanism) is in Warranty. Kindly arrange the site visit. Issue: Motor mechanism issue Address Tricolite Electrical Industries Limited Site-IV Plot No- 18/1-A, Industrial Area Sahibabad 201010 Uttar Pradesh India Contact person Details: - Mr.Dinesh 9463622232 | 2023-09-12 | 2023-09-14 13:28 | No | Warranty | Tricolite Electrical Industries Limited Site-IV. | Plot No- 18/1-A, Industrial Area | Sahibabad | 201010 | Uttar Pradesh | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the MT found not mechanism working , Hence faulty replaced. LV432641 - 1 nos Email : dinesh.kumar@tricolite.com | Repair |  | 9- Service Validated | 2023-09-14 16:11 |  |  | 52 | INR | 52 | ENM POWER PRODUCTS
WO-11249028 | 103957082 | 2023-09-12 23:27 | 2023-09-12 |  | 2023-09-12 19:14 | 30002385 | 30002385 | 30002385 | 54230460814 | As per the Sr. no, The Product is in Warranty. Kindly arrange the site visit. Issue: Display issue Address Adarsha Control & Automation Pvt. Ltd. A -274, 6th Main, 2nd Stage, Peenya Industrial Area Bengaluru 560058 Karnataka India Contact person Details: - Mr.Thirtha 8971485345 | 2023-09-12 | 2023-09-13 13:30 | No | Warranty | Adarsha Control & Automation Pvt. Ltd.- 9833 | A -274, 6th Main, 2nd Stage, Peenya Industrial Area | Bengaluru | 560058 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | C Gunasekaran_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported 3phase ammeter the problem found was y phase reading not coming due to internal issue. So we had arranged for the replacement to the customer from our stock. after replacing found working ok. | Repair |  | 9- Service Validated | 2023-09-14 09:22 | Hi Team, Material booked zfre Zvo : 226052058 |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11249045 | 103963207 | 2023-09-13 11:29 | 2023-09-12 |  | 2023-09-12 19:22 | LV525333 | LV525333 | LV525333 |  | As per the invoice, The Product is in Warranty. Kindly arrange the site visit. Issue: tripping issue Address Bhagirath Quarry Works Unit-1, Nr. Railway Crossing, At. Tulsigam, Ta. Savli Baroda 388710 Gujarat India Contact person Details: - Mr.Santosh 9879770733 | 2023-09-12 | 2023-09-14 12:23 | No | Warranty | Bhagirath Quarry Works | Unit-1, Nr. Railway Crossing, At. Tulsigam, Ta. Savli | Baroda | 388710 | Gujarat | India FS ED&I CSP West Team Jay Services Vadodara | Ghanshyam Kachiya_Jay Services Vadodara | Jay Services | We visited at site & checked MCCB ON position with load & Not trip last 2 hours MCCB set 250 Amp. MCCB used in 125 HP star Delta feeder incommer. Measure load R-102A, Y-92A, B-91. 8 A. It is incerese & decrease as per material quality. Checked I/C cable 70 sq alu with alu lugs. Measure MCCB terminal Temp R-36c, Y-36 c, B-35. 9c. Measure MCCB spredor & lugs connection Temp R-36c, Y-37c, B-38c. Measure cable lugs crimping temp R-36.6c, Y-40. 8c, B-39.1c. Measure top side cable termination temp w/o spredor R-40c, Y-37 c, B-37c. Measure voltage RY-393. 6v, YB-384. 5v, RB-399 volt. Customer replace cable end lugs before our visit. Now working ok. We suggest to be mount spredor top side terminal. | Repair |  | 9- Service Validated | 2023-09-14 12:25 |  |  | 74 | INR | 74 | ENM POWER PRODUCTS
WO-11252913 | 103991557 | 2023-09-14 14:49 | 2023-09-13 |  | 2023-09-13 11:10 | LRD16 | LRD16 | LRD16 |  | As per the invoice, The Product is in Warranty. Kindly arrange the site visit. Issue: pole open issue Address Basic Automation Solution Pvt. Ltd. Plot No.-289, 16/2, Phase-1, Mathura Road Faridabad 121002 Haryana India Contact person Details: - Mr.Feroz 9891176284 | 2023-09-13 | 2023-09-13 14:51 | No | Warranty | Basic Automation Solution Pvt. Ltd. | Plot No.-289, 16/2, Phase-1, Mathura Road | Faridabad | 121002 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the relay found damage / not working, Hence no replacement given to customer. Email : id not provided by customer . | Repair |  | 9- Service Validated | 2023-09-14 14:56 |  |  | 52 | INR | 52 | ENM POWER PRODUCTS
WO-11252972 | 103990086 | 2023-09-14 14:23 | 2023-09-13 |  | 2023-09-13 11:35 | GCR_MVS | GCR_MVS | GCR_MVS |  | Fwd: SHREE RUPANADHAM STEEL (P) LTD, Raigarh, CG- ACB CALL PART REFERENCE :- MVS20N4MWL QTY.:- 1NOS. SHIPMENT ADDRESS : SHREE RUPANADHAM STEEL PRIVATE LIMITED VILL: SARAIPALI, POST: GERWANI, RAIGARH,RAIGARH,CHHATTISGARH,INDIA WO-11221513 SHREE RUPANADHAM STEEL (P) LTD Customer Confirmed Shutdown for pending work. Please generate new case & WO. | 2023-09-13 | 2023-09-16 12:00 | No | Warranty | SHREE RUPANADHAM STEEL (P) LTD | VILL- SARAIPALI, GERWANI RAIGARH | RAIGARH | 496001 | chhattisgarh | India FS ED&I CSP East Team SOMDEV & COMPANY RAIPUR | SOUMYA BEHERA_SOMDEV & COMPANY RAIPUR | Somdev & Company | the chasis is replaced now we are closing the complaint. | Repair |  | 9- Service Validated | 2023-09-16 10:28 |  |  | 287 | INR | 287 | ENM POWER PRODUCTS
WO-11254005 | 103994149 | 2023-09-15 14:46 | 2023-09-13 |  | 2023-09-13 18:07 | C10N6TM100 | C10N6TM100 | C10N6TM100 |  | As per the invoice, The Product is in Warranty. Kindly arrange the site visit. Issue: pole open issue Address Reshmi Electrical A1/205-206, Sector-17, Kavinagar Industrial Area, Swadeshi Compound Ghaziabad 201010 Uttar Pradesh India Contact person Details: - Mr.Vivek 9918467466 | 2023-09-13 | 2023-09-15 14:49 | No | Warranty | Reshmi Electrical | A1/205-206, Sector-17, Kavinagar Industrial Area, Swadeshi Compound null | Ghaziabad | 201010 | Uttar Pradesh | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mccb found R phase burnt due to overheating, Hence no replacement given to customer. Email : id not provided by customer . | Repair |  | 9- Service Validated | 2023-09-15 16:53 |  |  | 52 | INR | 52 | ENM POWER PRODUCTS
WO-11254923 | 104001108 | 2023-09-14 11:40 | 2023-09-14 |  | 2023-09-13 19:16 | LRE08 | LRE08 | LRE08 | 8C2306 | As per the Sr. no(8C2306), The Product is in Warranty. Kindly arrange the site visit. Issue: hardware issue Address SPEAR TRANSPOWER Survey no.976,Plot no.A/395, opp. NK-1 Industrial estate, Nr.Mahakali Mandir, Dhamatvan- Bakrol Road, Bakrol Ahmedabad 382210 Gujarat India Contact person Details: - Mr.Ragesh 9173689721 | 2023-09-13 | 2023-09-14 18:57 | No | Warranty | SPEAR TRANSPOWER | Survey no.976,Plot no.A/395, opp. NK-1 Industrial estate, Nr.Mahakali Mandir, Dhamatvan- Bakrol Road, Bakrol | Ahmedabad | 382210 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | Parthiv Patel JKS Ahmedabad | JKS Engineering Co. | We visited at site check relay body and terminal found check relay stop buttons not working 1nos relay replacement. | Repair |  | 9- Service Validated | 2023-09-15 10:13 | =S= Consig Fill up 226050775 |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11256840 | 104006631 | 2023-09-14 12:35 | 2023-09-14 | Contactor & MCb not operating | 2023-09-14 09:57 | LC1D25M7 | LC1D25M7 | LC1D25M7 |  | complaint for LC1D25M7 Name of Customer ACG PAM Pharma Technologies Pvt. Ltd Site Address Factory : Gat No.446/2, Village Bebadohol, Taluka Maval, Dist Pune- 410506 , India. Name of contact person at site Krishna Pawar Contact Phone / Mob. No: 9175809347 Defective product details LC1D25M7 Product Make Schneider Electric Nature of Defect Contactor plunger mechanical Jam Shutdown availability if applicable NA Serial Num Number of the product: Warranty status In Warranty Commissioned / Installed date 8/31/2023 Invoice Number 225922275 | 2023-09-14 | 2023-09-16 15:19 | No | Warranty | ACG Pam Pharma Technologies Pvt Ltd | Bebadohal Maharashtra | pune | 410506 |  | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Swamesh S_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the contactor found that the contactor coil found burn due to low voltage and this contactor is out of warranty. and then we checked MCB found that the MCB pole open, So MCB Needs to be replaced. Required Material : A9N1P04C - 01 nos | Repair |  | 9- Service Validated | 2023-09-18 10:47 | =S= Consig Fill up 226063650 |  | 55 | INR | 55 | ENM POWER PRODUCTS
WO-11232791 | 103908498 | 2023-09-09 10:38 | 2023-09-09 |  | 2023-09-09 10:21 | APC Smart-UPS RT 10000VA 230V | SURT10000XLI | SURT10000XLI | IS0702011435 | FW: RR : IM15449407 ¦ Store Code : 8409 ¦ SCHNEIDER ¦ DELHI -JEWELLERY Serial# IS0702011435 P: UPS BACKUP Issue S: AMC | 2023-09-09 | 2023-09-09 12:45 | No | Contract | Reliance Retail | GROUND FLOOR,PROPERTY NO:HD-7,,PITHAMPURA | Delhi | 110034 | Delhi | India FS North1 HBN CSP ARCHIT POWER SERVICES Delhi | Vinay Patel_Archit Power Services New Delhi | ARCHIT POWER SERVICES | Site visit is done, found no problem, battery good ups is ok & working fine. | Repair |  | 10- Closed | 2023-09-09 12:47 |  |  | 2 | INR | 2 | ENM SECURE POWER
WO-11256851 | 104006687 | 2023-09-14 10:36 | 2023-09-14 |  | 2023-09-14 10:06 | LC1D40AM7 | LC1D40AM7 | LC1D40AM7 |  | COMPLAIN ? A9N3P63C - QTY - 01, LC1D40AM7 - QTY - 01, MEHVCHDY250A44 - QTY - 01, MEHVCHDY100A44 - QTY - 01 (V.M. CONTROLS.) Name of Customer M/S V.M.CONTROLS 2 Site Address SHED NO. C1-6221, NEAR BSNL TELEPHONE EXCHANGE, ROAD NO. 6 GIDC, SACHIN. DIST: SURAT-394230 Contact Phone / Mob. No: 9879614023 3 Name of contact person at site MR. RAVI J. PATEL 5 Defective product details A9N3P63C - QTY - 01 , LC1D40AM7 - QTY - 01 , MEHVCHDY250A44 - QTY - 01 ,MEHVCHDY100A44 - QTY - 01 6 Product Make SCHNEIDER-MCB , CONTACTOR , CAPACITOR 7 Nature of Defect NOT WORKING 8 Shutdown availability if applicable 9 Warranty status UNDER WARRANTY 10 Commissioned / Installed date 11 Serial No: or DOM of the product BILL NO - : 8089/22-23 DATE - 16-12-2022 | 2023-09-14 | 2023-09-15 12:47 | No | Warranty | V.M.Controls | SHED NO. C1-6221, NEAR BSNL TELEPHONE EXCHANGE, ROAD NO. 6, GIDC SACHIN, | Surat | 394230 | Gujarat | India FS ED&I CSP West Team SHIV SAI ELECTRICALS Vapi | SHIVAM LAD SHIV SAI ELECTRICALS VAPI | shivsai electricals | AS PER SITE VISIT WE CHECK THE PRODUCT AND FOUND OK ON VISUAL INSPECTION.AFTER THAT CHECK THE PROUCT AND FOUND CONTCATOR POLE IS OPEN.WHEN WE CHECK THE PRODUCT WARRNTY STATUS AND FOUDN THE PRODUCT IS UNDER WARRNTY NEEDS TO BE REPLACED. | Repair |  | 9- Service Validated | 2023-09-16 12:48 | =S= Consig Fill up 226042048 |  | 141 | INR | 141 | ENM POWER PRODUCTS
WO-11234183 | 103908800 | 2023-09-09 11:36 | 2023-09-09 |  | 2023-09-09 11:01 | MISCELLANEOUS ANCILLARY EQUIPMENT | ANC-MISC | ANC-MISC | IK-RAC-35A-SS-BF-5870 | FW: RE : HITA/BESTPOWER CALL ID : INC0004008493//B23H02-000073 ¦¦ INC0004419327 P: Chargeable basis case logged for 1time UPS checking (mention serial number of IK-RAC-35A-SS-BF-5870) No Spares support APC will Pay the charges S: Chargeable basis case logged for 1time UPS checking : (mention serial number of IK-RAC-35A-SS-BF-5870) | 2023-09-09 | 2023-09-11 16:15 | No | Commercial Action - Sales | HDFC BANK LTD | 127 RAMDASPETH NAGPUR MAHARASHTRA NAGPUR | Nagpur | 444001 | Maharashtra | India FS West2 Cooling CSP Gale HVAC Pune | Yesudas Sing Gale HVAC Pune | GALE HVAC | We hvae attend your complaint found gas pressure low in the system, so we have done R22 gas topup to the unit upto 1 kg then unit working normally | Repair |  | 10- Closed | 2023-09-11 16:34 |  |  | 802 | INR | 802 | ENM SECURE POWER
WO-11256868 | 104006896 | 2023-09-14 11:43 | 2023-09-14 |  | 2023-09-14 10:13 | LC1D12M7 | LC1D12M7 | LC1D12M7 |  | Name of Customer:-V.D.ELECTRICALS & ENGINEERING CO Site Address:-B1001 GROUND FLOOR SHALIN HEIGHT-4, OPP LAMBH TURN, LAMBHAVATVA CANAL RD NR DIVINE SCHOOL,NAROL Ahmedabad, 382405 Name of contact person at site:-Shakya Sonu Contact Phone / Mob. No:-9427302722.00 Defective product details:-A9N2P06C(1 QTY),LC1D12M7(1 QTY),LC1D18M7(1 QTY) Invoice no.:-PSI/23003270(15/06/2023) Nature of Defect:-MECHANICAL PROBLEM,PHASE PROBLEM | 2023-09-14 | 2023-09-14 12:49 | No | Warranty | V D Electrical & Engineering Co. | B001, Ground Floor, Shalin Height-4, OPP: Lambha Turning, Lambha Vatva Canal Road, Nr, Divine Life International School Narol | Ahmadabad | 382405 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | Parthiv Patel JKS Ahmedabad | JKS Engineering Co. | We visit at site check a9n2p06c on/off working ok body and terminal site not any problem.check lc1d12m7 on/off workingfound check terminal and all bolt found coil side not any problem.check lc1d18m7 on/off working ok check no/nc contactact working check terminal and body found ok all matriyal found ok our products site not any problem working ok. | Repair |  | 9- Service Validated | 2023-09-14 12:54 |  |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11258554 | 104026001 | 2023-09-14 17:03 | 2023-09-14 |  | 2023-09-14 11:29 | LC1D95F7 | LC1D95F7 | LC1D95F7 | pk23045 | As per the Sr. no(pk23045), The Product is in Warranty. Kindly arrange the site visit. Issue: coil issue Address MAHESHWARI TRADERS 365/29, Hansa Puri Rd, Onkar Nagar A, Vishram Nagar, Onkar Nagar, Tri Nagar Delhi 110035 Delhi India Contact person Details: - Mr.Harshit 7428335546 | 2023-09-14 | 2023-09-14 17:07 | No | Warranty | MAHESHWARI TRADERS | 365/29, Hansa Puri Rd, Onkar Nagar A, Vishram Nagar, Onkar Nagar, Tri Nagar | Delhi | 110035 | Delhi | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the contactor found resitance wire burnt due to abnormal voltage, Hence no replacement given to customer. Email : id not provided by customer. | Repair |  | 8- Service Completed | 2023-09-14 17:14 |  |  | 20 | INR | 20 | ENM POWER PRODUCTS
WO-11234214 | 103909140 | 2023-09-09 17:08 | 2023-09-09 |  | 2023-09-09 11:38 | APC Easy UPS Online 6000VA Indian Outlet Rackmount 230V India | SRV6KL-IN | SRV6KL-IN | 9S1948A98801 | FW: RR : IM15449449 ¦ Store Code : TDI9 ¦ SCHNEIDER ¦ DELHI -DIGITAL Serial# 9S1948A98801 P: UPS not working S: AMC | 2023-09-09 | 2023-09-09 17:11 | No | Contract | Reliance Retail Limited | BM GF FF, H 1 Model Town -3 | Delhi | 110009 | Delhi | India FS North1 HBN CSP Martech Systems & Services New Delhi | Raju prasad Martech Systems & Services New Delhi | Martech Systems & Services-Gurgaon | Eng. visited at site check the ups found ups running bypass now problem resolved ups is working fine so call closed | Repair |  | 10- Closed | 2023-09-09 17:15 |  |  | 22 | INR | 22 | ENM SECURE POWER
WO-11259069 | 104024875 | 2023-09-14 14:51 | 2023-09-14 | NA | 2023-09-14 14:33 | LC1D25F7 | LC1D25F7 | LC1D25F7 |  | As per the invoice, The Product is in Warranty. Kindly arrange the site visit. Issue: coil issue Address Eletech Enterprises Ground Floor¸Gala No.10, Samkit Sagar Signature Indl.Complex, Waliv Phata, Vasai (East) - Thane 401208 Maharashtra India Contact person Details: - Mr.Walter 9920412120 | 2023-09-14 | 2023-09-18 16:10 | No | Warranty | Eletech Enterprises | Ground Floor¸Gala No.10, Samkit Sagar Signature Indl.Complex, Waliv Phata, Vasai (East) - | Thane | 401208 | Maharashtra | India FS ED&I CSP West Team East India Power Engineers Mumbai | Akshya Vidhate_East India Power engineers Mumbai | East India Power Engineers (5043) | Visited the site and checked the 25 3pole Contactor no nay continuity and resistance coil is faulty. hence the contactor needs to be a replace with new one | Repair |  | 8- Service Completed | 2023-09-23 13:10 | =S= Consig Fill up 226061242 |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11234251 | 103908868 | 2023-09-09 12:09 | 2023-09-09 |  | 2023-09-09 11:52 | IDAV1311AN-CPD | UFDX | UFDX | JK2151000242 | FW: Regarding PAC-6 showing alarm Serial# JK2151000242 P:Loss of Air Flow Alarm S:Out of warranty( approval in the trail mail- approved by Sankar ganesh) | 2023-09-09 | 2023-09-18 09:15 | No | Pending Contract | Samsung India Electronics Pvt Ltd | Tower No.11 ,Plot No.20-21,IT/ITES SEZ,SECTOR 135 | NOIDA | 201304 | Uttar Pradesh | India FS North2 Cooling CSP D K AIRCON Delhi | Mubarak Ali_D K AIRCON Delhi | DK AIRCON | Indoor Unit Blower Motor and contactor was faulty. We have replaced Blower motor and Contacter 9A and testing done. | Repair |  | 8- Service Completed | 2023-09-18 21:13 |  |  | 32 | INR | 32 | ENM SECURE POWER
WO-11259404 | 104034780 | 2023-09-14 17:36 | 2023-09-14 | MCB Tripping Problem & Add block not working | 2023-09-14 17:10 | SQD-LA1KN04 | SQD-LA1KN04 | SQD-LA1KN04 |  | LA1KN04 Complaint. We have received Complaint from the Jayshree Enterprises saying 1. LA1KN04 - 2 Qty has an issue Contact block open. SO.NO - 300719273 2. A9KF71202 - 1 Qty has an issue MCB dolly not operating. SO.NO - 225521313 site address- Jayshree Enterprises S.No. 29/3 ,Plot No. 13, Borate Wasti, Kharadi, Pune- 411014 Contact person- Mr.Manvi (9850770814) | 2023-09-14 | 2023-09-16 15:32 | No | Warranty | Jayashree Enterprises | Plot no.13,Sr.no.29/3,Boratewasti, Kharadi, | Pune | 411014 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Amit Patil_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the MCB Tripping Problem & Add block not working. MCB is dolly free.it's not getting , this MCB is not repairable. So we checked another Add on Block found that the they used revers and foreword operation. so add block is working they used stock material . So Required material :A9KF71202BQ- 01 nos, LA1KN04 - 02 nos | Repair |  | 9- Service Validated | 2023-09-18 10:43 | =S= Consig Fill up 226060677 |  | 10 | INR | 10 | ENM POWER PRODUCTS
WO-11088725 | 103119366 | 2023-08-09 13:06 | 2023-08-08 |  | 2023-08-08 13:28 | MVS40N4MF5A | MVS40N4MF5A | MVS40N4MF5A |  | From: [rajuenterpriseskol@gmail.com] Sent: 31/7/2023 12:17 pm To: customercare.in@schneider-electric.com; bhardwajvk15@gmail.com Subject: Fwd: Complation Dear Team, Please respond to the email. Customer's ACB is not working and he is not being able to dispatch his panel to the end customer. Please extend your support. PLEASE MENTIONED THE ADDRESS AND CONTACT NUMBER IS BELOW NANDI ENTERPRISES SHYAMBAZAR LANE , RAJBATI BHARDHAMAN 713104 WEST BANGAL MANDEEP SINGH 628489539 OUR GST NO. 19AADFR3147E1ZB WE ARE AUTHORIZED DISTRIBUTORS OF SCHNEIDER, MESCAB and MICOM RELAY Thanks & Regards, _________________________________________________________________________________________ Rajendra Kothari ¦ rajuenterpriseskol@gmail.com , sales.rajuenterprises@gmail.com For Raju Enterprises ¦ M. +91 9830043465 , +91 9836940566 ¦ O. +91 33 46022460/61, +91 33 40071823 7 Pollock Street, Ground Floor, Kolkata 700 001, West Bengal _________________________________________________________________________________________ ---------- Forwarded message --------- From: Raju Enterprises <rajuenterpriseskol@gmail.com> Date: Fri, Jul 21, 2023 at 2:21?PM Subject: Fwd: Complation To: Customer Care <customercare.in@se.com>, Vinod Bhardwaj <bhardwajvk15@gmail.com> Dear Team, Please resolve the issue of our Client - Bhardwaj Electrical. We have received a complaint from our client, they had purchased ACB 4000 Amp. 4 Pole EDO from us and its not working properly. Request you to depute a engineer immediately to resolve this issue. OUR GST NO. 19AADFR3147E1ZB WE ARE AUTHORIZED DISTRIBUTORS OF SCHNEIDER, MESCAB and MICOM RELAY Thanks & Regards, _________________________________________________________________________________________ Rajendra Kothari ¦ rajuenterpriseskol@gmail.com , sales.rajuenterprises@gmail.com For Raju Enterprises ¦ M. +91 9830043465 , +91 9836940566 ¦ O. +91 33 46022460/61, +91 33 40071823 7 Pollock Street, Ground Floor, Kolkata 700 001, West Bengal _________________________________________________________________________________________ ---------- Forwarded message --------- From: Vinod Bhardwaj <bhardwajvk15@gmail.com> Date: Thu, Jul 20, 2023 at 8:48?PM Subject: Re: Complation To: Raju Enterprises <rajuenterpriseskol@gmail.com> BEW/22-23/RE/P.O.26/12/2022 Purchase ACB 4000 Amp. 4 POle EDO Control Terminal Broken when open the Packing & ACB 1000 Amp. 4 POLE MDO not Draw out due to any issue , Plz arrange The Engg on our Burdwan Site. Its Very Urgent Salve this issue Then we Dispatch the panel Thanks With Regards From Vinod Bhardwaj BHardwaj Electrical Works 9932010007 9872115362 | 2023-08-08 | 2023-09-13 20:48 | No | Warranty | Nandi Enterprises | Sham bazar Lane, Rajbati null | Burdwan | 713104 | West Bengal | India FS ED&I CSP East Team SREYAM SERVICES BHATPARA | AMIT BHATTACHARYA_SREYAM SERVICES BHATPARA | Sreyam Services(8513) | AFTER SITE VISIT CHANGE 4000A ACB 11NOS CONTACT & 1 NOS TERMINAL SHIELD & 1000A ACB CHANGE IN NEW CHASIS AND CHANGE RACK IN RACK OUT MECHANISHM AND CHECK FOUND OK. | Repair |  | 9- Service Validated | 2023-09-14 20:10 | =S= Free Order 225968184 has been saved |  | 118 | INR | 118 | ENM POWER PRODUCTS
WO-11234260 | 103909316 | 2023-09-09 13:19 | 2023-09-09 |  | 2023-09-09 12:01 | SRC6KUXIQ | SRC6KUXIQ | SRC6KUXI | BQ1528000445 | FW: AIR UPS APC ¦¦ Call ID : INC0004423014 Branch : 4004_Jawahar Nagar P:UPS backup issue S:AMC | 2023-09-09 | 2023-09-13 17:18 | No | Contract | HDFC BANK LTD | New Building, Subash Chandra Bose Road | cochin | 682019 | Kerala | India FS South2 HBN CSP AutopowerSystems&Solutions Kochi | NISHANTH GOPI AutopowerSystems&Solutions Kochi | AUTOPOWER SYSTEMS & SERVICES | no backup Battery fault - need to replace battery | Repair |  | 10- Closed | 2023-09-13 17:22 |  |  | 5 | INR | 5 | ENM SECURE POWER
WO-11234261 | 103909040 | 2023-09-09 15:51 | 2023-09-09 |  | 2023-09-09 12:02 | EFC MONOBLOCK 1.3TR R410A START KIT RS485 SEQ CONTROL | WDF0181BN040-1 | WDF0181BN040-1 | JK2047001853 | RJIL BD Call Gidderbha Ag1 Serial# JK2047001853 P:Controller Faulty S:AMC | 2023-09-09 | 2023-09-12 18:32 | No | Contract | Reliance Jio Infocomm Ltd | Jagmeet Singh, Motor Market, Bhatinda-Malout Road, Giddarbaha | Bathinda | 152101 | Punjab | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Abhishek Sharma Freezeotech Airconditioning & Refrigeration Chandigarh | Freezeotech Refrigeartion & Air Conditioning Corporation | We visited the site there is controller faulty we need to replaced it part not delivered at site so we will be replaced it during PM after part delivery. | Repair |  | 10- Closed | 2023-09-12 18:35 |  |  | 280 | INR | 280 | ENM SECURE POWER
WO-11264472 | 104055438 | 2023-09-15 13:25 | 2023-09-15 | NA | 2023-09-15 12:36 | 30003006D | 30003006D | 30003006D |  | Fw: Item Damage Details for Damage. No: 5361 Po no. 225919039 SAP no: 300790781 Invoice No : 9008665058 Type No :PM5330 (30003006D) Problem : Display found damage Qty : 1 Nos Kindly arrange replacement & Service engineer below mention address: Site Address- M/s. Marine Electricals (I) Pvt Ltd. PLOT NO. N-51,52,59 & 60, PHASE IV, VERNA INDUSTRIAL ESTATE, VERNA, SALCETE, GOA - 403722. Contact : Mr. Imtiyaz Khan 99552 15847 | 2023-09-15 | 2023-09-16 17:08 | No | Warranty | MARINE ELECTRICALS (I) LTD. GOA UNIT -II | PLOT NO. N-51,52,59 and 60, PHASE IV, VERNA INDUSTRIAL ESTATE VERNA, SALCETE | goa | 403722 | Goa | India FS ED&I CSP West Team East India Power Engineers Mumbai | Abhishek Parab_East India Power engineers Mumbai | East India Power Engineers (5043) | Visited the site and checked the power logic PM5300 front display found damaged. Also black spot observed on display. Scratch make foun an display screen paper. Meter inner / outer packing not available on site. | Assessment/ Inspection | Data Collection | 8- Service Completed | 2023-09-27 16:37 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11264566 | 104032703 | 2023-09-19 15:48 | 2023-09-15 |  | 2023-09-15 12:56 | METSEEM7230 | METSEEM7230 | METSEEM7230 |  | As per the DOM, The Product is in Warranty. Kindly arrange the site visit. Issue: Quality issue Address Novateur Electrical & Digital Systems Pvt. Ltd. NEAR IUP JINDAL FACTORY ROHAD BAHADURGARH 124507 Haryana India Contact person Details: - Mr.Jonum 8077190713 | 2023-09-15 | 2023-09-19 15:52 | No | Warranty | Novateur Electrical & Digital Systems Pvt. Ltd. | NEAR IUP JINDAL FACTORY ROHAD | BAHADURGARH | 124507 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Pradeep Sharma_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the meter found display not working , Hence faulty replaced. 30002975 - 1 nos Email : id not provided by customer. | Repair |  | 8- Service Completed | 2023-09-19 17:11 |  |  | 65 | INR | 65 | ENM POWER PRODUCTS
WO-11234305 | 103909581 | 2023-09-09 14:08 | 2023-09-09 |  | 2023-09-09 13:05 | Leonardo EV,DX,R22,EC Fan,TDAV1021A,Downflow With Heater & Hum | TDAV1021AN001 | TDAV1021AN001 | ZK1334000825 | RJIL Aurangabad AG2 OTN Condenser fan faulty Serial# ZK1334000825 P: Condenser fan faulty S: AMC | 2023-09-09 | 2023-09-13 22:21 | No | Contract | Reliance Jio Infocomm Limited | Survey No. 2/2, Gajanan Maharaj Mandir Road,Garkheda Road, Aurangabad | Aurangabad | 431005 | Maharashtra | India FS West2 Cooling CSP Gale HVAC Pune | Vishal Paul Gale HVAC Pune | GALE HVAC | We have replaced the condenser fan of the unit then unit working normally | Repair |  | 8- Service Completed | 2023-09-14 01:29 |  |  | 260 | INR | 260 | ENM SECURE POWER
WO-11264951 | 104037917 | 2023-09-15 17:06 | 2023-09-15 |  | 2023-09-15 15:16 | LC1D95M7 | LC1D95M7 | LC1D95M7 |  | Name of Custome:-WINDSOR MACHINES LTD. Site Address:-PLOT NO. 6/7, G.I.D.C. INDUSTRIAL ESTATE TALUKA KALOL, Gandhinagar, 382729 Name of contact person at site:-Ajay Bhai Contact Phone / Mob. No:-7490024055.00 Defective product details:-LC1D95M7 (1 QTY) Invoice no.:-PSI/23003552(22/06/2023) Nature of Defect:-STAR DELTA CONTACTOR BURNT | 2023-09-15 | 2023-09-19 17:28 | No | Warranty | Windsor Machine Ltd | Plot # 6\7 GIDC Industrial Estate Chatral | Gandhinagar | 382729 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | Parthiv Patel JKS Ahmedabad | JKS Engineering Co. | We visit at site check lc1d95m7 contactor on/off not working contactor contect burning issue.check contactor t2 terminal burning high voltage issue.As per not a product problem. | Repair |  | 9- Service Validated | 2023-09-19 17:33 |  |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11234310 | 103909832 | 2023-09-09 13:39 | 2023-09-09 |  | 2023-09-09 13:13 | BX1100C-IN | BX1100C-IN | BX1100C-IN | B22250009501 | DOP:02/03/ 2023 P:Back UPS-No back up C:PC T:Consumer request for fse S:POP Invoice copy shared with laldev | 2023-09-09 | 2023-09-09 17:20 | No | Warranty | Amitpal Singh | N95 Ground floor Greater kailash 1 | New Delhi | 110048 | Delhi | India FS North1 HBN CSP HITEK BUSINESS SYSTEMS PVT LTD Delhi | Brajesh B_Hitek Business Systems New Delhi | Hitek Business Systems Pvt Ltd | Engineer this site UPS check found UPS battery saver on so off UPS working ok | Repair |  | 10- Closed | 2023-09-09 17:42 |  |  | 15 | INR | 15 | ENM SECURE POWER
WO-11265072 | 104060755 | 2023-09-16 15:29 | 2023-09-15 |  | 2023-09-15 16:21 | LRE08 | LRE08 | LRE08 |  | As per the invoice, The Product is in Warranty. Kindly arrange the site visit. Issue: pole open issue Address TVS Supply Chain Solutions Ltd. Khewat No.271/38, Village Marakhari, Opp. CRPF HQ, Industrial Area, GANGYAL JAMMU 180010 Jammu and Kashmir India Contact person Details: - Mr.Jagjeet 9103156086 | 2023-09-15 | 2023-09-18 15:49 | No | Warranty | TVS Supply Chain Solutions Ltd. | Khewat No.271/38, Village Marakhari, Opp. CRPF HQ, Industrial Area, GANGYAL null | JAMMU | 180010 | Jammu and Kashmir | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Ram Ashish Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the LRD relay found pole open issue. Hence faulty replaced. LRE08 - 1 Nos. email : jagjeet.singh03@in.panasonic.com | Repair |  | 8- Service Completed | 2023-09-18 15:52 |  |  | 360 | INR | 360 | ENM POWER PRODUCTS
WO-11265186 | 104062683 | 2023-09-16 10:38 | 2023-09-15 | Relay Reset Button not operating | 2023-09-15 16:59 | LRE483 | LRE483 | LRE483 | 8C2305 3 | As per the Sr. no, The Product is in Warranty. Kindly arrange the site visit. Issue: reset Button issue Address AUTOTECHNIX CONTROL SYSTEMS PVT.LTD Plot A-5/4/10, Opp. Mahindra Gate 2, MIDC, Chakan Ind. Area, Phase 4, Pune 410501 Maharashtra India Contact person Details: - Mr.Amit 8669666548 | 2023-09-15 | 2023-09-16 13:01 | No | Warranty | AUTOTECHNIX CONTROL SYSTEMS PVT.LTD. | Plot A-5/4/10, Opp. Mahindra Gate 2, MIDC, Chakan Ind. Area, Phase 4, | Pune | 410501 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Amit Patil_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked Relay Reset Button not operating we observed stop button stuck inside So relay NC Contact not operating. so problem observed in Relay. It's Needs to be replaced. Required Material : LRE483- 01 nos | Repair |  | 9- Service Validated | 2023-09-16 13:01 | =S= Consig Fill up 226061111 |  | 60 | INR | 60 | ENM POWER PRODUCTS
WO-11234313 | 103909954 | 2023-09-09 16:19 | 2023-09-09 |  | 2023-09-09 13:13 | BX2000UXI | BX2000UXI | BX2000UXI | 9B1538A00811 | DOP: AMC P: Back UPS: not powering on, burning smell from ups C:4 pc T:Need fse S: AMC | 2023-09-09 | 2023-09-11 13:05 | No | Contract | RAJPAL ABHIKARAN BHOPAL P LTD | Rajpal Abikaran C/O Rajpal Toyota Hoshangabad Road | Bhopal | 462026 | Madhya Pradesh | India FS West2 HBN CSP_Stream Line Indore | Santosh Prajapati_Stream Line Indore | Stream Line | customer site ups not powering on so faulty pcb replaced after ups working ok, new pcb serial number 0J-31-010596--9B2331A17033 | Repair |  | 10- Closed | 2023-09-11 13:06 |  |  | 10 | INR | 10 | ENM SECURE POWER
WO-11265196 | 104062732 | 2023-09-16 14:57 | 2023-09-15 |  | 2023-09-15 17:12 | LV540316 | LV540316 | LV540316 | 1022426 | As per the Sr. no, The Product is in Warranty. Kindly arrange the site visit. Issue: tripping issue Address SMAPCON O-8,SITE V KASNA INDUSTRIAL AREA KASNA NOIDA 203202 Uttar Pradesh India Contact person Details: - Mr. RASHID SAIFI 9899118424 | 2023-09-15 | 2023-09-16 14:58 | No | Warranty | SMAPCON | O-8,SITE V KASNA INDUSTRIAL AREA KASNA | NOIDA | 203202 | Uttar Pradesh | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mccb found not proper working due to tripping lever broken / damage, Hence no replacement given to customer. Email : id not provided by customer. | Repair |  | 8- Service Completed | 2023-09-16 15:32 |  |  | 65 | INR | 65 | ENM POWER PRODUCTS
WO-11234326 | 103910173 | 2023-09-11 10:51 | 2023-09-09 |  | 2023-09-09 13:39 | SURT6000XLI-CC | SURT6000XLI-CC | SURT6000XLI-CC | B21617001757 | FW: RR : Store Code : TB88 ¦ SCHNEIDER ¦ MAHARASHTRA -DIGITAL Serial# B21617001757 P: UPS Re-installation S: UPS Re-installation | 2023-09-09 | 2023-09-11 15:42 | No | Commercial Action - Sales | RRL CDIT Seawoods Grand Central | Seawoods Grand Central Mall Lower Groun, Unit No -2324105106107 Plot R-1 Sector 4, Seawoods Railway Station Nerul Node Navi | Mumbai | 400706 | Maharashtra | India FS West1 HBN CSP_Mahavir Sys Power Pvt Ltd Vashi | Sanju Chauthmol_Mahavir Sys Power Pvt Ltd Vashi | Mahavir Sys Power Pvt Ltd -Vashi | Engineer visited the customer site to Installation ups and found that ups was in disconnect condition there is no input supply connected to it since past 2 months due to which batteries are totally discharged 5 & 7V. On main supply ups showing 11000 Fault. Require battery 1st to check the ups properly | Commissioning & Installation | Start-up | 8- Service Completed | 2023-09-11 15:48 |  |  | 13 | INR | 13 | ENM SECURE POWER
WO-11183669 | 103662369 | 2023-08-30 17:47 | 2023-08-31 |  | 2023-08-30 16:38 | Leonardo Max,DX,R407c,EC Fan,TDAV3342A Downflow With Heater and Humidifier | TDAV3342AN001 | TDAV3342AN001 | NUCW4453 | AMC P: MCB Melting issue S: AMC | 2023-08-30 | 2023-09-02 15:47 | No | Contract | Aricent Technologies (Holdings) Ltd | Aricent Group , 2nd floor, Chandilya Tower, | KANCHIPURAM | 600032 | Tamil Nadu | India FS South4 Cooling CSP Unity Air conditioning Engineers Chennai | V Ramkumar_ Unity Air conditioning Engineers Chennai | UNITY AIRCONDITIONING ENGINEERS | Isolator melting issue : Now we Checked and changed the new isolator and observe unit working normal. | Repair |  | 10- Closed | 2023-09-02 15:51 |  |  | 18 | INR | 18 | ENM SECURE POWER
WO-11184632 |  | 2023-09-08 11:23 | 2023-09-19 | very satisfied | 2023-08-30 18:52 | SURT20KUXI-IN | SURT20KUXI-IN | SURT20KUXI-IN | B21621000033 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-08-30 | 2023-09-08 11:50 | No | Contract | UBS Business Solution Pvt Ltd | Unit No 1201 1301 and 1401 Building No.2 Minds Mugalsan Rd Mindspace, (West, Sector 20 B, Sector 20 Mind Space Gigaplex Plot NO IT 5 MIDC Aeroli Knowladge Park TTC Industrial Area, Aeroli West null | Navi Mumbai | 400708 | Maharashtra | India FS West1 HBN CSP_Mahavir Sys Power Pvt Ltd Vashi | Shubham Mirjulkar Mahavir Sys Power Pvt Ltd Vashi | Mahavir Sys Power Pvt Ltd -Vashi | Engineer had done the PM activity of ups and checked its working fine one nos battery is faulty | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-08 12:02 |  |  | 8 | INR | 8 | ENM SECURE POWER
WO-11276867 | 104086093 | 2023-09-18 13:04 | 2023-09-18 |  | 2023-09-18 12:43 | MEHVCSDY250A44PB | MEHVCSDY250A44PB | MEHVCSDY250A44PB |  | Case No. reqd. A/c Paonta Frontier Alloys Steels Ltd Jamniwala Rd Jambookala Badrinagar Paonta Sahib,Sirmour,Himachal Pradesh. Mr. Gurpreet Singh 9805702813 Product : MEHVCSDY250A44PB - Qty:1 Srn : ME-M2074050 , DOP: 26/5/2023 Swell issue / Derating Issue | 2023-09-18 | 2023-09-18 13:05 | No | Warranty | Frontier Alloys Steels Ltd | Jamniwala rd Jambookala Badrinagar Paonta Sahib | Sirmaur | 173025 | Himachal Pradesh | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Karnail Singh Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the capacitor found Swell issue /Derated Issue. Hence faulty replaced. MEHVCSDY250A44 - 1 Nos. email : id not provided by the customer. | Repair |  | 8- Service Completed | 2023-09-18 15:36 |  |  | 125 | INR | 125 | ENM POWER PRODUCTS
WO-11276876 | 104086766 | 2023-09-18 16:07 | 2023-09-19 |  | 2023-09-18 12:50 | MEHVBAPP200A44 | MEHVBAPP200A44 | MEHVBAPP200A44 |  | MEHVBAPP200A44--1 no Invoice : Brisk Electronics--8 months back Not operating MEHVBAPP200A44--1 no Invoice : Brisk Electronics--8 months back Not operating 9898050575 | 2023-09-18 | 2023-09-19 10:55 | No | Warranty | GYATRI ELECTRICAL | Shop number 5 dholeswer shoping center oposite shakti complex and gopi pan Changoder | Ahmadabad | 382213 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | Parthiv Patel JKS Ahmedabad | JKS Engineering Co. | We visit to at side check capacitor traminal found ok.check capacitor body side not any damage.capacitor voltage ry=438v yb=429v br=421v.check capacitor all terminal mfd=oo open found check capacitor amp not show found.so now customer satisfaction 1time 1nos capacitor give a free replacement. | Repair |  | 9- Service Validated | 2023-09-25 16:14 |  |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11277297 | 104092928 | 2023-09-19 11:02 | 2023-09-18 |  | 2023-09-18 15:57 | LC1D32 | LC1D32 | LC1D32 |  | LC1D32--2 no Screw not tightening Sr : 1023294,1023294 LC1D32--2 no Screw not tightening Sr : 1023294,1023294 Site : Sunil Commercial Corporation Nr Gold Building Sardarpura Jodhpur Raj 342003 Mr.Manish Kalani : 9314710073 | 2023-09-18 | 2023-09-30 11:01 | No | Warranty | Manish Kalani | Sunil Commercial Corporation Nr Gold Building Sardarpura | Jodhpur | 342003 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Amarjeet Singh Sharma Electric Jaipur | Sharma Electric Works | Checked the contactor found phase screw not tighten, Hence faulty, replaced. LC1D32N7 - 2 nos Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-30 11:07 | 226067327 ZFRE BOOKED. |  | 338 | INR | 338 | ENM POWER PRODUCTS
WO-11277394 | 104087786 | 2023-09-19 18:23 | 2023-09-20 |  | 2023-09-18 17:08 |  |  |  |  | As per the invoice, The Product is in Warranty. Kindly arrange the site visit. Issue: Test button issue Address SIDDHI VINAYAK INDUSTRIES Plot no 1604, G.I.D.C., Phase ? IV Wadhwan City Surendranagar 363035 Gujarat India Contact person Details: - Mr. Ravi 7486014673 | 2023-09-18 | 2023-09-20 17:39 | No | Warranty | SIDDHI VINAYAK INDUSTRIES | Plot no 1604, G.I.D.C., Phase ? IV Wadhwan City null | Surendranagar | 363035 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | Jayesh J_JKS Rajkot | JKS Engineering Co. | Visited site and observed Check earth relay with external supply then press test button but out put no nc contact not working Check other relay with same and this working ok So as per customer satisfaction we have give replacement 1 nos relay | Repair |  | 9- Service Validated | 2023-09-21 18:36 | =S= Consig Fill up 226072623 |  | 115 | INR | 115 | ENM POWER PRODUCTS
WO-11280086 | 104093706 | 2023-09-20 10:23 | 2023-09-19 |  | 2023-09-19 11:09 | LC1D95M7 | LC1D95M7 | LC1D95M7 |  | LC1D95M7-Faulty Materials. ) PART NO: LC1D95M7 PART NO : LC1D95M7 QTY. : 1 NO. ISSUE : Body Part Found in damage condition during Unboxing of contactor. (Photos attached) Invoice No. : 9008272781 - Copy Attached. # Location and contact details. Location : Survey No. 248-250, First Floor Sardar Patel Ring Road, Nana Chiloda, Gandhinagar - 382330 Contact person : Nilesh Jansari Contact No. : +91 97253 85545 | 2023-09-19 | 2023-09-22 12:06 | No | Warranty | Lubi Electronics Pvt. Ltd. | Survey No. 248-250, Sardar Patel Ring Road, Nana Chiloda, Basement & 1st Floor, Gandhinagar, | Ahmedabad | 380025 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Nijesh Patel_Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physically observed ok. checked the contactor box damaged observed . take a contactor and contactor box photo but master box not available. and pod not available. customer invoice no : 9008272781 dtd 30/09/2022. take a photograph for further action. further action taken by schneider. | Assessment/ Inspection | Data Collection | 8- Service Completed | 2023-09-22 12:06 |  |  | 15 | INR | 15 | ENM POWER PRODUCTS
WO-11280311 | 104097897 | 2023-09-19 16:40 | 2023-09-19 |  | 2023-09-19 12:36 | GCR_NSX | GCR_NSX | GCR_NSX | TC - 2022 - W46 - 3 | As per the Sr. no, The Product is in Warranty. Kindly arrange the site visit. Issue: UV coil issue Address POLMON PROCESS CONTROLS PVT LTD PLOT NO F 23 SY NO. 70 & 174 FICCI - FLO, MEDICAL DEVICES PARK, SULTHANPUR(V) AMEENPUR(M) PATANCHERU SANGAREDDY 502319 Telangana India Contact person Details: - Mr.Krishna 7702944004 | 2023-09-19 | 2023-09-26 12:00 | No | Warranty | POLMON PROCESS CONTROLS PVT LTD | PLOT NO F 23 SY NO. 70 & 174 FICCI - FLO, MEDICAL DEVICES PARK, SULTHANPUR(V) AMEENPUR(M) PATANCHERU | SANGAREDDY | 502319 | Telangana | India FS ED&I CSP South Team Sumanth Electrical Services Hyderabad | Venkata Prasad_SUMANTH ELECTRICAL SERVICES HYDERABAD | Sumanth Electrical Services | Visited the Site and Inspected the Schneider Electric- LV429407-01 No's. Here in our observation we found that the Under-voltage pin got damaged. So,we have replaced with New Coil and we have checked the ON/OFF operations which found OK.Complaint is closed. | Repair |  | 8- Service Completed | 2023-09-26 17:29 |  |  | 25 | INR | 25 | ENM POWER PRODUCTS
WO-11280857 | 104121820 | 2023-09-20 10:01 | 2023-09-19 |  | 2023-09-19 15:43 | LC1D40AM7 | LC1D40AM7 | LC1D40AM7 | 8B21432001 | As per the Sr. no, The Product is in Warranty. Kindly arrange the site visit. Issue: Chattering issue Address Naresh Textile Dahar.Back Side Govt.School Panipat 132103 Haryana India Contact person Details: - Mr.Soumitra 8168663976 | 2023-09-19 | 2023-09-21 15:08 | No | Warranty | Naresh Textile | Dahar.Back Side Govt.School null | Panipat | 132103 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Customer used contactor LC1D40AM7 and Contactor LC1D50AM7 is capacitor panel. It is used for operating in 25KVAr capacitor with back up of 63A MCB. Due to this contactor contact weld and suggested customer to use contactor as per capacitor rating. email : id not provided by the customer. | Repair |  | 8- Service Completed | 2023-09-21 15:08 |  |  | 165 | INR | 165 | ENM POWER PRODUCTS
WO-11280953 | 104115907 | 2023-09-19 20:05 | 2023-09-19 |  | 2023-09-19 16:39 | LV563309 | LV563309 | LV563309 | 1022034 | As per the Sr. no, The Product is in Warranty. Kindly arrange the site visit. Issue: Tripping issue Address TIREX TRANSMISSION PVT LTD C/o DEPOT 29 BMTC, 2M3R+VHX, HALE DEVASANDRA, KRISHNARAJAPUR BENGALURU 560036 Karnataka India Contact person Details: - Mr. Mithun 9972766846 | 2023-09-19 | 2023-09-20 12:23 | No | Warranty | TIREX TRANSMISSION PVT LTD | C/o DEPOT 29 BMTC, 2M3R+VHX, HALE DEVASANDRA, KRISHNARAJAPUR null | BENGALURU | 560036 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | C Gunasekaran_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported the problem found was mccb output side got burnt issue due to cable lose termination the problem found happen external so we arranged the replacement | Repair |  | 9- Service Validated | 2023-09-20 12:29 |  |  | 10 | INR | 10 | ENM POWER PRODUCTS
WO-11283272 | 104126708 | 2023-09-20 10:26 | 2023-09-21 |  | 2023-09-20 09:38 | GV2P20 | GV2P20 | GV2P20 |  | FW: DEFECTIVE MATERIAL @ V D ELECTRICAL AND ENGINEERING CO. Invoice : Brisk--10/8/2023 V D ELECTRICAL AND ENGINEERING CO. Model & Qty GV2P20 Qty 1 NOS Fault POWER TERMINAL NOT WORKING INVOICE NO. AS2324-107289 INVOICE DATED 10.08.2023 Site Address B001 Ground Floor Shalin Height-4, OPP: Lambha Turning Lambha -Vatva Canal Road,Nr, Divine Life School, Narol, Ahmedabad-382405 Gujarat, India Contact Person Name MR. MAYUR DAVE Contact Person No. 9427302722 | 2023-09-20 | 2023-09-20 14:33 | No | Warranty | V D Electrical & Engineering Co. | B001, Ground Floor, Shalin Height-4, OPP: Lambha Turning, Lambha Vatva Canal Road, Nr, Divine Life International School Narol | Ahmadabad | 382405 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | Parthiv Patel JKS Ahmedabad | JKS Engineering Co. | We visited at side check mpcb on/off button not working check mpcb terminal and body site not any damage.so now customer satisfaction 1time 1nos mpcb give a free replacement. | Repair |  | 9- Service Validated | 2023-09-20 14:47 | =S= Consig Fill up 226071061 |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11285227 | 104144971 | 2023-09-20 13:30 | 2023-09-20 |  | 2023-09-20 12:55 | LC1D25BD | LC1D25BD | LC1D25BD |  | As per the invoice, The Product is in Warranty. Kindly arrange the site visit. Issue: coil issue MCb tripping Address MARUTI SUZUKI INDIA LIMITED NEAR MANTRY WEB CITY, BIBLE COLLEGE OPPOSITE HORIZON INTERNATION SCHOOL HENNUR ROAD BANGALORE 560077 Karnataka India Contact person Details: - Mr. Amit 9999118368 | 2023-09-20 | 2023-09-25 13:48 | No | Warranty | MARUTI SUZUKI INDIA LIMITED | NEAR MANTRY WEB CITY, BIBLE COLLEGE OPPOSITE HORIZON INTERNATION SCHOOL HENNUR ROAD | BANGALORE | 560077 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | MANOJ GANESAN SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | As per the previous site visit the problem found was contactor not getting on hardly press manual continuity not came so we booked the replacement to the customer | Repair |  | 9- Service Validated | 2023-09-25 20:29 |  |  | 15 | INR | 15 | ENM POWER PRODUCTS
WO-11285520 | 104147556 | 2023-09-20 14:41 | 2023-09-20 |  | 2023-09-20 14:29 | METSEEM6436HCL10RS | METSEEM6436HCL10RS | METSEEM6436HCL10RS |  | Meter Complaint 20.09.2023 Name of Customer Forrest Trails by Pacifica Site Address Nr.Kins villa At Chabasar ,Bavla,Ahmedabad-382220 Name of contact person at site Mr.sanjay Dani Contact Phone / Mob. No: 9016253089 Defective product details METSEEM6436HCL10RS Nature of Defect Display Problem Name & phone No: of person registering the complaint Ketul Patel - 9913908596 INVOICE NO WITH DATE 9008310634 - 03.11.2022 | 2023-09-20 | 2023-09-21 12:52 | No | Warranty | Sanjay Dani | Forrest Trails by Pacifica,Nr.Kins villa,At Chabasar ,Bavla | Ahmedabad | 382220 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | Parthiv Patel JKS Ahmedabad | JKS Engineering Co. | We visit at side check meter auxiliary voltage ry=230v yb=227 br=228v check meter not show the display.So now customer satisfaction 1time 1nos meter give a free replacement. | Repair |  | 9- Service Validated | 2023-09-21 16:06 | =S= Consig Fill up 226057156 |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11285719 | 104147294 | 2023-09-20 16:02 | 2023-09-20 |  | 2023-09-20 15:34 | GCR_NSX | GCR_NSX | GCR_NSX |  | As per the Sr. no, The Product(UV coil) is in Warranty. Kindly arrange the site visit. Issue: UV coil issue Address ELECTRO CONTROL SYSTEMS INDIA PVT.LTD. PLOT NO.1123, AAJI INDUSTRIAL AREA, NER THORALA ROAD RAJKOT 360002 Gujarat India Contact person Details: - Mr. Dhaval 9512505023 | 2023-09-20 | 2023-09-21 14:45 | No | Warranty | ELECTRO CONTROL SYSTEMS INDIA PVT.LTD. | PLOT NO.1123, AAJI INDUSTRIAL AREA, NER THORALA ROAD | RAJKOT | 360002 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | Jayesh J_JKS Rajkot | JKS Engineering Co. | VISITED SITE & OBSERVED CHECK WITH NEW UV & MCCB FOUND NOT OPERATE THEN CHECK MCCB UV PRESS LEVER FOUND BEND DUE TO The customer was wronged INSTALLED THEN WE STRAIGHT THIS LEVER AND CHECK MCCB WORKING FOUND OK THEN CHECK 2 NOS FAULTY UV , the customer had damaged it by fitting it wrongly AND IN THIS UV ONE IS FULLY DAMAGE AND 2ND IS NOT WORK PROPRELY SO WE HAVE CONSIDER IN WARRANTY ONLY ONE NUMBER UV, IN FUTURE SAME PROBLEM WE WILL AVOIDE WARRANTY 1 NOS UV COLLECT FROM CUSTOMER.SUGGEST TO CUSTOMER UV INSTALL AS PER SCHNEIDER GUIDELIN | Repair |  | 9- Service Validated | 2023-09-21 16:03 | =S= Consig Fill up 226072336 |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11285784 | 104147489 | 2023-09-21 11:07 | 2023-09-20 | product found in transit damaged | 2023-09-20 15:50 | LC1F1000 | LC1F1000 | LC1F1000 |  | FW: Broken material Recd by AIR Flexi- Chennai Attached pls find photos of broken material recd by Air Invoice no:AA3330136684 DT 19/09/2023 System Inv No:9008719947 through Felxi Inland Logistic Pvt Ltd , Docket No : 21253 dt 19.09.2023 In this Invoice Item LC1F1000 ...01 Nos .but actual recd in Broken condition . Broken Qty LC1F1000 : 01 Nos | 2023-09-20 | 2023-09-21 12:44 | No | Warranty | Brisk Electronics Pvt. Ltd.(1760) | A/P Bhukum, H. No. 607, Gat No. 182,Pune Paud Road, Tal. Mulshi, | Pune | 412115 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Samadhan S_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the product found in transit damaged. Observed contactor Add on Block holding molded part found damaged condition in transit. this problem is not repairable. Customer not accepted it. So Problem observed in Contactor. So Required material; : LC1F1000- 01 nos | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-26 12:18 |  |  | 45 | INR | 45 | ENM POWER PRODUCTS
WO-11006551 | 102586025 | 2023-07-19 11:23 | 2023-07-18 |  | 2023-07-18 13:58 | LTMR100MBD | LTMR100MBD | LTMR100MBD | 466051131130136 | Schneider LTMR issue in HPCL Visakha Refinery Very Urgent!!! Dear Team, Please do the needful , as customer is chasing for LTMR support since a couple of days . Subject: RE: Schneider LTMR issue in HPCL Visakha Refinery Dear Sir, As discussed verbally yesterday request to share LTMR expert of schneider company who could address our queries and schedule your service partner in Visakhapatnam today to check the issue in our suspected malfunctioned LTMR Relay on priority. As discussed On 15-07-2023 it is observed that without any Local or DCS stop & start commands to 90-PM-31B (DHT RGC STND BY LO PUMP) Motor having LTMR Relay has stopped at 7:00:49 AM & started again at 7:00:50 AM (SCADA trend of the Motor attached) & also due to loss of Run feedback of this motor auto cutin of main LO pump has occurred . We have checked for any LCS/DCS stop & start commands in INST PLC & also in our Substation SCADA & found no events of start & stop recorded. In this scenario since the control commands to the motor are through LTMR I/O?s (detailed drawing attached) we are suspecting that LTMR has malfunctioned leading to Stop & start of the motor in the 1 s time span. Schneider to look into this issue which is a serious concern for process interruptions and as discussed depute your best expert service engineer immediately for checking the healthiness & troubleshooting of the same relay. Also Request to share any such issues in LTMR?s faced by Schneider in other Operating industries & provide any latest upgradation in technologies to record & store I/O?s of LTMR for effective functioning & troubleshooting. Please find the details of the enclosure attached Customer :HPCL Vizag Customer name: Mr. Pavan Karri Contact No:8309098985. pavankumar.karri@hpcl.in LTMR100MBD 04660 511311 30136 | 2023-07-18 | 2023-09-12 10:49 | No | Warranty | Hindustan Petroleum Corporation Lim | Visakh Refinery, Post Box No 15 Malkapuram | Visakhapatnam | 530011 | Andhra Pradesh | India FS ED&I CSP South Team Voltamp Electrical Works Visakhapatnam | Doni RajeshReddy_VOLT AMP ELECTRICAL WORKS Visakhapatnam | Voltamp Electrical Works | As per the issue we have address the site and we have take the so move back file and observed starter LED while Applying rated auxiliary supply found ok for further Analysis we have asked customer to Shane wire diagram of LTRM communication SLD also we have taken photo SNAP OF site condition so that we will submit to our higher official we get back soon with the Appropriate so inotions | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-12 10:49 |  |  | 25 | INR | 25 | ENM POWER PRODUCTS
WO-11285932 | 104152543 | 2023-09-21 14:00 | 2023-09-20 |  | 2023-09-20 16:08 | LC1E40M7 | LC1E40M7 | LC1E40M7 | KH2221 | As per the Sr. no, The Product(UV coil) is in Warranty. Kindly arrange the site visit. Issue: one pole open Address Bajrang Rice mill vpo Barsana kaithal 136026 Haryana India Contact person Details: - Mr. Parveen 9996707614 | 2023-09-20 | 2023-09-21 14:03 | No | Warranty | Bajrang Rice mill | vpo Barsana null | kaithal | 136026 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | checked the contators found coil burnt due to voltage issue. hence no replacement given to customer. Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-21 14:24 |  |  | 140 | INR | 140 | ENM POWER PRODUCTS
WO-11285988 | 104146332 | 2023-09-21 16:06 | 2023-09-20 |  | 2023-09-20 16:35 | LV563319 | LV563319 | LV563319 |  | As per the invoice, The Product is in Warranty. Kindly arrange the site visit. Issue: MCCB is not getting reset Address Vintech Controls & Devices Pvt. Ltd. 519/2, Athipalayam Road, Chinnavedampatti, Coimbatore 641006 Tamil Nadu India Contact person Details: - Mr. Latha 9994943480 | 2023-09-20 | 2023-09-23 12:24 | No | Warranty | Vintech Controls & Devices Pvt. Ltd. | 519/2, Athipalayam Road, Chinnavedampatti, | Coimbatore | 641006 | Tamil Nadu | India FS ED&I CSP South Team Power Pro Engineering Services Coimbatore | KV ARUNKUMAR_POWER PRO ENGINEERIG SERVICES COIMBATORE | Powerpro Engineering Services | WE HAVE VISITED THE SITE AND INSPETED WE FOUND MCCB UV OPERATING LEVER BEND DUE TO WRONG FXING OF UV COIL WE HAVE RECTFIY THE SAME TESTED AND FOUND WORKING TESTED AND ALL ATHE FUNCTION ARE FOUDN WORKING OK | Repair |  | 9- Service Validated | 2023-09-23 12:25 |  |  | 31 | INR | 31 | ENM POWER PRODUCTS
WO-11287134 | 104152758 | 2023-09-22 10:00 | 2023-09-20 |  | 2023-09-20 19:41 | GCR_MVS | GCR_MVS | GCR_MVS |  | As per the invoice, The Product is in Warranty. Kindly arrange the site visit. Issue: Rack in /out issue Address Advance Panel & Switchgear Pvt. Ltd. Plot No. 30 & 31, Sector - 5, I.I.E. Ranipur, SIDCUL, Haridwar 249403 Uttarakhand India Contact person Details: - Mr. Ashish 6392578145 | 2023-09-20 | 2023-09-22 17:03 | No | Warranty | Advance Panel & Switchgear Pvt. Ltd. | Plot No. 30 & 31, Sector - 5, I.I.E. Ranipur, SIDCUL, | Haridwar | 249403 | Uttarakhand | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the ACB found working ok. email : id not provided by the customer. | Repair |  | 8- Service Completed | 2023-09-22 17:12 |  |  | 210 | INR | 210 | ENM POWER PRODUCTS
WO-11289219 | 104154681 | 2023-09-21 10:38 | 2023-09-21 |  | 2023-09-21 10:12 | LC1E80004M5WB | LC1E80004M5WB | LC1E80004M5WB |  | FW: Pls.arrangement visit plan for Power Tech -Solex Contactor site Surendranagar . Contact Phone / Mob. No: 9510733104 3 Name of contact person at site MR. Parth Solex Sir Goldi 5 Defective product details LC1E80004M5WBIN - QTY - 1 6 Product Make SCHNEIDER-CONTACTOR 7 Nature of Defect NOT WORKING 8 Shutdown availability if applicable 9 Warranty status UNDER WARRANTY 10 Commissioned / Installed date 11 Serial No: or DOM of the product BILL NO - : 7757/22-23 DATE - 06-12-2022 Hi-Tech Mktg.,SURAT. | 2023-09-21 | 2023-09-21 15:51 | No | Warranty | PRINCIPLE SHRI MODEL SCHOOL | GOKHARVADA , TAL CHUDA null | Surendranagar | 363410 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | Jayesh J_JKS Rajkot | JKS Engineering Co. | Check contector and found terminal l1 & l2 side burning dueto loose connection and lugs not used as per Schneider giued line however customer satisfaction we have consider in warranty and give 1time free replacement. | Repair |  | 9- Service Validated | 2023-09-21 15:56 | =S= Free Order 226049309 has been saved |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11290303 | 104090865 | 2023-09-21 13:54 | 2023-09-21 | NA | 2023-09-21 13:25 | GCR_NSX | GCR_NSX | GCR_NSX |  | As per the invoice, The Product is in Warranty. Kindly arrange the site visit. Issue: hardware issue Address CARS24 Bharat Bhai Compund, Near Padgha Toll Plaza Next to RKG Logistics, Adjacent to Godrej Warehouse, Mumbai ? Nasik Highway,Village: Padgha, Bhiwandi Thane 421101 Maharashtra India Contact person Details: - Mr Paresh 8652509999 | 2023-09-21 | 2023-09-23 13:35 | No | Warranty | CARS24 | Bharat Bhai Compund, Near Padgha Toll Plaza Next to RKG Logistics, Adjacent to Godrej Warehouse, Mumbai ? Nasik Highway,Village: Padgha, Bhiwandi null | Thane | 421101 | Maharashtra | India FS ED&I CSP West Team East India Power Engineers Mumbai | Akshya Vidhate_East India Power engineers Mumbai | East India Power Engineers (5043) | Visited the site and Motor Mechanism no replace due to wrong motor mechanism available on site. | Repair |  | 8- Service Completed | 2023-09-24 13:36 |  |  | 40 | INR | 40 | ENM POWER PRODUCTS
WO-11293896 | 104185122 | 2023-09-22 10:33 | 2023-09-22 | MCB & Contactor dolly free | 2023-09-22 10:08 | CAD32F7 | CAD32F7 | CAD32F7 |  | ISSUE COMPLAINT Company Name & Complete Address with pin code - Where product is installed SHRI SAMARTH ENTERPRISES PLOT NO 09 RS NO 281A/2 SAMARAT COLONY KOLHAPUR-416012 Contact Person at Site : Name & Mobile No. OMKAR JOSHI 7888043208 Alternate Mobile No : Contact Person at Site - Email Address** omkar.joshi@briskelectronics,com Defective Product Model/Part No (Pls refer FAQ sheet ) CAD32F7 , A9N3P32C , A9N1P32C Nature of Defect* - Defects Video and Photographs CAD32F7- NC NOT OPERATE A9N3P32C - Y PHASE PROBLEM A9N1P32C - TRIP PROBLEM Shutdown availability if applicable YES POP - SE Authorised Partner Invoice soft copy Brisk Electronics--21/8/2023 | 2023-09-22 | 2023-09-26 16:35 | No | Warranty | SHRI SAMARTH ENTERPRISES | PLOT NO 09 RS NO 281A/2 SAMARAT COLONY | KOLHAPUR | 416012 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Sachin Jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the MCB & Contactor dolly free. MCB 3P 32Amp Dolly free. and 1 pole 32Amp Pole open issue. then we checked CAD32F7 found that the Contactor NC Terminal 21 & 22 not changeover. So above material needs to be replaced. Required Material : A9N3P32C - 01 nos, A9N1P32C - 01 nos, CAD32F7 - 01 nos | Repair |  | 9- Service Validated | 2023-09-26 17:28 | =S= Consig Fill up 226081475 |  | 280 | INR | 280 | ENM POWER PRODUCTS
WO-11293900 | 104184231 | 2023-09-22 11:38 | 2023-09-23 |  | 2023-09-22 10:11 | 30002366 | 30002366 | 30002366 |  | RE: Schneider Complaint Registration Form [ thread::CRzr-51EfT-F6l1hQAO0uD4:: ] Name of Customer INDIAN SWITCHGEARS AND CONSULTANTS Site Address 945/1, GIDC ESTATE, MAKARPURA, VADODARA - 390 0100 Name of contact person at site Mr. Milan Hire Contact Phone / Mob. No: 9313572553 Defective product details 30002366 Nature of Defect Display is not working Shutdown availability if applicable Yes Warranty status Yes Commissioned / Installed date INV2324-04062 Serial No: or DOM of the product 54231230987 | 2023-09-22 | 2023-09-23 10:30 | No | Warranty | Indian Switchgear & Consultants | 945, GIDC Estate, Makarpura | Baroda | 390010 | Gujarat | India FS ED&I CSP West Team Jay Services Vadodara | Ghanshyam Kachiya_Jay Services Vadodara | Jay Services | We visited at site & checked above meter found physically ok. We test by Aux supply 230 VAC & observed terminal voltage L & N ok but display not ON. Now we replaced from our distributor stock. | Repair |  | 9- Service Validated | 2023-09-23 10:30 | =S= Consig Fill up 226071076 |  | 14 | INR | 14 | ENM POWER PRODUCTS
WO-11295238 | 104189269 | 2023-09-23 11:35 | 2023-09-22 | NA | 2023-09-22 11:47 | GCR_NSX | GCR_NSX | GCR_NSX |  | As per the invoice, The Product(Motor mechanism) is in Warranty. Kindly arrange the site visit. Issue: Spring charging issue Address Union Bank of India 6th Floor, Mafatlal Centre, Nariman Point Mumbai 400021 Maharashtra India Contact person Details: - Mr. Ramprakash 9769947316 | 2023-09-22 | 2023-09-25 10:18 | No | Warranty | Union Bank of India | 6th Floor, Mafatlal Centre, Nariman Point null | Mumbai | 400021 | Maharashtra | India FS ED&I CSP West Team East India Power Engineers Mumbai | Sandeep Ingavale East India Power engineers Mumbai | East India Power Engineers (5043) | Visited the site & checked the MCCB with the motor mechanism found not working. Checked the breaker type and found the breaker is CVS type & the Motor mechanism is not suitable for this CVS MCCB. The wrong selection of products was used in this case. | Repair |  | 8- Service Completed | 2023-09-26 10:32 |  |  | 34 | INR | 34 | ENM POWER PRODUCTS
WO-11295865 | 104213991 | 2023-09-23 09:56 | 2023-09-22 |  | 2023-09-22 15:39 | SQD-LC1D32BD | SQD-LC1D32BD | SQD-LC1D32BD |  | FW: FW: DEFECTIVE MATERIAL@ V D ELECTRICAL AND ENGINEERING CO. [ thread::I6odQKZ7cIqiV-JwpwT8Wz4:: ] Brisk Electronics---15/9/2023 V D ELECTRICAL AND ENGINEERING CO. Model & Qty LC1D32BD Qty 1 NOS Fault SCREW NOT FIT PROPERLY INVOICE NO. AS2324-109145 INVOICE DATED 15.09.2023 Site Address B001 Ground Floor Shalin Height-4, OPP: Lambha Turning Lambha -Vatva Canal Road,Nr, Divine Life School, Narol, Ahmedabad-382405 Gujarat, India Contact Person Name MR. MAYUR DAVE Contact Person No. 9427302722, 9033315500 | 2023-09-22 | 2023-09-25 09:59 | No | Warranty | V D Electrical & Engineering Co. | B001, Ground Floor, Shalin Height-4, OPP: Lambha Turning, Lambha Vatva Canal Road, Nr, Divine Life International School Narol | Ahmadabad | 382405 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Mistri Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the contactor observed ok. taken on off operation working satisfactory taken screw thread operation obsreved IL1 screw not tighten properly. free replacement. | Repair |  | 9- Service Validated | 2023-09-25 10:00 | 226076558 |  | 17 | INR | 17 | ENM POWER PRODUCTS
WO-11295976 | 104214531 | 2023-09-22 16:56 | 2023-09-22 | MPCB Handle on/off operation issue | 2023-09-22 16:27 | SQD-GV2APN01 | SQD-GV2APN01 | SQD-GV2APN01 |  | GV2APN01 Complaint. Saying GV2APN01 - 24 Qty of MPCB handle has an on/off problem. AB controls--20 June 2023 Site address- Phoenix Mecano India Private Limited 408, Urse ¦ Taluka Maval ¦ Talegaon Urse Road ¦ Pune ¦ 410506 ¦ India Contact Person-Mr.Asaram Deshmukh (8329428108) | 2023-09-22 | 2023-09-25 12:51 | No | Warranty | Phoenix Mecano India Pvt Ltd | Gate No. 408, Taluka Maval Talegaon Urse Road Pune - | Pune | 410507 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Swamesh S_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the MPCB Handle on/off operation issue. opening operation gets normal hard. we checked 4 nos MPCB handle. there is no problem observed in product.this operation performance as per design. | Repair |  | 9- Service Validated | 2023-09-25 12:58 |  |  | 53 | INR | 53 | ENM POWER PRODUCTS
WO-11296151 | 104114370 | 2023-09-23 12:13 | 2023-09-22 |  | 2023-09-22 17:46 | METSEEM6400NGRSCL5 | METSEEM6400NGRSCL5 | METSEEM6400NGRSCL5 | 540180302370 | As per the DOM, The Product is in Warranty. Kindly arrange the site visit. Issue: Reading issue Address Tamara Resorts O by Tamara, 483, Lion's Stop,Kamarajar Road, Sakkarai Chettiyar Colony, Uppilipalayam Coimbatore 641015 Tamil Nadu India Contact person Details: - Mr. Muthu 8072547961 | 2023-09-22 | 2023-09-25 18:16 | No | Warranty | Tamara Resorts | O by Tamara, 483, Lion's Stop,Kamarajar Road, Sakkarai Chettiyar Colony, Uppilipalayam null | Coimbatore | 641015 | Tamil Nadu | India FS ED&I CSP South Team Power Pro Engineering Services Coimbatore | KV ARUNKUMAR_POWER PRO ENGINEERIG SERVICES COIMBATORE | Powerpro Engineering Services | WE HAVE VISITED THE SITE AND INSPECTWE WE FOUND METER ALL THE READING FOUND WORKING OK WE HAVE INFORMED TO CUSTOMER | Repair |  | 9- Service Validated | 2023-09-25 18:18 |  |  | 12 | INR | 12 | ENM POWER PRODUCTS
WO-11301081 | 104131094 | 2023-09-26 17:55 | 2023-09-23 |  | 2023-09-23 11:06 | MVS12N3NW6L | MVS12N3NW6L | MVS12N3NW6L | 10224820094 | As per the Sr. no, The Product is in Warranty. Kindly arrange the site visit. Issue: Spring charging issue Address GURU GOBIND SINGH REFINERY HMEL PHULLOKRI VILLAGE, TALWANDI SABOO TALUKA BATHINDA 151301 Punjab India Contact person Details: - (1St) RAVI SIR, PH-9468459541,(2nd)-AMARESH SINGH, PH-9125585480 | 2023-09-23 | 2023-09-26 17:57 | No | Warranty | GURU GOBIND SINGH REFINERY | HMEL PHULLOKRI VILLAGE, TALWANDI SABOO TALUKA | BATHINDA | 151301 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the acb found working properly. email : id not provided by the customer. | Repair |  | 8- Service Completed | 2023-09-26 18:00 |  |  | 302 | INR | 302 | ENM POWER PRODUCTS
WO-11301143 | 104218695 | 2023-09-25 10:30 | 2023-09-23 |  | 2023-09-23 12:40 | LC1D25BNE | LC1D25BNE | LC1D25BNE |  | As per the invoice, The Product is in Warranty. Kindly arrange the site visit. Issue: coil issue Address Chandigarh Electric and Tool Company Sco 8 Gupta Complex Sai Road Baddi Solan 173205 Himachal Pradesh India Contact person Details: - Mr. Vishal 9805007363 | 2023-09-23 | 2023-09-29 13:49 | No | Warranty | Chandigarh Electric and Tool Company | Sco 8 Gupta Complex Sai Road Baddi | Solan | 173205 | Himachal Pradesh | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Vinod Kumar_Sharma Electric Chandigarh | Sharma Electric works(1003) | checked the contactor found not getting power up. Hence faulty replaced. LC1D25BNE - 1 Nos. email : chandigarhelectric@gmail.com | Repair |  | 8- Service Completed | 2023-09-29 13:52 |  |  | 55 | INR | 55 | ENM POWER PRODUCTS
WO-11301195 | 104229385 | 2023-09-23 17:59 | 2023-09-23 |  | 2023-09-23 13:46 | LC1D25BL | LC1D25BL | LC1D25BL |  | As per the invoice, The Product is in Warranty. Kindly arrange the site visit. Issue: coil issue Address VINAYAKA CONTROLS #30,3rd Cross, Behind Ranganatha Milk Diary Near Peenya 2nd Stage Bengaluru 560026 Karnataka India Contact person Details: - Mr. Dinesh 9731299226 | 2023-09-23 | 2023-09-28 14:04 | No | Warranty | VINAYAKA CONTROLS | #30,3rd Cross, Behind Ranganatha Milk Diary Near Peenya 2nd Stage | Bengaluru | 560026 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Nagaraja G_P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | Inspected and found below mentioned 1)Ref: LC1D09BL S/N:102307 = 2 No'S contactor continuity issue. 2)Ref: A9K71206 S/N:D2328 = 4 No MCB, MCB screw threading issue. Hence we will give same new good warranty replacement ASAP | Repair |  | 8- Service Completed | 2023-09-28 14:04 |  |  | 12 | INR | 12 | ENM POWER PRODUCTS
WO-11301258 | 104229349 | 2023-09-23 17:05 | 2023-09-23 |  | 2023-09-23 16:24 | 30002385 | 30002385 | 30002385 | 54230440845 | As per the Sr. no, The Product is in Warranty. Kindly arrange the site visit. Issue: hardware issue Address Srinivasa Electrical Engineering works Plot No 22, Phaseiv Ida, Cherlapally, Hyderabad, Rangareddy Hyderabad 500051 Telangana India Contact person Details: - Mr. Lakshmana 9440825063 | 2023-09-23 | 2023-09-26 12:00 | No | Warranty | Srinivasa Electrical Engineering works | Plot No 22, Phaseiv Ida, Cherlapally, Hyderabad, Rangareddy | Hyderabad | 500051 | Telangana | India FS ED&I CSP South Team Sumanth Electrical Services Hyderabad | Basanth Reddy_SUMANTH ELECTRICAL SERVICES HYDERABAD | Sumanth Electrical Services | Visited the Site and Inspected the Schneider Electric- 30002385- DM3110-01 No's. Here in our observation we found that the Meter is getting ON. But, while we tried to program the meter thr digits were shipped and getting return to main display on Menu. So,we have replaced with New Meter from ASC Stock and we have checked the ON/OFF Operations which found Ok. Complaint is closed. | Repair |  | 8- Service Completed | 2023-09-26 11:25 |  |  | 15 | INR | 15 | ENM POWER PRODUCTS
WO-11301265 | 104230105 | 2023-09-23 17:21 | 2023-09-23 |  | 2023-09-23 16:38 | INA_ENSET_PANEL | INA_ENSET_PANEL | INA_ENSET_PANEL |  | RE: LTX 2291 LTMCU Display screen not working LTX-2291 During Internal testing we found that one Number LTMU screen has Blur in screen. Due to this Display Number not Shown proper Please take action to resolve the issue Board are under Dispatch Site Address : SCHNEIDER ELECTRIC INFRASTRUCRE LTD . (LV FAT ) Mile Stone -87 , Village , Kotambi, Vadodara ? Halol Highway, Post ? Jarod , Vadodara Gujrat -391510, India Contact Person : Mr. Vineet Kushwaha Mo No: 8882478124 Mr. Amit Parida Mo No: 8249545477 | 2023-09-23 | 2023-09-25 15:11 | No | Warranty | M/s Schneider Electric Infrastructure Ltd. ( LV FAT) | Milestone 87,Village: Kotambi Vadodara-Halol Highway Post : Jarod, Dist. : Vadodara Vadodara, Gujarat - 391510 | VADODARA | 391510 | Gujarat | India FS ED&I CSP West Team Jay Services Vadodara | Ghanshyam Kachiya_Jay Services Vadodara | Jay Services | We visited at site & checked that LTMCU physically ok. We operate with LTMR observed LTMCU display between white line cut digit . So not take reading properly. It is display issue. We recommended to be replace. | Repair |  | 9- Service Validated | 2023-09-25 15:41 |  |  | 28 | INR | 28 | ENM POWER PRODUCTS
WO-11304242 | 104235627 | 2023-09-25 10:37 | 2023-09-25 |  | 2023-09-25 10:05 | CA2KN22M7 | CA2KN22M7 | CA2KN22M7 | 8B2204 | As per the Sr. no, The Product is in Warranty. Kindly arrange the site visit. Issue: coil issue Address OM India Stainless Tube Ltd HB 158, Bihta Road HSIDC Indl. Area Saha, Yamunanagar 135001 Haryana India Contact person Details: - Mr. Nand 9878327576 | 2023-09-25 | 2023-09-25 11:47 | No | Warranty | OM India Stainless Tube Ltd | HB 158, Bihta Road HSIDC Indl. Area Saha, | Yamunanagar | 135001 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the control relay found not working and capacitor found leakage issue & meter found display not showing, Hence faulty replaced. CA2KN22M7 - 1 nos MEHVCSDY150A44 - 1 nos METSEEM6436HCL10RS - 1 nos Email : | Repair |  | 8- Service Completed | 2023-09-25 13:36 |  |  | 106 | INR | 106 | ENM POWER PRODUCTS
WO-11115207 | 103255606 | 2023-08-14 16:36 | 2023-08-14 |  | 2023-08-14 16:13 | MVS08N4NW6A | MVS08N4NW6A | MVS08N4NW6A | 102201130063 | MVS08N4NW6A - 102201130063 nuisance tripping issue | 2023-08-14 | 2023-09-18 16:04 | No | Warranty | IIHMR University | 1, Prabhudayal Marg, Near Sanganer Airport, Jaipur, Rajasthan | Jaipur | 302029 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Sunny Sharma Sharma Electric Jaipur | Sharma Electric Works | New ACB replaced on site. | Repair |  | 8- Service Completed | 2023-09-18 16:07 |  |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11122889 | 102975811 | 2023-09-12 16:15 | 2023-08-15 |  | 2023-08-15 19:52 |  |  |  |  | RMA 102975811 _RO 61362681 | 2023-08-15 | 2023-09-12 16:17 | No | Warranty | Sai Electricals | ,23, Near Fire Station Dolewal, | Ludhiana | 141003 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | new material directly sent by plant | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-12 16:24 |  |  | 10 | INR | 10 | ENM POWER PRODUCTS
WO-11123187 | 103083344 | 2023-09-19 14:39 | 2023-08-19 |  | 2023-08-15 21:46 |  |  |  |  | RMA 103083344_RO 61363413 | 2023-08-15 | 2023-09-20 12:00 | No | Warranty | N K Electricals | 93/4, Govindappa, Naicken Street, | Chennai | 600001 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | =S= Free Order 226069354 has been saved | Assessment/ Inspection | Data Collection | 8- Service Completed | 2023-09-20 09:32 |  |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11305418 | 104237353 | 2023-09-25 16:33 | 2023-09-25 |  | 2023-09-25 15:57 | NA04004V | NA04004V | NA04004V |  | service form no 33 AARAV FRAGRANCES AND FLAVORS PVT. LTD. C 61, TTC Industrial Area, MIDC , Road No. RC1, Thane Belapur road, Vill.: Pawane, Post : Turbhe, Navi Mumbai, Maharashtra 400705 Mr. Prashant Patil 8879524085 WATSN 400A ATS NA04004V 6 Nature of Defect MSEB INPUT SUPPLY LED Is continuously blinking And the operation of ATS is happening in AUTO Mode 14 EMAIL ID vrajlink09@gmail.com MSEB INPUT SUPPLY LED Is continuously blinking. And the operation of ATS is happening in AUTO Mode NEW PRODUCT PURCHASE ON DATED 07.09.2023 DIPSY TRADERS DISTRIBUTOR 23184390050 | 2023-09-25 | 2023-09-27 14:31 | No | Warranty | AARAV FRAGRANCES & FIAVOURS LTD. | PLOT NO. C-61, TTC, MIDC AREA, RC-1,,THANE BELAPUR ROAD, PAWANE | Navi Mumbai | 400705 | Maharashtra | India FS ED&I CSP West Team R P Electrical Mumbai | Shridhar Dongare R P Electrical Mumbai | R P Electrical | Checked 400A ATS found in good condition. Customer has connected stabiliser at out side of ATS. We have observed at site now stabiliser goes ON/OFF mode therefore customer has facing power failure issue. This is not ATS problem. We suggest to to check stabiliser. ATS is manual mode during the observation. | Repair |  | 9- Service Validated | 2023-09-27 14:36 |  |  | 43 | INR | 43 | ENM POWER PRODUCTS
WO-11305351 | 104229937 | 2023-09-26 12:51 | 2023-09-25 |  | 2023-09-25 15:40 | LV525343 | LV525343 | LV525343 |  | As per the issue, The Product is in Warranty. Kindly arrange the site visit. Issue: tripping issue Address Balaji Wafers Before Gyandhara company, Industrial area phase 3, Sandila Hardoi 241204 Uttar Pradesh India Contact person Details: - Mr. Hareram 7486826092 | 2023-09-25 | 2023-09-27 18:42 | No | Warranty | Balaji Wafers | Before Gyandhara company, Industrial area phase 3, Sandila | Hardoi | 241204 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Abhishek Patel Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked the Found MCCB having lose termination issue, so we resolve now MCCB working fine. | Repair |  | 8- Service Completed | 2023-09-28 11:46 |  |  | 80 | INR | 80 | ENM POWER PRODUCTS
WO-11123261 | 103154533 | 2023-08-18 10:06 | 2023-08-15 |  | 2023-08-15 23:03 |  |  |  |  | RMA 103154533_RO 61362575 | 2023-08-15 | 2023-09-15 13:17 | No | Warranty | B R Electricals(500017459) | TC.53/2232, Opposite Police Station | Trivandrum | 695020 | Kerala | India FS ED&I CSP South Team Connect Plus Technologies Cochin | Azif J_Connectplus Technologies Cochin | Connect Plus Technologies | RMA list verified and taken the return materials from BR electricals. | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-15 13:18 |  |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11188086 | 103689091 | 2023-08-31 20:44 | 2023-09-02 |  | 2023-08-31 14:45 | Amico 6 Tr,R407c,DX,Downflow with Heater & Hum | SDA0601AN002 | SDA0601AN002 | C21711000785 | DOP : AMC P : Fan Noise from the Unit S : AMC/SIB | 2023-08-31 | 2023-09-02 19:22 | No | Contract | Shardul Amarchand Mangaldas & Co | 216, 1st Floor, Amarchand Towers, Okhla Industrial Estae, Phase 3 | Delhi | 110020 | Delhi | India FS North1 Cooling CSP Hitech solutions New Delhi | Arvind Kumar_Hitech solutions New Delhi | Hitech Solutions-New Delhi-Delhi | check the unit and found compressor noisy change the compressor and vacuum the machine and gas charging done ok .(R 407 C) | Repair |  | 10- Closed | 2023-09-02 19:40 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two persons is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 35 | INR | 35 | ENM SECURE POWER
WO-11305483 | 104246729 | 2023-09-27 16:29 | 2023-09-25 |  | 2023-09-25 16:36 | LC1D32M7 | LC1D32M7 | LC1D32M7 |  | As per the sr. no(1022064), The Product is in Warranty. Kindly arrange the site visit. Issue: pole open issue Address MUNJAL SPINNERS Near Balaji Temple, Kabri Road Panipat 132103 Haryana India Contact person Details: - Mr. Satish 9034312859 | 2023-09-25 | 2023-09-30 15:52 | No | Warranty | MUNJAL SPINNERS | Near Balaji Temple, Kabri Road | Panipat | 132103 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | checked the contactor found phase missing. Hence faulty, replaced. LC1D32M7 - 1 Nos. Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-30 15:54 |  |  | 165 | INR | 165 | ENM POWER PRODUCTS
WO-11188062 | 103691590 | 2023-08-31 16:28 | 2023-08-31 |  | 2023-08-31 14:38 | Easy UPS 3S 30 kVA 400 V 3:3 UPS for external batteries | E3SUPS30KH | E3SUPS30KH | 9E2311T13403 | DOP : IN Warranty P : Bypass Not Available C : LAB Machine T : Check and tray to reset the alarm but alarm is not clear. S : Onsite | 2023-08-31 | 2023-08-31 19:30 | No | Warranty | Indepth ultrasound centre | SCO 29 Sector 11 | Panchkula | 134109 | Haryana | India FS North2 HBN CSP Essar Engineers Chandigarh | Dan Singh_Essar Engineers Chandigarh | Essar Engineers | UPS showing Bypass not available alarm. Reset the alarm. Now UPS tested on load, its working ok. Also found Earthing Voltage is high. Advised customer to do the needful. UPS registration done. | Repair |  | 10- Closed | 2023-09-01 10:52 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two persons is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 25 | INR | 25 | ENM SECURE POWER
WO-11305484 | 104243813 | 2023-09-25 17:00 | 2023-09-25 |  | 2023-09-25 16:38 | B2ADTLB30160KD | B2ADTLB30160KD | B2ADTLB30160KD | 210125194522220H0009 | RE: PROVIDE COMPLAIN NUMBER @ SHIVSHAKTI ENGINEERS [ thread::41zAmLChfDmrqfmD-YeLcT4:: ] Here is the SL No, pls create WO. Sl No - 210125194522220H0009 Cat No ? B2ADTLB30160KD; Dear sir, Pls provide complain number of below details. CUSTOMER NAME : SHIVSHAKTI ENGINEERS ADRESS : VILLAGE : BHAVDA, INDORE HIGHWAY, AHMEDABAD. CONTACT PERSON : MR ASHOK (M) 9328522128 EMAIL : production.shivshakti4151@gmail.com PRODUCT : SERIES 230- 160 AMP / B2ADTLB30160KD00 QTY : 01 FAULT : ATS NOT TRANSFER. | 2023-09-25 | 2023-09-25 17:03 | No | Warranty | Shivshakti Engineers | Survey No. 1187, 88, 89, Village Bh | Ahmedabad | 382350 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Ritesh Prajapati_Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked above ATS physically observed ok. Trial taken ats not transfer in automode. Set dip switch setting as per customer requirement and trial taken ATS transfer satisfactory source 1 to source 2 and source 2 to source 1. Problem due to dip switch setting not proper. | Repair |  | 8- Service Completed | 2023-09-25 17:03 |  |  | 53 | INR | 53 | ENM POWER PRODUCTS
WO-11305681 | 104240574 | 2023-09-26 12:13 | 2023-09-26 |  | 2023-09-25 18:32 | METSEPM1125HCL05RD | METSEPM1125HCL05RD | METSEPM1125HCL05RD |  | As per the DOM, The Product is in Warranty. Kindly arrange the site visit. Issue: reading mismatch issue Address RMZ One Paramount 110, Mount Poonamalle High Road, Porur Chennai 600116 Tamil Nadu India Contact person Details: - Mr. Suresh 9884070689 | 2023-09-25 | 2023-09-26 18:00 | No | Warranty | RMZ One Paramount | 110, Mount Poonamalle High Road, Porur null | Chennai | 600116 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | site visit Done | Repair |  | 8- Service Completed | 2023-09-26 20:33 |  |  | 3 | INR | 3 | ENM POWER PRODUCTS
WO-11310306 | 104269704 | 2023-09-27 16:19 | 2023-09-26 |  | 2023-09-26 12:08 | LV563306 | LV563306 | LV563306 | TC-2023-W06-3U2 | LV563306 - again Tripping Issue coming even after tightening the terminals TC-2023-W06-3U2 LV563306 - again Tripping Issue coming even after tightening the terminals TC-2023-W06-3U2 Mr. Rahul Garg 09050070354 Malakshmi Enterprises Address chajjpur kalan bapoli road Panipat 132103 | 2023-09-26 | 2023-09-28 16:56 | No | Warranty | Malakshmi Enterprises | chajjpur kalan bapoli road | Panipat | 132103 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | checked the mcb found dolly free. hence faulty, replaced. EZ9F76132 - 1 Nos. Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-28 16:59 |  |  | 165 | INR | 165 | ENM POWER PRODUCTS
WO-11310730 | 104267193 | 2023-09-26 14:32 | 2023-09-26 |  | 2023-09-26 14:18 | METSEEM6436HCL10NC | METSEEM6436HCL10NC | METSEEM6436HCL10NC |  | CTR & Meter Complaint - 26092023 - Swift Name of Customer The Marsden Bakubhai & Sons Pvt. Ltd Site Address Darshan', Near Parimal Railway Underpass, Paldi, Ahmedabad- 380 007 Gujarat Name of contact person at site MR. ASHWIN SOLANKI Contact Phone / Mob. No: 99789 90416 Defective product details METSEEM6436HCL10NC-1 NOS, LC1E2510M7-1 NOS Nature of Defect Display not working, Screw Problem Shutdown availability if applicable YES Warranty status YES Commissioned / Installed date Serial No: or DOM of the product Name & phone No: of person registering the complaint Bhavesh Parmar - 9512900514 INVOICE NO WITH DATE 9008633814 - 06.07.2023, 9008567289 - 22.05.2023 | 2023-09-26 | 2023-09-29 09:47 | No | Warranty | The Marsden Bakubhai &Sons Pvt. Ltd | 'Darshan', Near Parimal Railway Underpass,Paldi, Ahmedabad | AHMEDABAD | 380 007 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Mistri Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physically observed ok. METSEEM6436HCL10NC SR NO : 280223 Observed customer meter no display . so we give the supply but meter not working properly. so may be internal problem so free replacement. | Repair |  | 8- Service Completed | 2023-09-29 09:48 | =S= Consig Fill up 226088847 |  | 17 | INR | 17 | ENM POWER PRODUCTS
WO-11316624 | 104300619 | 2023-09-28 16:52 | 2023-09-27 |  | 2023-09-27 13:52 | LV525313 | LV525313 | LV525313 | 10-2023-w22-2 | As per the Sr. no, The Product is in Warranty. Kindly arrange the site visit. Issue: Tripping issue Address J.S Metals Plot no. 476 sector 8 IMT MANESAR GURUGRAM 122052 Haryana India Contact person Details: - Mr. Gourav 8860713869 | 2023-09-27 | 2023-09-28 16:53 | No | Warranty | J.S Metals | Plot no. 476 sector 8 IMT MANESAR null | GURUGRAM | 122052 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mccb found working ok. Email : id not provided by customer . | Repair |  | 8- Service Completed | 2023-09-28 17:00 |  |  | 55 | INR | 55 | ENM POWER PRODUCTS
WO-11317117 | 104309908 | 2023-09-28 10:59 | 2023-09-28 |  | 2023-09-27 16:34 | METSEEM6436HCL10RS | METSEEM6436HCL10RS | METSEEM6436HCL10RS |  | Re: EM6436H Meter R Phase CT Terminal thread Problem, Case: 104267472, [ thread::mutI3jq8dlCkEYMl_LobRz4:: ] We have purchased EM6436H meter, The Meter R phase CT Terminal Thread problem, Kindly replace the meter. Meter Model No: EM6436H,Cl:1.0,RS485 S/N: 540420250029 DOM : 25/7/2023 Our New Office Address OM SARAVANA ELECTRICALS No.T-22, First Floor, Gnanaoli Street, Jaffarkhanpet Chennai-600 083 Ph No: 7358161880 | 2023-09-27 | 2023-09-30 16:30 | No | Warranty | Om Saravana Electricals | T-22,Gnanaoli street,jaffarkhanpet,Chennai- | CHENNAI | 600083 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Visited done - Replacement | Repair |  | 8- Service Completed | 2023-09-30 16:53 |  |  | 15 | INR | 15 | ENM POWER PRODUCTS
WO-11320214 | 104329590 | 2023-09-29 10:53 | 2023-09-28 |  | 2023-09-28 10:26 | LC1D32M7 | LC1D32M7 | LC1D32M7 |  | As per the Sr. no(102147 2), The Product is in Warranty. Kindly arrange the site visit. Issue: pole open issue Address A2Z power solution 1/51 refinery nagar township Mathura 281006 Uttar Pradesh India Contact person Details: - Mr. Puspinder 9719212273 | 2023-09-28 | 2023-09-29 15:47 | No | Warranty | A2Z power solution | 1/51 refinery nagar township | Mathura | 281006 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Monu Pandey_Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found contactor having dust issue, so we open and clean. now contactor working fine. | Repair |  | 8- Service Completed | 2023-09-29 16:01 |  |  | 390 | INR | 390 | ENM POWER PRODUCTS
WO-11321718 | 104314112 | 2023-09-28 15:14 | 2023-09-28 |  | 2023-09-28 10:58 | LRD340 | LRD340 | LRD340 |  | Name of Customer:-BRADY & MORRIS ENGG.CO.LTD Site Address:-PLOT NO. 326/B, OPP. GOVT. BORE WELL,SARSA-KANERA ROAD, SARSA PATIA, VILL-KANERA, TA-MATAR Nadiad, 387540 Name of contact person at site:-TUSHAR PRAJAPATI Contact Phone / Mob. No:-9687840481.00 Defective product details:-LRD340(1 QTY) Invoice no.:-PSI/23007107(13/09/2023) Nature of Defect:-Not Working Ok | 2023-09-28 | 2023-09-29 09:51 | No | Warranty | BRADY & MORRIS ENGG.CO.LTD | PLOT NO. 326/B, OPP. GOVT. BORE WELL,SARSA-KANERA ROAD, SARSA PATIA, VILL-KANERA, TA-MATAR Nadiad null | KHEDA | 387540 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Mistri Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physically observed ok. LRD365 SR NO : 7Q23251 physically observed ok . but mounting box damaged obseved. so free replacment for customer satisfaction. LRD340 SR NO : 7Q22495 physically obaseved ok but nc no not workingg underwarranty status free replacement for customer satisfaction. | Repair |  | 8- Service Completed | 2023-09-29 09:52 | =S= Consig Fill up 226093246 |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11188935 |  | 2023-09-30 21:26 | 2023-09-16 |  | 2023-08-31 18:44 | InRow RD, 300mm, Air Cooled, 220-240V, 50Hz | ACRD101 | ACRD101 | JK1525000963 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-08-31 | 2023-07-06 12:00 | No | Contract | IBM Embassy Tech Zone | Plot No. Z-104/105/106, Dahej SEZ II Dahej Taluka Vagra, Dist. Bharuch | Bharuch | 392130 | Gujarat | India FS West2 Cooling CSP DECENT HVAC SYSTEM Gandhinagar | Mickey Kabrawala DECENT HVAC SYSTEM Gandhinagar | DECENT HVAC SYSTEM | Preventive Maintenance (> 240 Km) | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-30 21:35 |  |  | 264 | INR | 264 | ENM SECURE POWER
WO-11188936 |  | 2023-09-30 21:28 | 2023-09-16 |  | 2023-08-31 18:44 | InRow RD, 300mm, Air Cooled, 220-240V, 50Hz | ACRD101 | ACRD101 | JK1525000958 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-08-31 | 2023-07-06 12:00 | No | Contract | IBM Embassy Tech Zone | Plot No. Z-104/105/106, Dahej SEZ II Dahej Taluka Vagra, Dist. Bharuch | Bharuch | 392130 | Gujarat | India FS West2 Cooling CSP DECENT HVAC SYSTEM Gandhinagar | Mickey Kabrawala DECENT HVAC SYSTEM Gandhinagar | DECENT HVAC SYSTEM | Preventive Maintenance (> 240 KM) | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-30 21:41 |  |  | 264 | INR | 264 | ENM SECURE POWER
WO-11322186 | 104333059 | 2023-09-28 15:17 | 2023-09-28 |  | 2023-09-28 13:50 | MVS16N4NW6L | MVS16N4NW6L | MVS16N4NW6L | 10224720012 | RE: COMPLAIN @ Unifrex India Pvt.Ltd., Case: 103390511,, Case: 103794419, [ thread::Ta0YGjU0coaydLQP1pXlKj4:: ] Dear Akshay sir, Please issue a work order against this subjected case id. @Vivek M. Khaire, Please assign this case to Vardhamaan electrosoft. Regards, Pradeep patil | 2023-09-28 | 2023-09-29 22:30 | No | Warranty | Unifrax India Limited | 99km Milestone Surendranagar Highway Lakhatar | Surendranagar | 382775 | Gujarat | India FS ED&I CSP West Team VARDHAMAN ELECTROSOFT Vadodara | MAHENDRA SINGH VARDHAMAN ELECTROSOFT Vadodara | VARDHAMAN ELECTROSOFT | we visited the site and check that breaker is physically ok we remove that breaker from panel After this open Arc suit and clean the breaker contact , Arc suit from CRC . after this we do the CRM test and getting all value in micro ohm . all CRM value is under range | Repair |  | 8- Service Completed | 2023-09-29 16:10 |  |  | 760 | INR | 760 | ENM POWER PRODUCTS
WO-11022240 | 102706832 | 2023-07-24 12:41 | 2023-07-25 |  | 2023-07-22 22:02 | LC1E0901B7 | LC1E0901B7 | LC1E0901B7 | invoice shared | Reg schneider contactor LC1E0901B7 - operation issue Site Address: SARAVANA ELECTRONICS SARAVANA TOWERS 7/26A, Thiruvalluvar Nagar, Mudangiyar road, Rajapalayam-626117 Phone: 04563 224588 Mr. V.R Rupasandyaa Cell: 9363118588, 9363118587 | 2023-07-22 | 2023-09-04 09:02 | No | Warranty | SARAVANA ELECTRONICS | 7/26A, Thiruvalluvar Nagar, Mudangiyar road, Rajapalayam null | Virudhunagar | 626117 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | George KJ_Omicon Engineering Madurai | Omicon Engineering | Inspected the site and cheked the contactor found B phase pole open condition . | Repair |  | 8- Service Completed | 2023-09-04 09:06 | Hi Team, Material booked zfre Zvo : 225908957 |  | 100 | INR | 100 | ENM POWER PRODUCTS
WO-11188937 |  | 2023-09-30 21:32 | 2023-09-16 |  | 2023-08-31 18:44 | InRow RD, 300mm, Air Cooled, 220-240V, 50Hz | ACRD101 | ACRD101 | JK1525000953 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-08-31 | 2023-07-06 12:00 | No | Contract | IBM Embassy Tech Zone | Plot No. Z-104/105/106, Dahej SEZ II Dahej Taluka Vagra, Dist. Bharuch | Bharuch | 392130 | Gujarat | India FS West2 Cooling CSP DECENT HVAC SYSTEM Gandhinagar | Mickey Kabrawala DECENT HVAC SYSTEM Gandhinagar | DECENT HVAC SYSTEM | Preventive Maintenance (> 240 Km) | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-30 21:41 |  |  | 264 | INR | 264 | ENM SECURE POWER
WO-11322555 | 104338316 | 2023-09-28 18:15 | 2023-09-28 |  | 2023-09-28 16:40 | LC1E2501M7 | LC1E2501M7 | LC1E2501M7 |  | REQUIRE CASE NO. A9N3P40C - 01 REASON : DOLLY FREE SR.NO. DD2023-W27-1-3 2] LC1E2501M7- 01 REASON : AUX CONTACT PROBLEM SR.NO. 1023266 Technicare Electronics 302, Sarita Complex Dhebar Road, RAJKOT. - 360002 MO. 63560 22623 | 2023-09-28 | 2023-09-28 18:31 | No | Warranty | Technicare Electronics | 302, Sarita Complex Dhebar Road | RAJKOT | 360002 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | RAHUL PARMAR JKS Rajkot | JKS Engineering Co. | Check a9n3p40c mcb body and terminal side not any damage mcb dolly free.check lc1e2501m7 contactor terminal side not any damage contactor nc contact not working 1nos contactor replacement. | Repair |  | 8- Service Completed | 2023-09-29 10:14 | =S= Consig Fill up 226090385 |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11189369 |  | 2023-09-06 14:42 | 2023-09-05 |  | 2023-08-31 18:53 | APC Smart-UPS VT 40kVA 400V, w/Start-Up 5X8, Internal Maintenance Bypass, & Para | SUVTP40KHS | SUVTP40KHS | PS1218330400 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-08-31 | 2023-09-14 13:33 | No | Contract | Jindal Steel & Power Limited | Nisha Campus Chandi Pada ROad Village Nisha P.O. Nisa , Angul | Angul | 759222 | Odisha | India FS East HBN CSP Disha Computers Bhubneshwar | TARUN PARIDA_Disha Computers Bhubneshwar | Disha Computers-Bhubaneshwar | PM SERVICE DONE , ALL PARAMETERS ARE OK , UPS WORKING NORMAL | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-14 13:36 |  |  | 160 | INR | 160 | ENM SECURE POWER
WO-11322574 | 104337063 | 2023-09-29 15:00 | 2023-09-28 | BBT Flash Issue | 2023-09-28 16:50 | GCR_PWR_BUSWAY | GCR_PWR_BUSWAY | GCR_PWR_BUSWAY |  | Re: PO NO 50165/SD/0002 LTB 3649 : Cummins: 6300 A BUSDUCT PIESE FOUND FAULTY, Case: 104305150, [ BBT flash issue Invoice : 9008592002--July 2023 ACE ENGINEERING SOLUTIONS INDIA PRIVATE LIMITED PLOT NO PAP-K-11, CHAKAN INDUSTRIAL AREA PHASE-II, KHALUMBRE KHED, Pune ? 410501, MAHARASHTRA, INDIA Name- Sandeep Pawar Email ID- projectbusduct@marineelectricals.com Contact Number-82906 35389 | 2023-09-28 | 2023-09-29 17:49 | No | Warranty | ACE ENGINEERING SOLUTIONS INDIA PRIVATE LIMTED | PLOT No- PAP K 11, Village Khalumbre, Chakan MIDC Phase 2 | pune | 410501 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Swamesh S_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the BBT Flash Issue . checked flange end flash found B phase and body. then we checked values continuity by meager. it's a satisfactory. this problem observed maybe some metallic bar comes across the body. customer is not accepted this material. | Repair |  | 8- Service Completed | 2023-09-30 16:28 |  |  | 55 | INR | 55 | ENM POWER PRODUCTS
WO-11189370 |  | 2023-09-06 14:43 | 2023-09-05 |  | 2023-08-31 18:53 | APC Smart-UPS VT 40kVA 400V, w/Start-Up 5X8, Internal Maintenance Bypass, & Para | SUVTP40KHS | SUVTP40KHS | PS1218330402 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-08-31 | 2023-09-14 13:38 | No | Contract | Jindal Steel & Power Limited | Nisha Campus Chandi Pada ROad Village Nisha P.O. Nisa , Angul | Angul | 759222 | Odisha | India FS East HBN CSP Disha Computers Bhubneshwar | TARUN PARIDA_Disha Computers Bhubneshwar | Disha Computers-Bhubaneshwar | PM SERVICE DONE , ALL PARAMETERS ARE OK , UPS WORKING NORMAL | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-14 13:39 |  |  | 0 | INR | 0 | ENM SECURE POWER
WO-11189371 |  | 2023-09-15 12:50 | 2023-09-15 |  | 2023-08-31 18:53 | Easy UPS 3S 40 kVA 400 V 3:3 UPS for external batteries | E3SUPS40KH | E3SUPS40KH | 9E1940T10321 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-08-31 | 2023-09-15 12:50 | No | Contract | HV AXLES Limited C/O Tata Motors Limited | Gamharia, Jamshedpur, null | JAMSHEDPUR | 831010 | Jharkhand | India FS East HBN CSP Power Solution Ranchi | KAMRANUL HAQUE_Power Solution Ranchi | Power Solution-Ranchi | Pm service done and dust clean UPS working normal call has been closed | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-15 14:14 |  |  | 133 | INR | 133 | ENM SECURE POWER
WO-11189376 |  | 2023-09-06 20:22 | 2023-09-05 |  | 2023-08-31 18:54 | InRow RD, 300mm, Air Cooled, 220-240V, 50Hz | ACRD101 | ACRD101 | UK1110110402 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-08-31 | 2023-09-23 07:04 | No | Contract | Jindal Steel & Power Limited | Nisha Campus Chandi Pada ROad Village Nisha P.O. Nisa , Angul | Angul | 759222 | Odisha | India FS East Cooling CSP Cool Care Refrigerant Bhubaneshwar | Debasis Sahoo_Cool Care Refrigerant Bhubaneshwar | Cool Care Refrigerant | PM DONE | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-23 07:04 |  |  | 2 | INR | 2 | ENM SECURE POWER
WO-11189379 |  | 2023-09-08 13:21 | 2023-09-08 |  | 2023-08-31 18:54 | APC Smart-UPS VT 40kVA 400V, w/Start-Up 5X8, Internal Maintenance Bypass, & Para | SUVTP40KHS | SUVTP40KHS | PS1305131044 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-08-31 | 2023-09-14 13:41 | No | Contract | Jindal Steel & Power Limited | Nisha Campus Chandi Pada ROad Village Nisha P.O. Nisa , Angul | Angul | 759222 | Odisha | India FS East HBN CSP Disha Computers Bhubneshwar | TARUN PARIDA_Disha Computers Bhubneshwar | Disha Computers-Bhubaneshwar | PM SERVICE DONE , ALL PARAMETERS ARE OK , UPS WORKING NORMAL | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-14 13:45 |  |  | 160 | INR | 160 | ENM SECURE POWER
WO-11146040 | 103413305 | 2023-08-22 11:12 | 2023-08-21 |  | 2023-08-21 17:37 | 51207 | 51207 | 51207 | RN-2023-W4-3 | complaint number required Dear Team, Shivalic Power Control Private Limited Plot No.- 72, Sector- 68, IMT aridabad.Haryana Mr.Mohan 9718388309 Product : 51207 Serial Number : RN-2023-W4-3 not power up -- *WITH REGARDS-* Sarabjit Singh | 2023-08-21 | 2023-09-26 15:17 | No | Warranty | Shivalic Power Control Private Limited | Plot No.- 72, Sector- 68, IMT null | Faridabad | 121004 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the relay found not power up, Hence faulty replaced 51207 - 8 nos Email : id not provided by customer . | Repair |  | 8- Service Completed | 2023-09-12 16:12 |  |  | 52 | INR | 52 | ENM POWER PRODUCTS
WO-11333119 | 104381624 | 2023-09-30 13:07 | 2023-09-30 |  | 2023-09-30 11:26 | METSEEM6436HCL10RS | METSEEM6436HCL10RS | METSEEM6436HCL10RS |  | METSEEM6436HCL10RS Srn : DOM 12-10-2022 Not Display / Not powering ON METSEEM6436HCL10RS Srn : DOM 12-10-2022 Not Display / Not powering ON Hotel Valley Orchid Near Modern Hospital Rajbagh,SRINAGAR, Jammu and Kashmir. PIN 190001 Md. ASIF 9419340850 Asif.jk@rediffmail.com | 2023-09-30 | 2023-09-30 13:09 | No | Warranty | Hotel Valley Orchid | Shop No. 132 / 86 Ravindra Bazar, Near Ravindra temple Temple | Srinagar | 190001 | Jammu and Kashmir | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Ram Ashish Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the meter found Not Display / Not powering ON and mcb found two mcb dolly free,1mcb phase missing. Hence faulty replaced. METSEEM6436HCL10RS - 1 Nos. EZ9F71263 - 3 Nos. email : asif.jk@rediffmail.com | Repair |  | 8- Service Completed | 2023-09-30 16:58 | 226080509 zfre booked. |  | 650 | INR | 650 | ENM POWER PRODUCTS
WO-11026042 | 102743177 | 2023-07-25 14:02 | 2023-07-24 |  | 2023-07-24 17:57 | LV432677 | LV432677 | LV432677 | 1021323 | Regarding 1 no 400A MCCB motorized malfunctioning at Howrah Station, KMRCL As Per The serial number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Howrah railway station Howrah railway station,platform #17,Howrah Howrah 711101 West Bengal India Contact Person Details:- Contact Person- Mr Abhay Kumar Contact No 92058 83471 Product and Issue:- LV432677 Serial number:- 1021323 Continuously getting spring charge not getting cut out by limit switch | 2023-07-24 | 2023-09-05 10:18 | No | Warranty | Howrah railway Station | New Complex Opp Dcrb null | Kolkata | 711101 | West Bengal | India FS ED&I CSP East Team SREYAM SERVICES BHATPARA | AMIT BHATTACHARYA_SREYAM SERVICES BHATPARA | Sreyam Services(8513) | AFTER SITE VISIT FOUND MOTOR MECHANISHM REPLACED BY NEW ONE AND DEFFECTIVE MATERIAL IS COLLECTED. | Repair |  | 9- Service Validated | 2023-09-05 10:24 |  |  | 15 | INR | 15 | ENM POWER PRODUCTS
WO-11222120 | 103824373 | 2023-09-07 12:05 | 2023-09-06 |  | 2023-09-06 17:54 | EZ9F71463 | EZ9F71463 | EZ9F71463 |  | MCB Complaint From Noida : MCB Dolly Free | 2023-09-06 | 2023-09-12 15:58 | No | Warranty | Gajendar Pal | C-100, Sector-65 | Ghaziabad | 201301 | Uttar Pradesh | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mcb found dolly free , Hence faulty replaced EZ9F71463 - 1 nos Email : id not provided by customer . | Repair |  | 9- Service Validated | 2023-09-12 16:00 |  |  | 52 | INR | 52 | ENM HOME DISTRIBUTION
WO-11147128 | 103402762 | 2023-08-23 11:22 | 2023-08-21 |  | 2023-08-21 21:05 |  |  |  |  | RMA 103402762_RO 61356785 | 2023-08-21 | 2023-09-21 12:00 | No | Warranty | Sunrise Electricals | 5,Sanskar Bharti Shopping Centre, Ashapuri Road, Dudhiya Talav | Surat | 396445 | Gujarat | India FS ED&I CSP West Team SHIV SAI ELECTRICALS Vapi | SHIVAM LAD SHIV SAI ELECTRICALS VAPI | shivsai electricals | =S= Free Order 226074438 has been saved | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-21 10:49 | =S= Free Order 226074438 has been saved |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11191403 |  | 2023-09-01 10:51 | 2023-09-01 |  | 2023-09-01 09:51 | TUAV1321AN003 | TUAV1321AN003 | TUAV1321AN003 | C22018000776 | PM | 2023-09-01 | 2023-09-20 12:04 | No | Contract | Johnson Matthey chemicals India Pvt Limited | Plot No: 12, Sector-3 IMT Manesar | Gurgaon | 122050 | Haryana | India FS North1 Cooling CSP Smart Engineering Services Delhi | Sunil Kumar Smart Engineering Services Delhi | Smart Engineering Services | REGULAR PM | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-20 12:08 |  |  | 64 | INR | 64 | ENM SECURE POWER
WO-11305512 | 104247076 | 2023-09-26 10:09 | 2023-09-25 |  | 2023-09-25 16:46 | A9N4P63C | A9N4P63C | A9N4P63C |  | DOP: 5/2/2023 A9N4P63C Qty:1 P: Dolly free | 2023-09-25 | 2023-09-27 11:06 | No | Warranty | Vinu Rati | A217 Sushant lok 2 Sec 55, 56 Metro Station Near Vasthu Apt | Gurgaon | 122011 | Haryana | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the MCB and found MCB continuity R and Y phase missing . So MCB is faulty. We replace the faulty MCB with new. Mail Id. veenurathee1909@gmail.com | Repair |  | 8- Service Completed | 2023-09-27 11:13 |  |  | 53 | INR | 53 | ENM HOME DISTRIBUTION
WO-11191405 |  | 2023-09-01 10:54 | 2023-09-01 |  | 2023-09-01 09:51 | Leonardo EvDXR407cTDAV0721A Downflow With Heater and Humidifier | TDAV0721AN002 | TDAV0721AN002 | JK2205001617 | PM | 2023-09-01 | 2023-09-06 14:19 | No | Contract | SGT University | Gurgaon-Badli Road Chandu, Budhera Shree Guru Gobind Singh Tricentenary University Gurugram Delhi NCR | Gurgaon | 122505 | Haryana | India FS North1 Cooling CSP Smart Engineering Services Delhi | Taranjeet Singh_Smart Engineering Services Delhi | Smart Engineering Services | REGULAR PM | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-06 14:24 |  |  | 45 | INR | 45 | ENM SECURE POWER
WO-11305529 | 104247343 | 2023-09-26 11:55 | 2023-09-25 |  | 2023-09-25 16:56 | P1001_6_DG_N | P1001_6_DG_N | P1001_6_DG_N |  | DOP: 4/2/2023 Livia Regulator Qty: 1 P: Not Working Kindly check invoice at site | 2023-09-25 | 2023-09-27 13:14 | No | Warranty | Rajeev Kumar | A 2/151 Ground floor Safdarjang Enclave | Delhi | 110029 | Delhi | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the fan regulator and found fan regulator have output problem, We replace the faulty fan regulator with new. | Repair |  | 8- Service Completed | 2023-09-27 13:17 |  |  | 27 | INR | 27 | ENM HOME DISTRIBUTION
WO-11191404 |  | 2023-09-01 10:55 | 2023-09-01 |  | 2023-09-01 09:51 | Leonardo EvDXR407cTDAV0721A Downflow With Heater and Humidifier | TDAV0721AN002 | TDAV0721AN002 | JK2205001618 | PM | 2023-09-01 | 2023-09-06 14:27 | No | Contract | SGT University | Gurgaon-Badli Road Chandu, Budhera Shree Guru Gobind Singh Tricentenary University Gurugram Delhi NCR | Gurgaon | 122505 | Haryana | India FS North1 Cooling CSP Smart Engineering Services Delhi | Taranjeet Singh_Smart Engineering Services Delhi | Smart Engineering Services | REGULAR PM | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-06 14:49 |  |  | 45 | INR | 45 | ENM SECURE POWER
WO-11309925 | 104267910 | 2023-09-26 12:03 | 2023-09-26 |  | 2023-09-26 10:53 | A9N3P20C | A9N3P20C | A9N3P20C |  | A9N3P20C ( 20 Amps MCB) Sr No D 2221 June 2022 Not Passing Current Phase Missing Raja Poultry Farms GT Road, Vill Badal Dabwali Punjab PIN 125104 Mr. Kamal Kumar 7087878966 | 2023-09-26 | 2023-09-26 12:20 | No | Warranty | Raja Poultry Farms | GT Road, Vill Badal Dabwali | Dabwali | 125104 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the MCB-(A9N3P20C ) found Not Passing Current / Phase Missing and EZ9F71463 found 1mcb dolly frree and 3 mcb not giving output. and Control relay found not working. Hence faulty replaced. A9N3P20C - 2 Nos. EZ9F71463 - 4 Nos. CA2KN40M7 - 1 Nos. email : kkdab86@yahoo.com | Repair |  | 8- Service Completed | 2023-09-26 17:13 |  |  | 187 | INR | 187 | ENM HOME DISTRIBUTION
WO-11310152 | 104247271 | 2023-09-27 10:54 | 2023-09-26 |  | 2023-09-26 11:10 | X1001WH | X1001WH | X1001WH |  | DOP: 2/6/2023 Opale Switches Qty:2 P: Customer is facing issues Opale 32 Ampere switches getting complaint frequently Abdul Jaleel VP Vellap house ,Vellap PO Trikaripur Kasargod Dt Pin 671310 Abdul Jaleel VP 9447361757 | 2023-09-26 | 2023-09-28 15:35 | No | Warranty | Abdul Jaleel v p | Vellap House Vellap po, Thrikaripur Kasaragod | Kasaragod | 671310 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Rejilesh APSMarketingCompany Calicut | APS Marketing Company | visit this site found opela 32dp switch crack issue opela 32dp switch replaced 3nos | Repair |  | 8- Service Completed | 2023-09-28 15:37 |  |  | 135 | INR | 135 | ENM HOME DISTRIBUTION
WO-11310490 | 104269478 | 2023-09-26 13:28 | 2023-09-28 | replacement material arranged from gear tech ZV excess Stock | 2023-09-26 12:53 | UNS162SW2M_WE | UNS162SW2M_WE | UNS162SW2M_WE |  | DOP: 2/6/2023 1. UNS162SW2M WHITE 16A 2WAY SWITCH 2MD UNICA - 1 nos 2. UNS6BPL2M WHITE 6A BELLPRESS WITH IND UNICA - 1 nos P: Not Working Mr. RIJO VARKEY PAINUNKAL HOUSE, PIPE LINE ROAD, SN PURAM, ALUVA. Mr. JAMES 8848459913 | 2023-09-26 | 2023-09-28 14:57 | No | Warranty | JAMES JAMES |  | Ernakulam | 683101 | Kerala | India FS ED&I CSP South Team Geartech Electric Cochin | Vineesh M_Geartech Electric Cochin | Geartech Electric ASC for Schneider Electric | Inspected the switch found the problem with struck, replaced the defective switch, and rectified the problem. replacement material arranged from gear tech ZV excess Stock. | Repair |  | 8- Service Completed | 2023-09-28 14:57 |  |  | 18 | INR | 18 | ENM HOME DISTRIBUTION
WO-11310544 | 104271910 | 2023-09-27 13:38 | 2023-09-26 |  | 2023-09-26 13:08 | A9N3P10C | A9N3P10C | A9N3P10C |  | 3 pole 10 amps No continuity in 2 pole Supply 2 months back to customer . | 2023-09-26 | 2023-09-27 13:40 | No | Warranty | Vijay Sales | shop no 2 Zuco complex vishwakarma chowk mirrorganj | Ludhiana | 141003 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | checked the mcb found phase missing. hence faulty, replaced. A9N3P10C - 1 Nos. Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-27 17:31 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11310546 | 104267863 | 2023-09-26 16:30 | 2023-09-26 |  | 2023-09-26 13:11 | UNS62SW1M_GY | UNS62SW1M_GY | UNS62SW1M_GY |  | DOP: 21/4/2023 Unicapure two way switch grey UNS62SW1M_GY Qty:8 P: Not Working VIPIN VIPIN BHAVANAM KALAYAPURAM P O KOTTARAKKARA KOLLAM 691560 9074087326,' 9447034953 '9526082492 | 2023-09-26 | 2023-09-30 09:06 | No | Warranty | Vipin Vipin |  | Kollam | 691560 | Kerala | India FS South2 ED&I CSP PrinterPeople Cochin | Renjith PR PrinterPeople Cochin | PRINTER PEOPLE-COCHIN | visited site and found problem with unwanted voltage in phase line in 2 way switch and bulb on with low light always. checked replacing the switch same issue continues.. informed customer to check wiring issue at site. | Repair |  | 8- Service Completed | 2023-09-30 17:08 |  |  | 165 | INR | 165 | ENM HOME DISTRIBUTION
WO-11310825 | 104276067 | 2023-09-27 11:12 | 2023-09-26 |  | 2023-09-26 14:58 | A9R12491 | A9R12491 | A9R12491 |  | DOP: 23/9/2023 A9R12491 Qty:2 P: Tripping issue INNOMAC ENGINEERING IND. PVT. LTD.(HARMONY) SURVEY NO. 48/1 & 48/2, CHIKKABIDARAKALLU, NH-4, TUMKUR ROAD, BENGALURU YOGESH B.S. - 6362905526 BHAVINBHAI- 8866201001 | 2023-09-26 | 2023-09-27 14:34 | No | Warranty | INNOMAC ENGINEERING IND. PVT. LTD | SURVEY NO. 48/1 & 48/2,CHIKKABIDARAKALLU,NH-4,TUMKUR ROAD | BENGALURU | 560073 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Nagaraja G_P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | Visited the site and inspected the 1) Ref: A9R12491 = S/L: EE-2022-W26 = 1 No RCCB. We have checked the RCCB with load RCCB getting tripped, due to as per RCCB 100MA current was crossed it is not RCCB problem. | Repair |  | 8- Service Completed | 2023-09-27 14:34 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11310845 | 104276294 | 2023-09-26 23:12 | 2023-09-26 | Validated By Prashant | 2023-09-26 15:04 | IN8486_32_BZ | IN8486_32_BZ | IN8486_32_BZ |  | 32 amps Zencelo dp switch mot working purchased 4day back only In8486 | 2023-09-26 | 2023-09-27 16:53 | No | Warranty | Sanjay randaul | andheri west 7 bunglows , jewel shoping center , shop no 13 | Mumbai | 400061 | Maharashtra | India FS ED&I CSP West Team S K SERVICES Mumbai | Ganesh Tati_S K SERVICES Mumbai | S.K. Services (10237) | We visited the site Product Ref No:-IN8486/32-1Nos Serial No:-23251 We check the material 32A DP switch is properly not operating We replace the product Our stock replacement. | Repair |  | 9- Service Validated | 2023-09-27 16:53 |  |  | 20 | INR | 20 | ENM HOME DISTRIBUTION
WO-11311033 | 104278658 | 2023-09-28 15:46 | 2023-09-26 |  | 2023-09-26 16:18 | A9N16204 | A9N16204 | A9N16204 |  | Sept 2022 purchases 63 amp 30 ma single pole | 2023-09-26 | 2023-09-28 15:48 | No | Warranty | Manish yadav | village + PO , lookhi , dist reqari | Reqari | 123303 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the 2 nos Rccb found 1 nos ok and 1 nos found dolly free but as per serial number found out of warranty, Hence no replacement given to customer. Email : id not provided by customer . | Repair |  | 8- Service Completed | 2023-09-28 15:56 |  |  | 85 | INR | 85 | ENM HOME DISTRIBUTION
WO-11314539 | 104280568 | 2023-09-28 11:27 | 2023-09-28 |  | 2023-09-27 09:50 | IH101ZWIFI | IH101ZWIFI | IH101ZWIFI |  | DOP: 20/9/2023 Fan Speed Controller 02 IR controller 01 2 Channel Dimmer 03 Automation Gateway (CAM ID) 01 IH1200010F IH101ZW2IR IH12000020 IH101ZWIFI P: Installation Customer Name ? Rinnku R Nigam Contact No ? 9999996208 Address ? B-56 Derawal Nagar Delhi -09 | 2023-09-27 | 2023-09-28 23:27 | No | Commercial Action - Sales | Rinnku R Nigam |  | Delhi | 110009 | Delhi | India FS ED&I CSP North Team Seamtek International Pvt. Ltd. GHAZIABAD | Satish Raika Seamtek International Pvt. Ltd. GHAZIABAD | Seamtek International Pvt. Ltd. | following wiser components has been installed: gateway: 1 qty dimmer controller : 3 qty fan speed controller : 2 qty ir controller : 1 qty | Commissioning & Installation | Start-up | 8- Service Completed | 2023-09-29 11:28 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11314555 | 104299231 | 2023-09-29 16:36 | 2023-09-27 |  | 2023-09-27 10:03 | IN8401_16_SP | IN8401_16_SP | IN8401_16_SP |  | DOP: 14/6/2022 Zencelo Switches Qty: 20 P: Not Working Kindly check invoice at site | 2023-09-27 | 2023-09-29 16:40 | No | Warranty | Poonam Goyal | House No.-254, HUDA Sector-5, | Karnal | 132001 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Rakesh Kumar Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the switch found not giving output. Hence faulty replaced. IN8401 - 2 Nos. email : id not provided by the customer. | Repair |  | 8- Service Completed | 2023-09-30 10:36 |  |  | 1 | INR | 1 | ENM HOME DISTRIBUTION
WO-10973087 | 102349715 | 2023-07-10 12:21 | 2023-09-08 |  | 2023-07-08 23:28 | SURT15KUXIG-INX | SURT15KUXIG-INX | SURT15KUXIG-INX | B22112000204 | Approved by Nitin DOP: In Warranty P: PM S: PM Note: Mail from Ramendra | 2023-07-08 | 2023-09-08 14:45 | No | Commercial Action - Service Ops | Airforce Station | Maude Lines, Delhi Cantonment Palam | Delhi | 110010 | Delhi | India FS North1 HBN CSP Martech Systems & Services New Delhi | Balwant Singh_Martech Systems & Services New Delhi | Martech Systems & Services-Gurgaon | PM DONE | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-08 14:46 |  |  | 0 | INR | 0 | ENM SECURE POWER
WO-11314556 | 104281538 | 2023-09-28 15:36 | 2023-09-27 |  | 2023-09-27 10:04 | A9KF71106 | A9KF71106 | A9KF71106 |  | DOP: 20/9/2023 A9KF71106 Qty:1 P: Tripping issue Expert Engineers G1-287 RIICO Industrial Area Khushkhera Bhiwadi Dist:-Alwar Rajasthan-301707 Vishal Goyal (9289867765) | 2023-09-27 | 2023-09-28 15:39 | No | Warranty | Expert Engineers | G1-287 RIICO Industrial Area Khushkhera Bhiwadi null | Alwar | 301707 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mcb found terminal screw free, Hence faulty replaced. A9N4P32C - 1 nos Email : quality@expertengineers.co.in | Repair |  | 8- Service Completed | 2023-09-28 17:18 |  |  | 80 | INR | 80 | ENM HOME DISTRIBUTION
WO-10973088 | 102349726 | 2023-07-10 12:16 | 2023-09-08 |  | 2023-07-08 23:28 | SURT15KUXIG-INX | SURT15KUXIG-INX | SURT15KUXIG-INX | B22112000234 | Approved by Nitin DOP: In Warranty P: PM S: PM Note: Mail from Ramendra | 2023-07-08 | 2023-09-08 14:40 | No | Commercial Action - Service Ops | Airforce Station | Maude Lines, Delhi Cantonment Palam | Delhi | 110010 | Delhi | India FS North1 HBN CSP Martech Systems & Services New Delhi | Balwant Singh_Martech Systems & Services New Delhi | Martech Systems & Services-Gurgaon | PM DONE | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-08 14:41 |  |  | 0 | INR | 0 | ENM SECURE POWER
WO-11316473 | 104302470 | 2023-09-27 16:50 | 2023-09-27 |  | 2023-09-27 12:54 | IN8401_16_SP | IN8401_16_SP | IN8401_16_SP |  | DOP: 7/8/2023 IN8401BZ Qty:4 P: Not Working SANGEETHA MOHAN, NOEL ECODEN, FLAT NO.1E, VALLATHOL PADI, JUDGEMUKKU, THRIKKAKARA, EDAPPALLY. Ernakulam Ph: 8089361221 | 2023-09-27 | 2023-09-29 11:44 | No | Warranty | Sangeetha Mohan |  | Ernakulam | 682021 | Kerala | India FS South2 ED&I CSP PrinterPeople Cochin | Renjith PR PrinterPeople Cochin | PRINTER PEOPLE-COCHIN | IN8401BZ - 2 nos replaced.. 2022 batch 1 nos switch refixed and found ok,, | Repair |  | 8- Service Completed | 2023-09-30 11:45 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-10973089 | 102349795 | 2023-09-07 17:18 | 2023-07-08 |  | 2023-07-08 23:28 | SRC3KUXI | SRC3KUXI | SRC3KUXI | B22246015129 | DOP : 7-7-2023 P : Smart UPS- Installation S : Installation | 2023-07-08 | 2023-09-07 17:20 | No | Commercial Action - Sales | FINCARE SMALL FINANCE BANK LIMITED | 835/39, 5th Floor, Bren Mercury,Kaikondanahalli, Sarjapur Main Road null | Bengaluru | 560035 | Karnataka | India FS South1 HBN CSP Central Data SystemsPvt.Ltd. Bangalore | Nagaraj Central Data SystemsPvt.Ltd. Bangalore | Central Data Systems Pvt Ltd-BLR004 | Installation has been done. UPS is working fine.. | Commissioning & Installation | Start-up | 10- Closed | 2023-09-07 17:21 |  |  | 20 | INR | 20 | ENM SECURE POWER
WO-11316801 | 104303540 | 2023-09-27 16:42 | 2023-09-27 |  | 2023-09-27 15:07 | IH14000100 | IH14000100 | IH14000100 |  | DOP: 31/3/2023 IH14000100 Qty:1 P: Not Working Jibin Ashraf 12/1478A Mehrab Chullickal Kochi 682005 Ph: 9895317021 | 2023-09-27 | 2023-09-28 09:41 | No | Warranty | Jibin Ashraf |  | Ernakulam | 682005 | Kerala | India FS South2 ED&I CSP PrinterPeople Cochin | Vysakht PrinterPeople Cochin | PRINTER PEOPLE-COCHIN | site visit done found input not there in 2 nos relay found tripped mcb product working fine checked tested ok | Repair |  | 8- Service Completed | 2023-09-28 13:42 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11320114 | 104314549 | 2023-09-28 17:16 | 2023-09-28 |  | 2023-09-28 09:38 | IH14000100 | IH14000100 | IH14000100 |  | RE: Wiser Installation For RS Illuminations [ thread::kd07TY-iciG1OayugtYJrz4:: ] | 2023-09-28 | 2023-09-30 13:32 | No | Warranty | Rajesh Rajesh | no.753, Hal Subbanna complex, d/847/1442/9, BB Rd, Yelahanka | Bangalore | 560064 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Mohammad Riyaz_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported wiser 4 channel relay -2nos and 2 channel dimmer relay- 1 nos, found 4 channel relay load 1 continuously ON. 2 ch dimmer found inactive.we resetted the 2ch dimmer relay and checked found working ok. As per ms.Neel Schneider, we handed over the defective 4channel relay -2 nos to the customer. | Repair |  | 8- Service Completed | 2023-09-30 17:06 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11320119 | 104312240 | 2023-09-29 14:51 | 2023-09-28 | Smart Doorbell not working | 2023-09-28 09:39 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Dear Team, Please arrange a technician for Service of Following Components at below Location: Product to be Serviced: Wiser Smart Doorbell ( IH100WFVDP ) ?> Quantity = 2. Project Name: V-Uptown by Tatvam Constructions Location: Ravet Kiwale Link Road, Kiwale Pune Near Jai Ganesh Lawns, Pimpri Chinchwad 412101. Contact: Mr. Hrushi Jadhav ? 7387852885. Note: Please check Invoice & Break Fix check list attached with this mail. | 2023-09-28 | 2023-09-29 16:17 | No | Warranty | Hrushi Jadhav | Ravet Kiwale Link Road, Kiwale Pune Near Jai Ganesh Lawns, Pimpri | Chinchwad |  | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Kunal jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the Smart Doorbell not working. as per customer this Smart Doorbell not working. we given supply to VDP and taken operation it's working found ok. We observed no problem found in VDP. VDP found ok. | Repair |  | 8- Service Completed | 2023-09-29 16:49 |  |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11167157 | 103569982 | 2023-08-26 12:01 | 2023-09-11 |  | 2023-08-26 11:34 | LV525442 | LV525442 | LV525442 | 10-2023-W07-7-3165L1 | FW: MCCB Phase Failure - Reg Case ID 103146864/ WO-11092606 From: Goutam Dutta <Goutam3.Dutta@se.com> Sent: 25-08-2023 12:28 PM To: AKSHATHA RANI <AKSHATHA.RANI@se.com>; SANJAY DHARMU <Sanjay.Dharmu@se.com> Subject: Re: MCCB Phase Failure - Reg Case ID 103146864/ WO-11092606 Hi Akshatha, Now there is no issue at customer site. But customer wants RCA. Kindly generate a WO under Assessment-Inspection Category. Also inform customer to share Panel Drawing, for which we are following up with them, still not received. Panel Drawing is must for analysis. | 2023-08-26 | 2023-09-11 14:27 | No | Warranty | Buhler India Pvt ltd | Bharat Oorja Distilleries Private Limited Industrial Park Part A | Muzaffarpur | 843111 | Bihar | India FS ED&I CSP East Team Vidya Enterprises Lucknow | Rana Ranjan_Vidya Enterprises Lucknow | Vidya Enterprises | RCA rejected, as there type-2 coordination not followed. | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-11 14:33 |  |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11320732 | 104329833 | 2023-09-28 14:12 | 2023-09-28 |  | 2023-09-28 10:45 | X1001WH_M3M_N | X1001WH_M3M_N | X1001WH_M3M_N |  | DOP: 11/4/2023 Opale Switches Qty: 2 P: Not Working Kindly check invocie at site | 2023-09-28 | 2023-09-29 14:53 | No | Warranty | Satendra Aggarwal | Flat No C-904, Amarpali Sapphire Apartment, Sec-45 , | Noida | 201301 | Uttar Pradesh | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the switches and found switches have breaking issue, As per serial number switches not cover under warranty, We replace the faulty switches only this time. We suggest to customer please contact to dealer next time. Mail Id. sat_agl@yahoo.com | Repair |  | 8- Service Completed | 2023-09-29 16:01 |  |  | 22 | INR | 22 | ENM HOME DISTRIBUTION
WO-11322241 | 104335656 | 2023-09-28 15:40 | 2023-09-28 |  | 2023-09-28 14:16 | IN84SFR_N | IN84SFR_N | IN84SFR_N |  | Zencelo fan regulator white color not working 4 no Purchased - Virat Intex In . Oct 2022 | 2023-09-28 | 2023-09-30 14:16 | No | Warranty | Naveen Kumar | no 3 , arihant apartmnet , opp bb bakery ., VV puram | Bangalore | 560004 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Santhosh DP_P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | Inspected and found below mentioned 1)Ref: IN84SFR_N S/N:16350L = 4 No's All switches are out of warranty. Hence we rejected the warranty replacement. | Repair |  | 8- Service Completed | 2023-09-30 14:17 |  |  | 9 | INR | 9 | ENM HOME DISTRIBUTION
WO-11326996 | 104358803 | 2023-09-30 13:44 | 2023-09-29 |  | 2023-09-29 11:10 | A9N2P16C | A9N2P16C | A9N2P16C |  | Supreme electrcial Purchases yetserday 16 amps 2 pole no continuity | 2023-09-29 | 2023-09-30 13:47 | No | Warranty | Preeti Sharma | 37 milestone , sector 33 , near rose land school hero honda chowk | Gurgaon | 122001 |  | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | checked the mcb found working ok. Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-30 13:52 |  |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11327008 | 104348480 | 2023-09-29 14:56 | 2023-09-29 | Switch not working | 2023-09-29 11:17 | X1001WH_N | X1001WH_N | X1001WH_N |  | 1. Name of Customer: Manish Saxena 2. Site Address: - Greens society, opp padumjee paper mill, thergaon, pune 3. Name of contact person at site :- Manish Saxena 4. Contact Phone / Mob. No: - 9824314282 5. Defective product details:-x1001wh 6. Product Make:- opale 7. Nature of Defect: switch not working 8. Shutdown availability if applicable :nil 9. Serial No: or DOM of - Not known 10. Dealer Name /OA no. /Invoice Details: - 10 years warranty 11. Commissioned / Installed date:- NIL 12. Name & phone No: of person registering the complaint: Manish Saxena / 9824314282 | 2023-09-29 | 2023-09-30 12:54 | No | Warranty | Manish Saxena | reens society, opp padumjee paper mill, thergaon | Pune | 411033 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Kunal jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the switch found that the Switch is not working it's found broken from inside the board . so this problem is not repairable.So switch Needs to be replaced, Required Material : X1001WH - 04 nos. we arranged the material from our stock and replaced it. | Repair |  | 8- Service Completed | 2023-09-30 17:18 | =S= Consig Fill up 226103981 |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11327052 | 104356087 | 2023-09-29 22:54 | 2023-09-29 |  | 2023-09-29 11:36 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Dear Team, My VDP is required Re Installation only. The team member call me he that your site is ready for installation I replied Yes. It's old installation done at site. Their is some re installation of VDP only. Please send some person for re installation of VDP at the earliest. customer name: ankur singh dinkar customer mobile: number 8840570925 address: A1202 paramount emotions sector 1 near yatharth hospital gr noida west 201306 | 2023-09-29 | 2023-09-29 23:10 | No | Commercial Action - Sales | Ankur Singh Dinkar | A1202 Paramount Emotions Sector 1 | Noida | 201306 | Uttar Pradesh | India FS ED&I CSP North Team Seamtek International Pvt. Ltd. GHAZIABAD | Satish Raika Seamtek International Pvt. Ltd. GHAZIABAD | Seamtek International Pvt. Ltd. | FOLLOWING WISER COMPONENTS HAS BEEN REPAIRE SMART DOORBELL: 1 QTY | Commissioning & Installation | Start-up | 8- Service Completed | 2023-09-30 11:11 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11327126 | 104360437 | 2023-09-29 13:04 | 2023-09-29 |  | 2023-09-29 12:19 | A9KF71106 | A9KF71106 | A9KF71106 |  | United Paint & Chemical Industries Plot No.B -20 Chak 7 E chhoti Suratgarh Hanumangarh by Pass,Opp. Chitlangia Dharam Kanta, Sri Ganganagar,Rajasthan 335001 Mr.Mahesh Sharma 9024827313 | 2023-09-29 | 2023-09-29 13:06 | No | Warranty | United Paint & Chemical Industries | Plot No.B -20 Chak 7 E chhoti Suratgarh Hanumangharh by Pass Opp. Chitlangia Dharmkanta, | Sri Ganganagar | 335001 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | Checked the mcb and rccb found phase missing and mccb found not getting on due to phase missing , Hence faulty replaced. A9N1P06C - 2 nos EZ9R55263 - 1 nos LV525312 - 1 nos Email : | Repair |  | 8- Service Completed | 2023-09-29 17:23 |  |  | 470 | INR | 470 | ENM HOME DISTRIBUTION
WO-11175168 | 103570541 | 2023-09-22 15:34 | 2023-08-28 |  | 2023-08-28 20:06 | MTN627819 | MTN627819 | MTN627819 |  | RMA 103570541_RO 61360710 | 2023-08-28 | 2023-09-23 11:43 | No | Warranty | Rexel India Private Limited | Plot No. C-71, Ground and First Floor, Vibhuti Khand, Gomti Nagar | Lucknow | 226010 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Aman Khare_Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found MCB having dolly free & rotary handle free, so we replaced. | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-23 12:01 |  |  | 15 | INR | 15 | ENM POWER PRODUCTS
WO-11178208 | 103618455 | 2023-08-30 10:51 | 2023-08-29 |  | 2023-08-29 11:08 | LC1D115 | LC1D115 | LC1D115 | PK22373 | Fwd: Case : 103528665 dt. 25.8.23 Dear Sir, Mujras toll plaza 25 km from bhilwara towards Rajsamand Bhilwara Mr.Suresh 9712892760 Product : LC1D115 Serial Number : PK22373 not working -- *WITH REGARDS-* Sarabjit Singh SHARMA ELECTRIC WORKS I CHANDIGARH | 2023-08-29 | 2023-09-04 11:21 | No | Warranty | Mujras toll plaza | 25 km from bhilwara towards Rajasamand | Bhilwara | 311001 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | Checked the contactor found contact weld issue and add on block found no/nc point issue, Hence faulty replaced. LC1D1150046M7 - 1 nos LAEN11 - 1 nos | Repair |  | 9- Service Validated | 2023-09-04 11:23 |  |  | 250 | INR | 250 | ENM POWER PRODUCTS
WO-11192543 |  | 2023-09-05 23:58 | 2023-09-16 |  | 2023-09-01 11:43 | Leonardo EV,DX,R407c,EC Fan,TUAV1822A,Upflow With Heater & Humidifier | TUAV1822AN002 | TUAV1822AN002 | ZK1523001683 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-01 | 2023-09-04 20:30 | No | Contract | HCL Technologies | 501-503 IV th Floor Oxford House No: 15 Rustam Bagh Main Road 2-4th Flr,HUB-1,Survey No.61/1,61/2,94/1 Kempapura Main Road, Nagavara | Bangalore | 560017 | Karnataka | India FS South3 Cooling CSP ERIC HVAC SYSTEM Bengaluru | Freddy Dass ERIC HVAC SYSTEM Bengaluru | ERIC HVAC SYSTEM | Preventive maintenance done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-06 00:02 |  |  | 30 | INR | 30 | ENM SECURE POWER
WO-11179002 | 103624175 | 2023-08-31 17:36 | 2023-08-29 |  | 2023-08-29 16:13 | CAE22M5 | CAE22M5 | CAE22M5 |  | Warning: Email body is too large and was truncated at 32 000 characters. Information may have been lost. faulty contactor image. That is a manufacture fault so we request you please provide us the replacement as soon as possible. 01) Received Faulty contactor part no- ( CAE22 M5) 2 nos 02) Received Faulty mcb part no- (A9N3P06C) 1 nos Sokindra kumar --7428316306 | 2023-08-29 | 2023-09-04 16:18 | No | Warranty | Accord Automation (P) Ltd | Plot No-798, Sec-69, IMT | Faridabad | 121001 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | checked the mcb and contactor and mpcb found phase missing. hence faulty,replaced, A9N3P06C - 1 Nos. LC1D09M7 - 1 Nos. GV2ME08 - 1 Nos. Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-05 16:23 |  |  | 45 | INR | 45 | ENM POWER PRODUCTS
WO-11179054 | 103628747 | 2023-08-31 15:52 | 2023-08-29 |  | 2023-08-29 16:38 | LV431541 | LV431541 | LV431541 |  | COMPLAINT NO. FOR LV431541 motor mechanism, MT 250 __ S.No-TC- 2022-W30-1 _07/2022 :: problem :: Tripping position Not Set/ Not Tripped Auto Mode. NAME OF CUSTOMER M/S CORONET ENGINEERS PVT. LTD 2 SITE ADDRESS KHASRA NO. 24/24/3, 27 SOUTH ZONE NATHUPUR INDUSTRIAL AREA, VILLAGE - NATHUPUR, DISTT - SONEPAT ? 131029 3 NAME OF CONTACT PERSON AT SITE MR. Mohan Sharma (iqc@coronet.in) 4 CONTACT PHONE / MOB. NO: 9910050281; 9760989655 5 DEFECTIVE PRODUCT DETAILS LV431541 motor mechanism, MT 250 6 NATURE OF DEFECT Display Problem Issue 7 SHUTDOWN AVAILABILITY IF APPLICABLE YES 8 WARRANTY STATUS YES 9 COMMISSIONED / INSTALLED DATE TC- 2022-W30-1 _07/2022 10 SERIAL NO: OR DOM OF THE PRODUCT TC- 2022-W30-1 _07/2022 Tripping position Not Set/ Not Tripped Auto Mode. | 2023-08-29 | 2023-09-06 14:30 | No | Warranty | CORONET | Khasra no. 24/24/3, 27 South Zone Nathupur Industrial Area, Village - Nathupur, null | Sonepat | 131029 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | checked the MT found not getting ON in Auto Mode.Hence faulty, replaced. LV431541 - 1 Nos. Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-06 14:36 |  |  | 65 | INR | 65 | ENM POWER PRODUCTS
WO-11180670 | 103556149 | 2023-09-08 12:07 | 2023-08-29 |  | 2023-08-29 21:51 |  |  |  |  | RMA 103556149_RO 61366843 | 2023-08-29 | 2023-09-08 12:09 | No | Warranty | Vidhyut Control India Pvt. Ltd. | D-12, Sector-17, Kavi Nagar Industrial Area, | Ghaziabad | 201002 | Uttar Pradesh | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | checked the meter found display not showing. Hence faulty, replaced . | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-12 11:55 |  |  | 52 | INR | 52 | ENM POWER PRODUCTS
WO-11181319 | 103636943 | 2023-08-30 16:18 | 2023-08-30 |  | 2023-08-30 09:58 | EZAUVR200AC | EZAUVR200AC | EZAUVR200AC |  | Dear Team Please arrange to depute service engineer to attend the below complaint . INVOICE COPY IS ATTACHED item ref = EZAUVR200AC PROBLEM = NOT WORKING ADDRESS VASUDEV POWER SOLUTION A-52 PRATAP NAGAR VISTAR MEENO KI DHANI OPPOSITE BANS FACTORY POST OFFICE NINDAR JAIPUR PIN = 302039 CONTACT PERSON RAJVEER JANGID CONTACT NO. 9928557449 , 9636825459 -- Rajesh Jain *R.K. Sales Agencies**30, Navjeevan Complex**Station Road, Jaipur - 302001 (Raj)**Tel. 0141-5103932,3919082,2372382**Cell. +91-9829220820,9413088854**Email id - rksalesagencies@gmail.com <rksalesagencies@gmail.com>**===========================================================================================**AUTHORISED DISTRIBUTER -* ** All type Motors & Pumps of Cromption Greaves Ltd. *** Poly Propylene Rope of Tufropes Pvt. Ltd. *** All Type Swichgears & Industrial Automation Product of Schneider Electric*** R R KABEL R R Make House Wire & Ind. Cable.*** HPL Switchgear & Wire cable.* ** Bonton Cables *** Siemens Ltd*** Socomec * | 2023-08-30 | 2023-09-02 18:06 | No | Warranty | Vasudev Power Solution | A 52 Pratap Nagar Ext , Near VKI 5 No. Sikar Road null | Jaipur | 302039 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | Checked the coil found not working , Hence faulty replaced. EZAUVR200AC - 1 nos Email : rksalesagencies@gmail.com | Repair |  | 9- Service Validated | 2023-09-04 15:09 |  |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11182997 | 103650954 | 2023-09-15 10:04 | 2023-08-30 |  | 2023-08-30 11:13 | LV438279 | LV438279 | LV438279 |  | FSB _ WO _ For Orchid activity Kindly create 2 nos FSB WO for minitop hammer replacement PRB-233066 , Please refer attachment for Customer address. 12 nos for each day. Product : NSX630S DC, LV438279,TC20417. Contact Name : Pradeep, 07619122865. Regards, P.BALAKUMAR, Field Service Team, Schneider Electric , PH: 7428380635, Bangalore. | 2023-08-30 | 2023-09-22 10:39 | No | Pending Contract | Juniper Networks India Pvt Ltd | Prestige Tech Park Elnath-Exora Business Park Survey No.111/1 to 115/4 Wing A & B Amane Bellandur Khane Village Marathahalli | Bangalore | 560103 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | C Gunasekaran_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | As per SE and customer request, we had visited the site and checked the customer installed MCCB.Found impacted date code .so we had replaced Hammer and checekd ON/OFF/TRIP working ok. | Field Service Bulletin | High - Immediate Action | 9- Service Validated | 2023-09-22 10:39 |  |  | 13 | INR | 13 | ENM POWER PRODUCTS
WO-11187637 | 103631826 | 2023-08-31 11:33 | 2023-08-31 |  | 2023-08-31 11:29 |  |  |  |  | RMA 103631826_RO 61364654 | 2023-08-31 | 2023-09-02 12:00 | No | Warranty | Crystal Controls | 601, Elanza Vertex, B/h Armieda House, Sindhu Bhavan Road, Bodakdev, | Ahmedabad | 380054 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Mohammad Aasif Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physicaly observed ok. METSEEM1220HCL1 SRNO : 060822 obseved ok. we give control power supply and observed. display not getting on. we measure control power supply observed 230vac voltage ok. so give free replacement for customer satisfaction. =S= Free Order 226022186 has been saved | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-02 13:42 | =S= Free Order 226022186 has been saved |  | 23 | INR | 23 | ENM POWER PRODUCTS
WO-11193312 |  | 2023-09-30 12:12 | 2023-09-23 |  | 2023-09-01 11:59 | Leonardo EV,DX,R410A, TDAV0721A (3/8" EVAP) downflow (DBL SKIN) with heater and | TDAV0721AN021 | TDAV0721AN021 | ZK1441009960 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-01 | 2023-09-30 12:14 | No | Contract | Pangea3 Legal Database Systems Pvt Ltd | Unit 102B, Leela Business Park Ground Flr Andheri-Kurla Rd , Andheri East | Mumbai | 400059 | Maharashtra | India FS West1 Cooling CSP Unique India Mumbai | Sanket More_Unique India Mumbai | Unique India- Mumbai HBN CSP | PM DONE | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-30 12:23 |  |  | 1 | INR | 1 | ENM SECURE POWER
WO-11188267 | 103695273 | 2023-09-01 15:51 | 2023-08-31 |  | 2023-08-31 16:29 | LC1D80AM7 | LC1D80AM7 | LC1D80AM7 |  | Model Number: LC1D80AM Contactor, MCCB( LV525303) 10-2022W37_6_5236L3 Contactor Not Working, And MCCB getting heat up 8b23053 Contact Person and number: Vinod Gupta 9896664816 Akshya spinning Mills panipat 132103 | 2023-08-31 | 2023-09-01 16:58 | No | Warranty | Akshay Spinning Mills_Panipat | Gohana Road-- Panipat- | Panipat | 132103 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the contactor and MCB found phase missing. Hence faulty , replaced. LC1D80AM7 - 2 Nos. LC1D65AM7- 1 Nos. A9N3P63C - 1 Nos. LC1D32BD - 1 Nos. email : vinodgupta1842@gmail.com | Repair |  | 9- Service Validated | 2023-09-01 17:01 | 226018963 LC1D32BD ALSO booked. |  | 165 | INR | 165 | ENM POWER PRODUCTS
WO-11188469 | 103695041 | 2023-09-01 11:46 | 2023-08-31 |  | 2023-08-31 17:43 | LC1DMK11M7 | LC1DMK11M7 | LC1DMK11M7 |  | Dear Sir, As per feedback from the site contactor not working , pictures enclosed , consi to dering the urgency of maintaining power factor we have replace this customer you are requested to depute your engineer at our works LC1DMK11M7 Site Address Hartek india private limited Plot no D 180 Industrial area phase 8 B Mohali Contact details as under signed Best Regards Harinder Singh ¦ Lead ? Quality Control Power Distribution Products Business HARTEK INDIA PRIVATE LIMITED T: 0172 4004121-26 M: 7740002914 W: www.hartek.com Hartek Towers ? F 321, Industrial Area, Phase 8-B, Mohali ? 160055 ????????????????????????????????????????????????????????.. Disclaimer- This transmission is confidential and intended solely for the person or organization to whom it is addressed. It may contain privileged and confidential information. If you are not the intended recipient, you should not copy, distribute or take any action in reliance on it. If you have received this transmission in error, please notify us immediately by e-mail at info@hartek.com | 2023-08-31 | 2023-09-01 13:43 | No | Warranty | Hartek India Private Limited | F 321, Phase 8B, Industrial Area, null | Mohali | 160055 | Punjab | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Vinod Kumar_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the contactor found resistance wire burnt. Hence faulty replaced. LC1DMKM7- 1 Nos. email : quality.hipl@hartek.com | Repair |  | 9- Service Validated | 2023-09-01 14:44 |  |  | 25 | INR | 25 | ENM POWER PRODUCTS
WO-11188467 | 103693184 | 2023-09-26 11:22 | 2023-09-26 |  | 2023-08-31 17:42 |  |  |  |  | RMA 103693184_RO 61366060 | 2023-08-31 | 2023-09-28 15:00 | No | Warranty | Ebasco Marketing - 500017223 | No :4/6,Budhhar Colony Main Road, Karambakkam,Porur - 600116. | chennai | 600116 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | ZVO 226085801 | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-28 16:05 |  |  | 15 | INR | 15 | ENM POWER PRODUCTS
WO-11188488 | 103686141 | 2023-09-01 11:25 | 2023-08-31 |  | 2023-08-31 17:47 | SQD-LADT2 | SQD-LADT2 | SQD-LADT2 |  | Complaint Form_S. B Syscon Pvt Ltd Company Name & Complete Address with pin code - Where product -------S. B Syscon Pvt Ltd, 1D-45A N.I T, Faridabad, Haryana -121001 · Contact Person at office : Name & Mobile No. : Mini Krishnan # 7506943307 Part.No:-LADT2-1Qty OA.No-300818142 Invoice.No-9008623084/03.07.2023 | 2023-08-31 | 2023-09-20 16:30 | No | Warranty | S.B Syscon Pvt. Ltd. | 1D-45A, N.I.T, | Faridabad | 121001 | Haryana | India FS ED&I CSP North Team S D Electric Delhi | Arif Raza S D Electric Delhi | S D Electric (500017662) | Timer Replaced and defective product in our custody. | Repair |  | 8- Service Completed | 2023-09-21 17:26 |  |  | 52 | INR | 52 | ENM POWER PRODUCTS
WO-11192238 | 103718133 | 2023-09-02 12:42 | 2023-09-01 |  | 2023-09-01 11:13 | LC1D115 | LC1D115 | LC1D115 |  | LC1D115 220 Sr PK22425 Contactor 31 March 2023 Invice Number SKT-1538/22-23 Issue : Kitt damage IRIDIUM Chemicals PVT LTD imtyaj1989@outlook.com Gangapar Tribhun Khedha , Thana:Ganga Ghat, Unnao NH 27 Kanpur Lko Uttarpardess UP 209862 Imtyaj Khan 8932879177 | 2023-09-01 | 2023-09-08 16:52 | No | Warranty | IRIDIUM Chemicals PVT LTD | Gangapar Tribhun Khedha , Thana:Ganga Ghat, Unnao NH 27 Kanpur Lko Road null | Unnao | 209862 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Aman Khare_Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found Contactor having pole open issue so we replaced. | Repair |  | 9- Service Validated | 2023-09-08 16:54 |  |  | 115 | INR | 115 | ENM POWER PRODUCTS
WO-11193369 | 103718302 | 2023-09-04 13:10 | 2023-09-01 |  | 2023-09-01 12:02 | SQD-LADT2 | SQD-LADT2 | SQD-LADT2 |  | Complaint Form_RSK Electricals Company name - RSK Electricals Address - PLOT NO-114,PHASE-IV,SECTOR-57,HSIIDC, INDL.ESTATE,KUNDLI,SONIPAT HARYANA-131028 HARYANA INDIA Contact person -Harjeet Singh Contact No. 9350906347 Product - LADT2 Status -- Faulty(Not Working) Qty - 1 Sales order number: 300818142-----28-06-2023 | 2023-09-01 | 2023-09-04 13:12 | No | Warranty | RSK Electricals | plot no 114, Phase 4, Sec 57, Kundli, | Sonepat | 131028 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the Timer found working ok. Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-04 15:48 |  |  | 65 | INR | 65 | ENM POWER PRODUCTS
WO-11199089 | 103740851 | 2023-09-02 11:21 | 2023-09-02 |  | 2023-09-02 10:27 | LV563306 | LV563306 | LV563306 | TC 2022-W44-3-U2 | complaint no. Required a/c JRL Dear CCC Please issue complaint No. JRL Laminates P LTD Jakhal Road Near Ajit Nursing institute Sunam, Punjab Mr Jaspal Singh 9501611157 Product L LV563306 MCCB Sr No. TC 2022-W44-3-U2 DOM Nov 2022 Not getting ON with UV Coil | 2023-09-02 | 2023-09-02 11:23 | No | Warranty | JRL Laminates P LTD | Jakhal Road Near Ajit Nursing institute Sunam | Sangrur | 148028 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the MCCB found not getting on due to plunger broken. Hence case is closed. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-02 11:40 |  |  | 120 | INR | 120 | ENM POWER PRODUCTS
WO-11193440 |  | 2023-09-05 23:50 | 2023-09-16 |  | 2023-09-01 12:10 | Leonardo EV,DX,R407c,EC Fan,TUAV2522A,Upflow With Heater & Humidifier | TUAV2522AN001 | TUAV2522AN001 | ZK1523003185 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-01 | 2023-09-04 21:10 | No | Contract | HCL Technologies | 501-503 IV th Floor Oxford House No: 15 Rustam Bagh Main Road 2-4th Flr,HUB-1,Survey No.61/1,61/2,94/1 Kempapura Main Road, Nagavara | Bangalore | 560017 | Karnataka | India FS South3 Cooling CSP ERIC HVAC SYSTEM Bengaluru | Freddy Dass ERIC HVAC SYSTEM Bengaluru | ERIC HVAC SYSTEM | Preventive maintenance done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-05 23:55 |  |  | 30 | INR | 30 | ENM SECURE POWER
WO-11199612 | 103727778 | 2023-09-05 15:09 | 2023-09-02 |  | 2023-09-02 10:55 | LC1E160M5 | LC1E160M5 | LC1E160M5 | 8C22293500011 | RE: Failure of contactor Mee. Schnieder LCIDE/Complent regestration [ thread::1Nza2y-fee2MyhvjM5vW4z4:: ] LC1e160m5 Sr: 8C22293500011 Fault:- Burnt out Y.P.Singh Parihar Contact No. At Delhi office ? 9818110896 / 011 49025329 Contact No. at Plant Site- 7880082521 | 2023-09-02 | 2023-09-05 15:11 | No | Warranty | SKS Ispat power ltd | F 84, 3rd floor Shiroji Place, Rajouri Gargen, Janta Market | Delhi | 110027 | Delhi | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the contactor found phase terminal burnt due abnormal voltage, Hence no replacement given to customer. Email : id not provided by customer . | Repair |  | 9- Service Validated | 2023-09-05 16:14 |  |  | 20 | INR | 20 | ENM POWER PRODUCTS
WO-11200509 | 103590720 | 2023-09-02 19:53 | 2023-09-02 | NA | 2023-09-02 11:33 | METSEPM8240 | METSEPM8240 | METSEPM8240 | 2201C249-02 | PowerLogic meter - PM8000 not working L1 Technical comment: Tried remote troubleshooting with customer but customer wants visit only. Please take care. METSEPM8240---programming Issue On more PM8000 meter communication Issue with PME ME-2201C249-02 EM6400NG Meter display Issue But End customer Mr.Parameshwaran C 9100950226 is asking for Site visit only Due to RS485 communication failure in the Power logic meter our EMS system is not working . We are facing issues on online Load monitoring and energy calculation issues. Kindly arrange your service engineer to sort out the issues immediately. PowerLogic meter Details - Model:- METSEPM8240 Sl No. ME-2201C249-02 PM8000 Thanks and Regards, Parameshwaran C Electrical - Manager Vasind Works, Village - Vasind, Tal. - Shahapur, Dist. - Thane ? 421601 ¦ Maharashtra ¦ India T: 02527 667400-26 Ext.: 423; M +91 910095022 | 2023-09-02 | 2023-09-04 16:00 | No | Warranty | JSW Steel Limited | Village Vasind ,Taluka - Shahapur | Thane | 421604 | Maharashtra | India FS ED&I CSP West Team East India Power Engineers Mumbai | Sandeep Ingavale East India Power engineers Mumbai | East India Power Engineers (5043) | Visited the site & following work done. As per customer feedback they not possible to feed the proper password for the meter to set the parameters. As required password feed vin the meter & handover meter to the customer for parameters setting. | Repair |  | 8- Service Completed | 2023-09-04 16:12 | VIP FSR= No 3. FSR Request: Unavailability of the preferred FSR, need to depute Non VIP FSR(nitin dhadve). |  | 53 | INR | 53 | ENM POWER PRODUCTS
WO-11200544 | 103576735 | 2023-09-06 10:05 | 2023-09-02 |  | 2023-09-02 11:53 | NA00634V | NA00634V | NA00634V |  | Re: Problems found in 100A 4P ATS_Protech Group Guwahati [ thread::CVwI81S8ca2RLORDDGQFWT4:: ] Ganpati Electricals 136, Fancy Bazar, Jail Road, Guwahati - 781001 Vinay Kasera 9864017298 NA00634V Getting discontinued from main power at a particular time of everyday Attached | 2023-09-02 | 2023-09-10 00:30 | No | Warranty | Ganpati Electricals (Distributor) | 136, Jail Road, Fancy Bazar | Guwahati | 781001 | Assam | India FS ED&I CSP East Team SHIV ELECTRICALS Guwahati | Parwez Alam SHIV ELECTRICALS GUWAHATI | SHIV ELECTRICALS | Adjust the voltage of ATS and it's okay now. | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-10 19:29 |  |  | 12 | INR | 12 | ENM POWER PRODUCTS
WO-11200564 | 103662655 | 2023-09-02 16:55 | 2023-09-02 |  | 2023-09-02 12:19 | CAD32BL | CAD32BL | CAD32BL |  | Fwd: Failure of contactor CAD 32 L1 Tehcnical team comment : Requires visit, VIP customer CAD32 NONC contact issue Site Address : Tata Metaliks Limited Vill ? Maheshpur, P.O. Samraipur, PS ? Kharagpur (Local), Paschim Medinipur, Pin ? 721301, West Bengal Contact Number - Mobile: +91 8373059359 Quantity affected - 20 pcs CAD32 NONC contact issue as per attached invoice its under warranty Please take immediate action on it. Dear sir This is to inform you that we have procured Contactor CAD 32 F7,110 VAC against PO NO: 4200016445. DT: 03.03.2023?..30 nos from M/S Raju Enterprise and against PO no: 4200016190, dt:15.02.23 ?30 nos from M/S Solitaire Electrical. We have used all contactor in our EOT crane on Apri?23 during annual shut down. It was found that above mention contactor has been failure within 8 to 30 days. It was observed that sometime contactor was chattering with 110vac coil voltage or sometimes contactor got pickup but it?s ?NO? OR ?NC? contact state not changed. I have attached snap of contactor. Kindly take suitable action also request you for send your Engg for suitable root cause find out. Thanks and Regards Ratan Jana Manager (E&I DIP1) Olitaire Tata Metaliks Limited Vill ? Maheshpur, P.O. Samraipur, PS ? Kharagpur (Local), Paschim Medinipur, Pin ? 721301, West Bengal Mobile: +91 8373059359 Email: ratan.jana@tatametaliks.co.in | 2023-09-02 | 2023-09-07 14:32 | No | Warranty | Tata Metaliks Limited | P O Samraipur, Gokulpur Kharagpur, Dist: Paschim Mednipur, West Bengal | Kharagpur | 713512 | West Bengal | India FS ED&I CSP East Team SREYAM SERVICES BHATPARA | AMIT BHATTACHARYA_SREYAM SERVICES BHATPARA | Sreyam Services(8513) | Site visited, but defective samples not ready at site for RCA purpose. | Repair |  | 9- Service Validated | 2023-09-07 14:36 | VIP FSR= No 3. FSR Request: Unavailability of the preferred FSR, need to depute Non VIP FSR(goutam dutta). |  | 148 | INR | 148 | ENM POWER PRODUCTS
WO-11200652 | 103741638 | 2023-09-04 09:55 | 2023-09-02 |  | 2023-09-02 14:03 | SQD-LRD10 | SQD-LRD10 | SQD-LRD10 |  | Replacement Scneider relay are not work properly so pls replace deatails are.- Lrd10 1 pcs Hari om electrical Sher e punjab building, Link road, dholewal Ludhiana 141016 Mob-9878035345 | 2023-09-02 | 2023-09-04 13:01 | No | Warranty | Hari Om electrical | Sher-e Punjab building, Dholewal link road | Ludhiana | 141003 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the relay found thread issue, Hence faulty replaced. LRD10 - 1 nos Email : samartiwari48@gmail.com | Repair |  | 9- Service Validated | 2023-09-04 16:20 |  |  | 25 | INR | 25 | ENM POWER PRODUCTS
WO-11200737 | 103742219 | 2023-09-04 11:45 | 2023-09-04 |  | 2023-09-02 16:28 | LC1DWK12M7 | LC1DWK12M7 | LC1DWK12M7 |  | Dear sir, We would like to inform you that 02 Nos of contactors Cat No LC1DWK12M7 are not working properly and have issues of High heating, For your kind information we have purchased this from M/S Durga Bhai & Co. Delhi vide Invoice No 23101426 Dated 04.08.23 request please visit our site as soon as possible address and Cont Person details are given below M/S Superior Industries Ltd 6ThKM Rampur Road Clutterbuck Ganj Bareilly UP-243502 Divyanshu Sukla-7617845166. Thanks & Regards, Anand Singh Patwal 9811720942 Please Note : Our Email Id has been changed to sales@evaengs.com. Please use this Id for all Future Communications. Eva Engineering Service Z-54, Okhla Industrial Area, Phase-II, New Delhi - 110020 Ph. 011 - 26387695, 41616517 Email Id: sales@evaengs.com Website: www.evaengs.com "AN ISO 9001:2015 CERTIFIED COMPANY" P Please don't print this Email unless you really need to - this will preserve trees on planet earth. | 2023-09-02 | 2023-09-04 14:28 | No | Warranty | superior industries limited bareily | 6ThKM Rampur Road Clutterbuck Ganj Bareilly null | Bareilly | 243502 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Monu Pandey_Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Visit the site found defective material not available at actual site. costumer return the material to durga bhai ( delhi ) now complain is closed | Repair |  | 9- Service Validated | 2023-09-04 14:29 |  |  | 270 | INR | 270 | ENM POWER PRODUCTS
WO-11200792 | 103742911 | 2023-09-04 11:41 | 2023-09-02 |  | 2023-09-02 17:45 | GCR_MVS | GCR_MVS | GCR_MVS | 1023311 | RE: Require Service Support [ thread::3-Cm3CiCc6OKW_fetFqeCD4:: ] Hi Please find the required details M/s Actech Engineers Address:- Plot-3222/3421, Nadarganj Industrial Area Lucknow Product:- MVS10N4OW6L S.N.- 1023311 Problem:- rackin mechanism issue Contact Person:- Ravi Wahi Mob.:- 8840855318 Regards Lalit Kumar | 2023-09-02 | 2023-09-04 14:37 | No | Warranty | Actech Engineers | No.-3222/3421,Nadarganj,Amausi Industrial Area, | Lucknow | 226016 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Aman Khare_Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found ACB having rackin rackout issue so we resolved now complaint was closed | Repair |  | 9- Service Validated | 2023-09-04 14:41 |  |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11210505 | 103755083 | 2023-09-04 11:05 | 2023-09-04 | NA | 2023-09-04 10:56 | METSEEM6400NGRSCL1 | METSEEM6400NGRSCL1 | METSEEM6400NGRSCL1 |  | Fw: Item Damage Details for Damage. No: 5330 Please find trail mail Rejection from GOA plant. Po no.G07/SD/17996 SAP no: 0225235777 Invoice No.9008363213 Type No : METSEEM6400NGRSCL1 Qty : 01 NO Problem : Not working Kindly arrange replacement & Service engineer below mention address: Site Address- M/s. Marine Electricals I Pvt Ltd. PLOT NO. N-51,52,59 & 60, PHASE IV, VERNA INDUSTRIAL ESTATE, VERNA, SALCETE, GOA - 403722. Contact : Mr. Imtiyaz Khan- 09955215847 | 2023-09-04 | 2023-09-04 17:49 | No | Warranty | MARINE ELECTRICALS (I) LTD. GOA UNIT -II | PLOT NO. N-51,52,59 and 60, PHASE IV, VERNA INDUSTRIAL ESTATE VERNA, SALCETE | goa | 403722 | Goa | India FS ED&I CSP West Team East India Power Engineers Mumbai | Abhishek Parab_East India Power engineers Mumbai | East India Power Engineers (5043) | Visited the site and inspected the EM6400NG meter and found that the display not glowing after giving the 230V control supply The meter display was found faulty. | Repair |  | 8- Service Completed | 2023-09-05 14:34 | =S= Consig Fill up 226019126 |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11193610 |  | 2023-09-30 12:33 | 2023-09-23 |  | 2023-09-01 12:32 | Leonardo EV,DX,R410A, TDAV0721A (3/8" EVAP) downflow (DBL SKIN) with heater and | TDAV0721AN021 | TDAV0721AN021 | ZK1441009959 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-01 | 2023-09-30 12:37 | No | Contract | Pangea3 Legal Database Systems Pvt Ltd | Unit 102B, Leela Business Park Ground Flr Andheri-Kurla Rd , Andheri East | Mumbai | 400059 | Maharashtra | India FS West1 Cooling CSP Unique India Mumbai | Sanket More_Unique India Mumbai | Unique India- Mumbai HBN CSP | PM DONE | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-30 12:40 |  |  | 1 | INR | 1 | ENM SECURE POWER
WO-11210899 | 103757411 | 2023-09-04 16:20 | 2023-09-04 | MCCB Not fitting in DB | 2023-09-04 13:01 | LV516313 | LV516313 | LV516313 |  | Pl issue complaint no. Pl issue complaint no. 1. Name of Customer: City Corporation Ltd 2. Site Address: - Tower 45, Gold Tower Amanora park Town hadapsar pune 411028. 3. Name of contact person at site :- Mr. Dhanraj Sir 4. Contact Phone / Mob. No: -9607636361 5. Defective product details:- LV516313 6. Product Make:-Schneider Electric 7. Nature of Defect: MCCB Not fitting in DB 8. Shutdown availability if applicable :nil 9. Serial No: or DOM of - 10-2022-W15-2 10. Dealer Name /OA no. /Invoice Details: - NIL 11. Commissioned / Installed date:- NIL 12. Name & phone No: of person registering the complaint: Mr. Amit Patil - 8888192174 =======Thanks&Regards=============================================== For Super Electrical's Engineering Services | 2023-09-04 | 2023-09-05 11:55 | No | Warranty | City Corporation Ltd. | Tower 45, Gold Tower Amanora park Town hadapsar null | Pune | 411028 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Amit Patil_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the MCCB Not fitting in DB . we removed DB & fitted MCCb properly in DB then MCCB fixed properly in that DB. then we taken on/off operation it's found ok. Product found ok. | Repair |  | 9- Service Validated | 2023-09-05 11:58 |  |  | 20 | INR | 20 | ENM POWER PRODUCTS
WO-11193611 |  | 2023-09-30 12:27 | 2023-09-23 |  | 2023-09-01 12:32 | Leonardo EV,DX,R410A, TDAV0721A (3/8" EVAP) downflow (DBL SKIN) with heater and | TDAV0721AN021 | TDAV0721AN021 | ZK1441009958 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-01 | 2023-09-30 12:29 | No | Contract | Pangea3 Legal Database Systems Pvt Ltd | Unit 102B, Leela Business Park Ground Flr Andheri-Kurla Rd , Andheri East | Mumbai | 400059 | Maharashtra | India FS West1 Cooling CSP Unique India Mumbai | Sanket More_Unique India Mumbai | Unique India- Mumbai HBN CSP | PM DONE | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-30 12:32 |  |  | 1 | INR | 1 | ENM SECURE POWER
WO-11210956 | 103758395 | 2023-09-05 11:18 | 2023-09-04 |  | 2023-09-04 13:17 | EZC250N4125 | EZC250N4125 | EZC250N4125 |  | Re: MCCB NOT WORKING AT SITE [ thread::TwSz-PCdd2mFl1FzXSSouj4:: ] Complete model ref of the faulty product - EZC250N4125 125A MCCB NOT WORKING Inv dated:- 24.06.2022 ontact:- R KAPOOR-9910072144 ACME PLASTICS PLOT NO-673 , SECTOR-69 IMT FARIDABAD-121004 | 2023-09-04 | 2023-09-04 17:20 | No | Warranty | ACME PLASTICS | Plot No-4 Gali No-6, Krishna Nagar, Opp- Plot No-79,Sector-25, Ballabhgarh null | Faridabad | 121004 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mccb found not getting on / off due to not available site application data, Hence no replacement given to customer. Email : id not provided by customer . | Repair |  | 9- Service Validated | 2023-09-05 11:28 |  |  | 45 | INR | 45 | ENM POWER PRODUCTS
WO-11211099 | 103757696 | 2023-09-05 15:19 | 2023-09-05 |  | 2023-09-04 14:01 | EM7230 | EM7230 | EM7230 |  | DEAR SIR M/S Power Packs Associates 1st Floor, New 33 South Mada Street, Nungmbakkam Chennai, Tamilnadu 600034 Invoice date : 12/02/2023 Invoice number ; 9008438939 Contact Person at Site : Name & Mobile No. P.RAGHAVAN (9884977360 ) Alternate Mobile No : 9941411808 Contact Person at Site - Email Address** kumar@powerpacksindia.com Product Issue Type (Please select from drop down of column C-9) Are you ready to troubleshoot the issue remotely ? Yes/NO. If Yes, Our technical support engineer will call back to troubleshoot the issue remotely. NO Defective Product Model/Part No (Pls refer FAQ sheet ) EM7200 Nature of Defect* - Defects Vide Regards, Kumar Office Mobile Number : 98849 77360 PHONE 044-42137161 TELE / FAX 044-2826 5660 Email: kumar@powerpacksindia.com Power Packs Associates, (GST NO : 33ADGPR5914H1ZI ) 33/15 ,SOUTHMADA STREET NUNGAMBAKKAM CHENNAI 600 034 I have changed my email address to kumar@powerpacksindia.com. Please send all future emails to kumar@powerpacksindia.com. You will not be able to send email to my old email address. | 2023-09-04 | 2023-09-07 17:00 | No | Warranty | Power Packs Associates - 1546 | 1st Floor, New 33 (Old 15) South Mada Street, Nungmbakkam | Chennai | 600034 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Site Visit Done | Repair |  | 9- Service Validated | 2023-09-07 17:23 | case registered in parent territory |  | 25 | INR | 25 | ENM POWER PRODUCTS
WO-11211560 | 103763563 | 2023-09-05 12:14 | 2023-09-04 |  | 2023-09-04 16:34 | EM6436-05RS | EM6436-05RS | EM6436-05RS |  | EM6436 NOT WORK Dear Schneider team, This is inform to you that Schneider MAKE switch gear EM6436H IS NOT WORK Date of purchase------------------------------8/08/23 Qty.-----------------------------------------------01 Rating------------------------------------------- SR. NO-------------------------------------------540410053444 DOM---------------------------------------------010723 Bill No ------------------------------------------O1058/2023-2024 Problem-----------------------------SUPPLY 220 VOLT ON BUT METER DISPLAY NOT ON So please depute your service engineer at SITE. and removed this PROBLEM at urgent basis SITE ADDRESS AMBAY ENGG. CORPORATION, PLOT NUM-2 SASOULI ROAD YAMUNANAGAR 135001 NEAR LARK OFFICE CLINT NAME? SAHIL KAMBOJ MOBILE NUM?9896136563 | 2023-09-04 | 2023-09-06 15:31 | No | Warranty | Ambay Engineering Corporation | Plot No-2, Sasouli Road | Yamunanagar | 135001 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the meter found not power up. Hence faulty replaced. METSEEM6436HCL10NC - 1 Nos. email : sahil.kamboj@groupambika.com | Repair |  | 9- Service Validated | 2023-09-06 15:31 |  |  | 105 | INR | 105 | ENM POWER PRODUCTS
WO-11211589 | 103764829 | 2023-09-05 12:12 | 2023-09-04 | NA | 2023-09-04 16:47 | NA02504V | NA02504V | NA02504V |  | P margin-top:0;margin-bottom:0; It is not functioning in auto mode. and phase barrier not received in packed sajal Kumar Mondal Vedic Village-BA-02, Gate No-4, shekharpur, kolkata-700135. ph-9903933741 NA02504V From: Schneider Electric Customer Care <customercare.in@schneider-electric.com> Sent: 04 September 2023 13:36 To: Sajal Mondal <vedicvilla@neometaliks.com>; nagabhushana.km@se.com <nagabhushana.km@se.com> Subject: Re: NA02504V instalation, Case: 103747121, [ thread::3T2ctM34f7iAMncsFkgxlz4:: ] [External Email] The e-mail below is from an external source. Please do not open attachments or click links from an unknown or suspicious origin! Dear Team, Greetings from Schneider!! Please share the below details : 1. Complete model ref of the product 2. Invoice copy for warranty validation 3.Complete proper site address and contact details @Naga: Please check if WO is required against the said issue. After your confirmation and having all the above requested details will proceed further accordingly. Abhijit Sarkar Customer Care Centre ¦ Schneider Electric India ¦ Toll Free: 18001030011 / 18004254272 / 18004194272 ¦ Email:Customercare.in@schneider-electric.com ¦ Site: www.schneider-electric.com " Still need help? Try Chat ( https://www.se.com/in/en/ ) with Us" --------------- Original Message --------------- From: [vedicvilla@neometaliks.com] Sent: 4/9/2023 12:28 pm To: customercare.in@schneider-electric.com Subject: Re: NA02504V instalation, Case: 103747121, [ thread::Pn4jGtRdc8Sua_53vLKp4j4:: ] Dear sir My ATS is not work auto mode. How is it work in Auto mode??? Sent from Outlook for Android From: Sajal Mondal <vedicvilla@neometaliks.com> Sent: Monday, September 4, 2023 12:15:36 PM To: Schneider Electric Customer Care <customercare.in@schneider-electric.com> Subject: Re: NA02504V instalation, Case: 103747121, [ thread::Pn4jGtRdc8Sua_53vLKp4j4:: ] Dear sir Please help me how to install described ATS. I request you to take necessary steps as early as possible. Sent from Outlook for Android From: Schneider Electric Customer Care <customercare.in@schneider-electric.com> Sent: Monday, September 4, 2023 11:37:34 AM To: Sajal Mondal <vedicvilla@neometaliks.com> Subject: NA02504V instalation, Case: 103747121, [ thread::Pn4jGtRdc8Sua_53vLKp4j4:: ] [External Email]The e-mail below is from an external source. Please do not open attachments or click links from an unknown or suspicious origin! Dear Sir,Greetings from Schneider Electric!If you have any query over below reply, please try chat with usClick on Chat to initiate the chatKindly brief your query in detail so that we can help you further. Please not if installation visit is required, It will be on paid basis. Kindly confirm for same. **For all further communication regarding this case, please reply directly to this email**Have a Nice day! Regards, Gursewak Singh Customer Care Centre ¦ Schneider Electric India ¦ Toll Free: 18001030011 / 18004194272 ¦ Email:customercare.in@se.com ¦ Site: www.se.com/in Our toll free lines are open from 9 am to 6 pm (Monday to Friday). Alternatively, you can also contact us via online chat (9 am to 8 pm, Monday-Saturday) or email customercare.in@se.com. You can access order related inquiries and technical FAQs through our website, mySE, and our mySchneider app. Links can be found via our website www.se.com/in Thank you. Sent On:3/9/2023 From:vedicvilla@neometaliks.com NA02504V instalation --------------- Original Message --------------- From: Schneider Electric Customer Care [customercare.in@schneider-electric.com] Sent: 4/9/2023 10:29 am To: vedicvilla@neometaliks.com Subject: RE: Schneider Electric Case # 103747121: NA02504V instalation - [ thread::Pn4jGtRdc8Sua_53vLKp4j4:: ] Dear Customer, Greetings for the day! Thankyou for contacting Schneider Electric. We have forwarded your request to the concerned team. A representative from the same will get in touch with you shortly on the same. Your patience and cooperation is highly appreciated. Feel free to reach out for any further queries or concerns. Regards, Case - Primary Support Center Queue Customer Care Centre ¦ Schneider Electric India ¦ Toll Free: 18001030011 / 18004194272 ¦ Email: customercare.in@se.com ¦ Site: www.se.com/in --------------- Original Message --------------- From: Schneider Electric [customercare.in@schneider-electric.com] Sent: 3/9/2023 12:33 pm To: vedicvilla@neometaliks.com Subject: Schneider Electric Case # 103747121: NA02504V instalation - Dear Sir/Madam, Thank you for contacting Schneider Electric India Customer Care Centre. We acknowledge receipt of your message. Your case has been registered with us and given below are the reference details. Please quote this reference number for all future communications on this subject. Your request / query would be responded to within one working day, unless the issue is a complex one that requires other functional interlocks. Please avoid sending reminders within this time, since the CRM systems will update the date / time to the latest e-mail received from you and and may cause duplication of case IDs and efforts at our end. Case Reference #: 103747121 Date Created: 9/3/2023 Question: NA02504V instalation We work from 0900 hrs to 2000 hrs, Monday to Saturday (except public holidays). You can reach us via email Customercare.in@schneider-electric.com or our toll free numbers 1800 103 0011 / 18004254272 Best Regards ----------------------------------------------------------------------------------------------------------- Customer Care Centre ¦ Schneider Electric ¦ India ¦ Site: www.schneider-electric.com ¦ Toll Free: 18001030011 / 18004254272 ¦ Email: Customercare.in@schneider-electric.com Schneider Electric Disclaimer This message and any attachment are confidential and may be privileged or otherwise protected from disclosure. If you are not the intended recipient, please telephone or email the sender and delete this message and any attachment from your system. If you are not the intended recipient you must not copy this message or attachment or disclose the content to any other person or entity. If you have received this email in error, please notify to in-care@in.schneider-electric.com *** Please consider the environment before printing this e-mail thread::Pn4jGtRdc8Sua_53vLKp4j4:: No Attachments linked to the email thread::3T2ctM34f7iAMncsFkgxlz4:: | 2023-09-04 | 2023-09-05 11:15 | No | Warranty | NEO METALIKS | sajal Kumar Mondal Vedic Village-BA-02, Gate No-4, null | kolkata | 700135 | West Bengal | India FS ED&I CSP East Team B.D Electroservices Kolkata | RAHUL RAY_B.D Electroservices Kolkata | B.D Electroservices(500017330) | Visited site and checked the ATS found that the DG supply is looped between R and Y phase thats way it is not working. For run into auto mode customer needs to give 3 phase supply to DG terminal in ATS. Customer adviced to give 3 phase for run ATS properly.Till then manually for change over. | Repair |  | 9- Service Validated | 2023-09-05 12:26 |  |  | 28 | INR | 28 | ENM POWER PRODUCTS
WO-11193798 |  | 2023-09-25 15:35 | 2023-08-09 |  | 2023-09-01 12:47 | Leonardo EV,CW,EC Fan,TDCV1200A,Downflow With Heater & Humidifier | TDCV1200AN001 | TDCV1200AN001 | NUCW4176 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-01 | 2023-08-09 15:39 | No | Contract | Statestreet HCL Technologies India Limited | MODULES 1,2,3, 2ND FLOOR, TIDEL PARK COIMBATORE LTD (TPCL) CIVIL AERODROME POST COIMBATORE Tamil Nadu 641014 India VILANKURICHI VILLAGE, CIVIL AERODROME POST,COIMBATORE 641 014, TAMILNADU, INDIA | COIMBATORE | 641014 | Tamil Nadu | India FS South4 Cooling CSP Unity Air conditioning Engineers Chennai | K.Mohan Raj_ Unity Air conditioning Engineers Chennai | UNITY AIRCONDITIONING ENGINEERS | PM service completed | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-25 15:49 |  |  | 1610 | INR | 1610 | ENM SECURE POWER
WO-11211646 | 103767254 | 2023-09-05 11:54 | 2023-09-04 |  | 2023-09-04 17:14 | LC1D80AT7 | LC1D80AT7 | LC1D80AT7 |  | Contactor LC1D80A Invoive 22 mrch 2023 Invice number 221 Ruchi Enterprices 9870965814 MR. Ashish Goyal Pacific Dynamics Salampure Rjaputan Industrial area Roorkee Uttrakhand 247667 Not working ashish.goel@pacific-dynamics.com | 2023-09-04 | 2023-09-05 11:55 | No | Warranty | Pacific Dynamics | Khasra No.- 986M & 987, Salempur Rajputan Industrial Area, | Roorkee | 247667 | Uttarakhand | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the contactor found working ok. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-05 12:03 |  |  | 2 | INR | 2 | ENM POWER PRODUCTS
WO-11193799 |  | 2023-09-25 15:29 | 2023-08-09 |  | 2023-09-01 12:47 | Leonardo EV,CW,EC Fan,TDCV1200A,Downflow With Heater & Humidifier | TDCV1200AN001 | TDCV1200AN001 | NUCW4179 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-01 | 2023-09-25 15:38 | No | Contract | Statestreet HCL Technologies India Limited | MODULES 1,2,3, 2ND FLOOR, TIDEL PARK COIMBATORE LTD (TPCL) CIVIL AERODROME POST COIMBATORE Tamil Nadu 641014 India VILANKURICHI VILLAGE, CIVIL AERODROME POST,COIMBATORE 641 014, TAMILNADU, INDIA | COIMBATORE | 641014 | Tamil Nadu | India FS South4 Cooling CSP Unity Air conditioning Engineers Chennai | K.Mohan Raj_ Unity Air conditioning Engineers Chennai | UNITY AIRCONDITIONING ENGINEERS | PM service completed | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-25 15:49 |  |  | 410 | INR | 410 | ENM SECURE POWER
WO-11193800 |  | 2023-09-25 15:34 | 2023-08-09 |  | 2023-09-01 12:47 | Leonardo EV,CW,EC Fan,TDCV1200A,Downflow With Heater & Humidifier | TDCV1200AN001 | TDCV1200AN001 | NUCW4177 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-01 | 2023-08-09 15:38 | No | Contract | Statestreet HCL Technologies India Limited | MODULES 1,2,3, 2ND FLOOR, TIDEL PARK COIMBATORE LTD (TPCL) CIVIL AERODROME POST COIMBATORE Tamil Nadu 641014 India VILANKURICHI VILLAGE, CIVIL AERODROME POST,COIMBATORE 641 014, TAMILNADU, INDIA | COIMBATORE | 641014 | Tamil Nadu | India FS South4 Cooling CSP Unity Air conditioning Engineers Chennai | K.Mohan Raj_ Unity Air conditioning Engineers Chennai | UNITY AIRCONDITIONING ENGINEERS | PM service completed | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-25 15:49 |  |  | 1610 | INR | 1610 | ENM SECURE POWER
WO-11215308 | 103769796 | 2023-09-05 12:24 | 2023-09-05 |  | 2023-09-05 11:07 | LC1D50AF7 | LC1D50AF7 | LC1D50AF7 |  | Dear Sir, KIndly find the attached COMPLAINT registration form. Company Name & Complete Address with pin code - Where product is installed M/s.LAKSHMI MACHINE WORKS FOUNDRY , UNIT-3, FMC SF NO.43 & 467 , ARASUR VILLAGE,PALLADAM TAKUK 641407 vpncbe@gmail.com Contact Person at Site : Name & Mobile No. MR.B.KARTHICK Alternate Mobile No : 0422-7198515 Contact Person at Site - Email Address** Defective Product Model/Part No (Pls refer FAQ sheet ) LC1D50AF7 Nature of Defect* Contactor tips got frequent open and cause breakdown in cranes -- | 2023-09-05 | 2023-09-21 15:53 | No | Warranty | M/s.LAKSHMI MACHINE WORKS FOUNDRY | M/s.LAKSHMI MACHINE WORKS FOUNDRY , UNIT-3, FMC SF NO.43 & 467 , ARASUR VILLAGE,PALLADAM TAKUK 641407 null | Coimbatore | 641407 | Tamil Nadu | India FS ED&I CSP South Team Power Pro Engineering Services Coimbatore | KV ARUNKUMAR_POWER PRO ENGINEERIG SERVICES COIMBATORE | Powerpro Engineering Services | WE HAVE VISITED THE SITE AND INSPECTED WE FOUND CONTACTOR POLE OPEN CIRCUITED & POLE OPEN CIRCUITED WE HAVE COLLECTED THE DETAILS WE WILL DISCUSSED WIT OUR SEIPL TEAM AND WE WILL GET BACK TO YOU | Repair |  | 9- Service Validated | 2023-09-21 15:55 |  |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11193801 |  | 2023-09-25 15:33 | 2023-08-09 |  | 2023-09-01 12:47 | Leonardo EV,CW,EC Fan,TDCV1200A,Downflow With Heater & Humidifier | TDCV1200AN001 | TDCV1200AN001 | NUCW4178 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-01 | 2023-09-25 15:37 | No | Contract | Statestreet HCL Technologies India Limited | MODULES 1,2,3, 2ND FLOOR, TIDEL PARK COIMBATORE LTD (TPCL) CIVIL AERODROME POST COIMBATORE Tamil Nadu 641014 India VILANKURICHI VILLAGE, CIVIL AERODROME POST,COIMBATORE 641 014, TAMILNADU, INDIA | COIMBATORE | 641014 | Tamil Nadu | India FS South4 Cooling CSP Unity Air conditioning Engineers Chennai | K.Mohan Raj_ Unity Air conditioning Engineers Chennai | UNITY AIRCONDITIONING ENGINEERS | PM service completed | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-25 15:49 |  |  | 410 | INR | 410 | ENM SECURE POWER
WO-11215366 | 103770894 | 2023-09-05 12:26 | 2023-09-05 |  | 2023-09-05 11:21 | GV2ME02 | GV2ME02 | GV2ME02 | TH2042 | Dear Sir, Kindly find the attached Complaint registration form. Company Name & Complete Address with pin code - Where product is installed M/s.LAKSHMI ELECTRICAL CONTROL SYSTEMS LIMITED ARASUR, COIMBATORE COIMBATORE -641407 Contact Person at Site : Name & Mobile No. MR.PRABHU Alternate Mobile No : 8344461323 Contact Person at Site - Email Address** prabhu.s@lecsindia.com Product Issue Type (Please select from drop down of column C-9) Defective Product Model/Part No (Pls refer FAQ sheet ) GV2ME02- 1NO. -- | 2023-09-05 | 2023-09-07 16:40 | No | Warranty | Lakshmi Electrical Control Systems | 399, ARASUR, AVINASHI Road | Coimbatore | 641407 | Tamil Nadu | India FS ED&I CSP South Team Power Pro Engineering Services Coimbatore | KV ARUNKUMAR_POWER PRO ENGINEERIG SERVICES COIMBATORE | Powerpro Engineering Services | WE HAVE VISITED THE SITE AND INSPECTE WE FOUND MPCB MOUNTING ISSUE WE HAVE RECTFIY THE SAME TESTED AND FOUND OK TESTED ELECTRICALLY OK | Repair |  | 9- Service Validated | 2023-09-07 16:45 |  |  | 31 | INR | 31 | ENM POWER PRODUCTS
WO-11193802 |  | 2023-09-25 15:36 | 2023-08-09 |  | 2023-09-01 12:47 | Leonardo EV,CW,EC Fan,TDCV1200A,Downflow With Heater & Humidifier | TDCV1200AN001 | TDCV1200AN001 | NUCW4175 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-01 | 2023-08-09 15:40 | No | Contract | Statestreet HCL Technologies India Limited | MODULES 1,2,3, 2ND FLOOR, TIDEL PARK COIMBATORE LTD (TPCL) CIVIL AERODROME POST COIMBATORE Tamil Nadu 641014 India VILANKURICHI VILLAGE, CIVIL AERODROME POST,COIMBATORE 641 014, TAMILNADU, INDIA | COIMBATORE | 641014 | Tamil Nadu | India FS South4 Cooling CSP Unity Air conditioning Engineers Chennai | K.Mohan Raj_ Unity Air conditioning Engineers Chennai | UNITY AIRCONDITIONING ENGINEERS | PM service completed | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-25 15:50 |  |  | 1610 | INR | 1610 | ENM SECURE POWER
WO-11215400 | 103770929 | 2023-09-05 12:28 | 2023-09-05 |  | 2023-09-05 11:32 | LC1D18BD | LC1D18BD | LC1D18BD |  | Dear Sir, Dear Sir, Kindly find the attached Complaint registration form. Company Name & Complete Address with pin code - Where product is installed M/s.LAKSHMI ELECTRICAL CONTROL SYSTEMS LIMITED ARASUR, COIMBATORE COIMBATORE -641407 Contact Person at Site : Name & Mobile No. MR.PRABHU Alternate Mobile No : 8344461323 Contact Person at Site - Email Address** prabhu.s@lecsindia.com Product Issue Type (Please select from drop down of column C-9) Are you ready to troubleshoot the issue remotely ? Yes/NO. If Yes, Our technical support engineer will call back to troubleshoot the issue remotely. NO Defective Product Model/Part No (Pls refer FAQ sheet ) LC1D18BD- 1NO. Shutdown availability if applicable Photograph of product where Serial No/Batch Code or Date of Manufacturing printed - Please refer FAQ sheet to find the Batch code details on the products Proof Of Purchase - Pease attach SE*** Authorised Partner Invoice soft copy along with this check list 9008657824/27.07.2023 Name & phone No: of person registering the Service Request Premanand PK - 9043006683 -- | 2023-09-05 | 2023-09-14 22:16 | No | Warranty | Lakshmi Electrical Control Systems Limited | Arasur, | Coimbatore | 641407 | Tamil Nadu | India FS ED&I CSP South Team Power Pro Engineering Services Coimbatore | KV ARUNKUMAR_POWER PRO ENGINEERIG SERVICES COIMBATORE | Powerpro Engineering Services | WE HAVE VISITED THE SITE AND INSPECTED WE FOUND MPCN POLE OPEN CIRCUITED INTERNALLY WE HAVE COLLECTED THE DETAILS FOR FURTHER ACTION AND ARRAGING FIR FREE REPALCEMENT FOR THIS | Repair |  | 9- Service Validated | 2023-09-14 22:18 | Hi Team, Material booked zfre Zvo : 226038975 |  | 21 | INR | 21 | ENM POWER PRODUCTS
WO-11215492 | 103768294 | 2023-09-05 14:24 | 2023-09-05 |  | 2023-09-05 12:05 | D2ADTLB30400KD | D2ADTLB30400KD | D2ADTLB30400KD |  | Subject: NON WORKING OF ASCO MAKE 400A 4P ATS SWITCH 0F SERIES 230 DEAR ALL, we are a leading panel manufacturer in Mumbai, last year we have purchased ASCO make 400A 4 pole ATS switch of 230 series with controller from SP electric. This ATS switch is not working at the site due to some short circuit problem. We request you to kindly depute your service person at the following address ASAP to check the issue/problem. site address - SERENITY VILLA, REVAS-MANDVA ROAD, ALIBAUG, maharashtra. CONTACT PERSON - MR. SAMPAT - 92218 15725 / 83800 15725 your quick action in this matter shall be highly appreciated. awaiting your kind reply THANKS & REGARDS, GAUTAM PANCHAL - 98212 92958 VIGELEC CONTROLS MSME - UDYAM - MH - 18 - 0204228 | 2023-09-05 | 2023-09-06 15:43 | No | Warranty | Surendra Kumar | serenity villa , revas-mandva road | Alibaug | 402207 | Maharashtra | India FS ED&I CSP West Team R P Electrical Mumbai | Samrat Pawaskar R P Electrical Mumbai | R P Electrical | Observed ATS found ATS not working in auto mode. PCB card burnt due to may be in short circuit. Hence replacement void. | Repair |  | 9- Service Validated | 2023-09-06 15:53 |  |  | 125 | INR | 125 | ENM POWER PRODUCTS
WO-11215677 | 103786345 | 2023-09-06 15:08 | 2023-09-05 |  | 2023-09-05 13:28 | LC1G5004KUEN | LC1G5004KUEN | LC1G5004KUEN |  | LC1G5004KUEN - Pole Burnt issue LJ2236200100116 Nasim Saifi KRS Handicraft Plot number G 326 Phase 2 MG Road Industrial area Gaziayabad 201015 naseem.saifi123@gmail.com Ankit Sharma 8010274525 | 2023-09-05 | 2023-09-12 15:39 | No | Warranty | KRS Handicraft | Plot number G 326 Phase 2 MG Road Industrial area Gaziayabad | Gaziayabad | 201015 | Uttar Pradesh | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the contactor found phase missing, Hence faulty replaced. LC1G5004KUEN - 1 nos Email : id not provided by customer. | Repair |  | 9- Service Validated | 2023-09-12 15:43 |  |  | 52 | INR | 52 | ENM POWER PRODUCTS
WO-11216255 | 103791817 | 2023-09-07 14:35 | 2023-09-05 |  | 2023-09-05 17:03 | METSEEM6436HCL10NC | METSEEM6436HCL10NC | METSEEM6436HCL10NC |  | Re: Please register complaint of Part Dear Team, In ref. to trailing mail, detail mentioned below;- Part ref - , METSEEM6436HCL10NC, QTY -1 Invoice no- AA3330021004 Inv doc no- 9008431475 Inv date - 13/02/2023 Customer mail Id:- jupl@jukentech.com Site Address :- JUKEN UNIPRODUCTS PVT. LTD. C-14 & 15, SECTOR ? 57, NOIDA ? 201307. Contact No. :- 8076668746(Dabral ji) | 2023-09-05 | 2023-09-07 14:43 | No | Warranty | Juken Uni Products Pvt Ltd | 14&15 Sector 57 | Noida | 201307 | Uttar Pradesh | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the meter found display not showing, Hence faulty replaced . METSEEM6436HCL10NC - 1 nos Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-07 15:51 |  |  | 65 | INR | 65 | ENM POWER PRODUCTS
WO-11216282 | 103792532 | 2023-09-06 10:18 | 2023-09-05 | Contactor struck issue | 2023-09-05 17:18 | LC1D115F7 | LC1D115F7 | LC1D115F7 |  | Pl issue complaint no. Pl issue complaint no. 1. Name of Customer: Diamond Electricals 2. Site Address: - GALA NO. 124, PARMAR COMPLEX, NEAR ADVANI ORLICON, CHINCHWAD, PUNE - 411019 3. Name of contact person at site: MR. JAYGUDE 4. Contact Phone / Mob. No: - 96574 97356 5. Defective product details:- LC1D115F7 6. Product Make:- Schneider Electric 7. Nature of Defect: - Contactor Stuck issue 8. Shutdown availability if applicable nil 9. Serial No: or DOM of the product- PK23121 10. Dealer Name /OA no. /Invoice Details: - 11. Commissioned / Installed date: - Nil 12. Name & phone No: of person registering the complaint: Swamesh Methare (Mob No 8888192186) | 2023-09-05 | 2023-09-08 11:10 | No | Warranty | Diamond Electricals | 124, Parmar Complex, Chinchwad, | Pune | 411019 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Sachin Jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked Contactor stuck issue. this part is already installed condition. this interlocking block not working properly. fitting the block properly. and Testing found ok. contactor found ok. | Repair |  | 9- Service Validated | 2023-09-08 11:14 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11216291 | 103769000 | 2023-09-05 17:56 | 2023-09-05 |  | 2023-09-05 17:21 | METSEEM6436HCL10RS | METSEEM6436HCL10RS | METSEEM6436HCL10RS | 190123 | EM6436H LED RS485 communication not working L1 Technical Team Comment: METSEEM6436HCL10RS DOM:- 190123 (Within Warranty) Checked the communication of meter remotely, EM6400NG and Pm8000 Meters are communicating with same converter only EM6436H meter is not communication, Suspecting port failure, Kindly arrange WO to check further. Customer mail We have received Total 20 Nos. Energy meter with PO No. 9100153374, Date of purchase Feb - 2023 ; PR No. 4000086517; Purchased From M/s. Smart Control Meter Details :- Model No. EM6436H LED Sl No. 540420218876, 540420218736, 540420218775 DOM:- 190123 Purchased From :- M/s. Smart Control ISSUE:- Modbus RS485 communication not working . Checked through Modscan32 -software image.png NOTE:- Other meters - EM6400NG , PM8000 communication are working fine . Schneider Electric Service Engineer MOM attached Kindly do the needful to sort-out the issue. Thanks and Regards, Parameshwaran C Electrical - Manager Vasind Works, Village - Vasind, Tal. - Shahapur, Dist. - Thane ? 421601 ¦ Maharashtra ¦ India T: 02527 667400-26 Ext.: 423; M +91 9100950226 | 2023-09-05 | 2023-09-06 17:00 | No | Warranty | JSW Steel Limited | Village Vasind ,Taluka - Shahapur | Thane | 421604 | Maharashtra | India FS ED&I CSP West Team Smart Control Mumbai | Prathmesh Gavde_Smartcontrol Mumbai | Smart Control (4109) | 1) Given 230 VAC supply on Meter & connect to Modscan and check communication found Even & Odd Parity meter communicated properly. But non Parity meter not communicated because EM6436H meter by default stop bit 02. 2) So change stop bit and checked communication found communicate properly. 3) Meter working properly. Site is closed. | Repair |  | 9- Service Validated | 2023-09-07 10:42 | VIP FSR= No 3. FSR Request: Unavailability of the preferred FSR, need to depute Non VIP FSR(Requester Name). |  | 57 | INR | 57 | ENM POWER PRODUCTS
WO-11216358 | 103796370 | 2023-09-06 10:25 | 2023-09-05 |  | 2023-09-05 17:58 | LV525303 | LV525303 | LV525303 |  | Fwd: Case : 103585700 dt. 28.8.23 Mr. Virendra Jain C- 46 HBU nagar,Opp SBI Bank,Pushkar Road,Ajmer Mr. Virendra Jain 9672712340 Product : A9KF71340 ,LV525303 Sr. no. :- D2212 ,10-2023-W16-4-1618L1 Dolly free -- *WITH REGARDS-* Sarabjit Singh SHARMA ELECTRIC WORKS | 2023-09-05 | 2023-09-11 15:36 | No | Warranty | Virendra Jain | C- 46 HBU nagar, Opp SBI Bank, Pushkar Road, Ajmer | Ajmer | 305004 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | Checked the mcb found dolly free and mccb found not getting on , Hence faulty replaced. A9N3P40C- 1 nos LV525303 - 1 nos Email : vei.ajmer2010@gmail.com | Repair |  | 9- Service Validated | 2023-09-11 15:38 |  |  | 160 | INR | 160 | ENM POWER PRODUCTS
WO-11221293 | 103795805 | 2023-09-06 12:31 | 2023-09-06 | Escalate to Schneider | 2023-09-06 12:22 | GCR_LV_APFC | GCR_LV_APFC | GCR_LV_APFC | ME-E-M140927 | Fwd: APFC + AHF Panel fault and abnormal sound from MCCB of transformer -2 AHF 2 Panel. 1 Name of Customer AVGOL India Private Limited 2 Site Address Plot 731&732,GIDC Masvad,Halol Panchamahals,Gujarat India,389350. 3 Name of contact Person at site Manikanta 4 Contact Phone / Mob. No: +917383769701 5 Defective product details Transformer 2 inside AHF 2 main breaker trip with abnormal sound from panel inside 6 Product Make Scheneider 7 Nature of Defect AHF main breaker trip and abnormal sound like some something burst and smoke came from panel inside. 8 Shutdown availability if applicable Siwtch off both ACB at LT panel and APFC+AHF panel seeking some urgent visit to site 9 Warranty status Yes 10 Commissioned / Installed date 01.03.2023 11 Serial No: or DOM of the product ME-E-M140926 12 Name & phone No: of person registering the complaint Manikanta & 7383769701 | 2023-09-06 | 2023-09-11 16:58 | No | Warranty | Avgol Nonwovens India Pvt Ltd | Industrial Plot num 731/732 ,Halol-2,Halol Maswad ,GIDC | Panchmahal | 389230 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Ritesh Prajapati_Anik Engineering Ahmedabad | Anik Engineering (554) | VIsited site and checked the AHF, observed Flashing att MCCB airvent, Open the AHf for primary analysis observed heavy flashing in the AHF, Y phase gate driver board and IGBT had flashover, Also flashing observed at Power board and capacitor are damaged, checked the filter assembly observed the line contactor is stuck dut eo flashing, checked the time delay fuses - F1 - F6 are ok, F 7 fuse is blown, case escalated to schneider for further action | Repair |  | 9- Service Validated | 2023-09-11 16:59 | =S= Consig Fill up 226042794 |  | 140 | INR | 140 | ENM POWER PRODUCTS
WO-11221452 | 103818173 | 2023-09-06 17:22 | 2023-09-06 |  | 2023-09-06 13:28 | LC1E1201M7 | LC1E1201M7 | LC1E1201M7 |  | Dear Mr. Akshay Gandotra, Inv. copy attached herewith. Shailesh Makwana From: Mail2Case India <customercare.in@schneider-electric.com> Sent: 05 September 2023 15:58 To: jignesh.sonagara@briskelectronics.com Cc: complaints@briskelectronics.com Subject: RE: FW: Book Complain @ KAIZEN SOLUTION [ thread::y4e383tWfrudXjnf55nYZT4:: ] Dear Sir/Ma'am, Greetings from Schneider!! Thank you for reaching out to us and giving us an opportunity to serve you. We understand your concern in this regard and please be rest assured that we are here to resolve your concern in the most appropriate manner. Request you to share the serial number or the invoice copy for us to validate the warranty and take up the issue further . Have a great day ahead! Regards , Akshay Gandotra Customer Care Centre ¦ Schneider Electric India ¦ Toll Free: 18001030011 / 18004194272 ¦ Email:Customercare.in@schneider-electric.com ¦ Site: www.se.com/in --------------- Original Message --------------- From: [jignesh.sonagara@briskelectronics.com] Sent: 5/9/2023 2:46 pm To: customercare.in@schneider-electric.com Cc: complaints@briskelectronics.com Subject: FW: Book Complain @ KAIZEN SOLUTION Dear Team, Kindly arrange service Engineers at below address for the Multiple product service case. CONTACT PERSON : CHINTAN PATEL CONTACT NUMBER : 94092 51404 ADDRESS : D-11 PANCHRATNA TWO INDUSTRIAL PARK, PALDI-KANKEJ BAREJA DASCROI, BAREJA AHMEDABAD 382425 Part no Qty Problem A9KF71425BQ 1 Tripping A9KF71432BQ 2 dolly A9KF71410BQ 1 dolly A9KF71210BQ 1 Tripping A9KF71106BQ 3 Tripping A9N4P63C 1 Tripping LC1DT40M7 1 Pole problem LC1E1201M7 6 Pole problem LC1E2510M7 1 Contact METSEEM6436HCL10RS 1 display LC1D18M7 1 Pole problem From: sales@kaizensolution.net Sent: 04 September 2023 16:27 To: jignesh.sonagara@briskelectronics.com Cc: kaizen121.solution@gmail.com Subject: Book Complain Dear Jignesh Bhai , Please book below direct complain at our address . Part no Qty Problem A9KF71425BQ 1 Tripping A9KF71432BQ 2 dolly A9KF71410BQ 1 dolly A9KF71210BQ 1 Tripping A9KF71106BQ 3 Tripping A9N4P63C 1 Tripping LC1DT40M7 | 2023-09-06 | 2023-09-08 14:06 | No | Warranty | Chintan Patel | D-11 PANCHRATNA TWO INDUSTRIAL PARK, PALDI-KANKEJ BAREJA DASCROI, BAREJA | AHMEDABAD | 382425 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Sitpuriya_Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the proudct found physically oibserved ok. LC1E2510M7 SR NO : 1022496 observed screw thread problem. in no ( 14 ) terminal so give free replacemnet. LC1E1210M7 SR NO : 10232322 screw thread problem so free replacemnet. LC1D18M7 SR NO : 1022336 observed no not working so give a free replacemnet. METSEEM6436HCL10RS SR NO : 540420229323 DOM : 210323 We give control supply but display not getting on so for customer satisfaction free replacemnt. A9KF71432 SR NO : D2311 -02 observed screw thread problem so give free rreplacemnet. A9KF71106 SR NO : D2231 - 02 Nos observed free replacement. A9KF71210 SR NO : D2303 Dolly free replacement. A9KF71410 SR NO : D2224 - 01 Nos observed so give free replacemnet. A9N4P63C SR NO : D2314 01 Dolly free. LC1DT40M7 SR NO : 1022304 observed ok and tested ok. LC1E1201M7 SR NO : 1022283 -06 Nos observed physically ok and testd ok by multimeter . | Repair |  | 9- Service Validated | 2023-09-08 14:07 | =S= Consig Fill up 226034255 |  | 24 | INR | 24 | ENM POWER PRODUCTS
WO-11222041 | 103825315 | 2023-09-07 16:59 | 2023-09-06 |  | 2023-09-06 17:13 | LC1D115 | LC1D115 | LC1D115 |  | Contactor Not working LC1D115 1PC Serial number : 13823420131A05 Not function Invoice Date: Tara Minerals and chemicals Pvt. Ltd 751 UMEID HOSPITAL ROAD NEAR GEETA BHAWAN, JODHPUR 342001 Rajasthan harsh@taraminerals.co.in 9413323335 Harsh Boob | 2023-09-06 | 2023-09-07 17:03 | No | Warranty | Tara Minerals and chemicals Pvt. Ltd | 751 UMEID HOSPITAL ROAD NEAR GEETA BHAWAN null | JODHPUR | 342001 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Amarjeet Singh Sharma Electric Jaipur | Sharma Electric Works | Checked the contactor found heating issue due customer not use MPCB in backup protection and contactor found out of warranty from serial number , Hence no replacement given to customer . Email : id not provided by customer . | Repair |  | 9- Service Validated | 2023-09-08 17:14 |  |  | 338 | INR | 338 | ENM POWER PRODUCTS
WO-11222140 | 103825063 | 2023-09-06 18:22 | 2023-09-06 |  | 2023-09-06 18:03 | GCR_ASCO_MV_IEC | GCR_ASCO_MV_IEC | GCR_ASCO_MV_IEC | 2312721-07WE | ASCO Complaint /Delhi Dear CCC Team, Please create WO for the complaint. ATS Ref:- GCR_ASCO_MV_IEC SL No:-2312721-002WE Under Warranty:- Yes Problem:- Few Inductions loads are tripping during re transfer. Customer details:- YOTTA Infrastructure Solutions LLP Greater Noida West Link Rd, Tusiana Village, Knowledge Park V, Greater Noida, Uttar Pradesh 201306. Mr. Lavkanth lsrivastava@yotta.com 8470803769 Thanks & Regards _________________________________________________________________________________________________ Nagabhushan K M Senior Manager | 2023-09-06 | 2023-09-07 10:58 | No | Warranty | YOTTA Infrastructure Solutions LLP | West Link Rd, Tusiana Village, Knowledge Park V | Greater Noida | 201306 | Uttar Pradesh | India FS ED&I CSP North Team Total Solution Services Delhi | Rahul Kumar Total Solution Services Delhi | Total Solution Services(500054203) | We have Visit the Site And Checked the ATS. I Observed the ATS in Controlling Issue. ATS in Working Ok | Repair |  | 9- Service Validated | 2023-09-07 10:58 |  |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11223392 | 103835167 | 2023-09-07 15:01 | 2023-09-07 |  | 2023-09-07 09:49 | GCR_NW_CB | GCR_NW_CB | GCR_NW_CB | 225461777 | Re: Problem in 5000A NW ACB, Case: 103826481, [ thread::m1sbW0zifHuru7wqU4aVBT4:: ] Here customer is Nestlé and they have insisted to service Engg. as this breaker is in restricted area, photo are not allowed there. Secondly this complete order is executed by Schneider -SITC. Request you to generate WO, our service team know this case and it will be resolved by their visit. Control Terminal are not working in 5000A ACB Qty-1 Nos. as per last purchase on 15/05/2023 so you will solve this problem as soon as possible. Nestle India Ltd. Plot No. SM-38, GIDC-II, Siyawada Chowkdi, Sanand,Ahmedabad-382170 Contact Person- Naman Pandey - 9971646011 So provide service & solve matter. Best Regards, Jitendra Patel ¦ Procurement Logo | 2023-09-07 | 2023-09-11 09:55 | No | Warranty | Nestle India Limited | Plot no 38, GIDC-II, Sanand Industrial Estate, Siyawada Chokadi, Sanand. | Ahmedabad | 382170 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Mistri Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physically observed ok. Taken rack in rack out operation observed in test button position control of terminal not connect properly . Remove acb from chasis taken with out acb rack in rack out operation observed rhs side ralt operating tenth from position . remove rail and set proper position. trial t aken on off and position contct are working properly | Repair |  | 9- Service Validated | 2023-09-11 09:56 | VIP FSR= No 1. Preferred VIP FSR not available in that Particular Region. |  | 55 | INR | 55 | ENM POWER PRODUCTS
WO-11223435 | 103792920 | 2023-09-09 11:18 | 2023-09-07 |  | 2023-09-07 10:36 |  |  |  |  | RMA 103792920_RO 61362380 | 2023-09-07 | 2023-09-12 12:00 | No | Warranty | Industrial Marketing Inc.(1666) | 55, Paradise Complex, Opp-College, Sayajiganj, | Vadodara | 390005 | Gujarat | India FS ED&I CSP West Team Jay Services Vadodara | Ghanshyam Kachiya_Jay Services Vadodara | Jay Services | We visited at site & checked that Relay all power contacts found ok. We checekd manually trip & Aux contact continuity observed NC open & NO continuity ok. After reset relay observed NC contact open . It is not repairable. Now we replace to enduser from our distributor stock. 226038999 | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-12 07:44 | 226038999 |  | 4 | INR | 4 | ENM POWER PRODUCTS
WO-11223741 | 103797099 | 2023-09-07 16:23 | 2023-09-07 |  | 2023-09-07 10:51 |  |  |  |  | RMA 103797099_RO 61365981 | 2023-09-07 | 2023-09-21 16:16 | No | Warranty | VPN Agenciies | 522, Nanjappa road, vpn agenciies, near avinasi road | COIMBATORE | 641018 | Tamil Nadu | India FS ED&I CSP South Team Power Pro Engineering Services Coimbatore | KV ARUNKUMAR_POWER PRO ENGINEERIG SERVICES COIMBATORE | Powerpro Engineering Services | we have inspected we found coil issue we have rectfied the same tested and found working ok | Assessment/ Inspection | Data Collection | 8- Service Completed | 2023-09-21 16:19 |  |  | 1 | INR | 1 | ENM POWER PRODUCTS
WO-11195129 | 103719315 | 2023-09-02 11:03 | 2023-09-01 |  | 2023-09-01 16:25 | Easy UPS 3S 20 kVA 400 V 3:3 UPS for external batteries | E3SUPS20KH | E3SUPS20KH | 9E2250T13416 | DOP: 14 mar 2023 P: No power output C: Normal T: Checked with Customer once power outage UPS will also turn off. S: Onsite | 2023-09-01 | 2023-09-02 18:23 | No | Warranty | Mata Amirtanandamayi Math | Amirtha Vidyalayam, Phase 3, Near TCS, Hinjewadi Rajiv Gandhi Infotech Park, Hinjawadi | Pune | 411057 | Maharashtra | India FS West1 HBN CSP_United Solutions Pune | Hamid Sayyad_United Solutions Pune | United Solutions | Checked UPS on mains battery and henset mode. Found ger set phase sequence wrong. Suggested to customer to correct it. UOs working fine on mains mode and on battery mode | Repair |  | 8- Service Completed | 2023-09-02 18:26 |  |  | 0 | INR | 0 | ENM SECURE POWER
WO-11223949 | 103846772 | 2023-09-07 12:08 | 2023-09-07 |  | 2023-09-07 10:59 | NX160TPXDI | NX160TPXDI | NX160TPXDI |  | Complaint No. reqd A/c MG petrochem Dear Team Please issue the Complaint No. M/S M G Petrochem Pvt Ltd, Village Ferozepur Raipur Rani Haryana. Mr Swapnil Jadhav 9767858241 Product : SDF NX160 , NX160TPXDI / LRE3 (30-40A) Srn : 10-22 G 123 Phase missing / Abnormal Heating Issue Regards Mukesh Kumar | 2023-09-07 | 2023-09-07 12:50 | No | Warranty | M.G.Petrochem Pvt.Ltd. | Village Firozpur, Tehsil Raipur Rani, | Panchkula | 134204 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Ram Ashish Sharma Electric Chandigarh | Sharma Electric works(1003) | Visited the site and collect the site details,(site date) for the analysis. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-07 17:27 |  |  | 45 | INR | 45 | ENM POWER PRODUCTS
WO-11224352 | 103846697 | 2023-09-07 12:07 | 2023-09-07 |  | 2023-09-07 11:04 | LV508241 | LV508241 | LV508241 | 10-23012 | Complaint No. reqd ear Team Please Issue Case No. Manoj Industries GT Road, Near Sarb Mall Focal Point Jalandhar Mr Manoj 9872398787 MCCB LV508241 Sr No. 10-23012 Handle Fitment Not Proper Regards Mukesh Kumar | 2023-09-07 | 2023-09-07 12:31 | No | Warranty | Manoj Industries | St. Gorge Street, Santokpura, | Jalandhar | 144004 | Punjab | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Ram Ashish Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the MCCB found Hendle found fitment issue and now working is properly. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-07 17:26 |  |  | 155 | INR | 155 | ENM POWER PRODUCTS
WO-11224493 | 103847714 | 2023-09-07 20:19 | 2023-09-08 |  | 2023-09-07 12:09 | LC1E120N5 | LC1E120N5 | LC1E120N5 |  | Complaint Form M/s P.P,Plastic Export Promotional Industrial Park,AIDC Complex,North Guwahati,Amingaon-781031,ASSAM MR.THAKURIA 9101576163 SCHNEIDER CONTACTOR 120AMP 440VAC (LC1E120N5) CONTRACTOR BURNING FREQUENTLY BEC/22-23/1964 DATED:29/07/2023 | 2023-09-07 | 2023-09-13 21:55 | No | Warranty | P.P Plastic | Export Promotional Industrial Park,AIDC Complex, Amingaon null | Guwahati | 781031 | Assam | India FS ED&I CSP East Team SHIV ELECTRICALS Guwahati | Partha Basar SHIV ELECTRICALS GUWAHATI | SHIV ELECTRICALS | Replace the contactors and now it's working properly. | Repair |  | 9- Service Validated | 2023-09-13 12:29 |  |  | 27 | INR | 27 | ENM POWER PRODUCTS
WO-11225081 | 103856576 | 2023-09-08 16:32 | 2023-09-07 | NA | 2023-09-07 16:01 | NX200TPNDI | NX200TPNDI | NX200TPNDI |  | SFU HANDLE NOT WORKING PROPERLY NX200TPNDI | 2023-09-07 | 2023-09-10 09:56 | No | Warranty | Lodha Group | LODHA UPPER THANE SERENO C1 WING null | Thane | 421302 | Maharashtra | India FS ED&I CSP West Team East India Power Engineers Mumbai | Sandeep Ingavale East India Power engineers Mumbai | East India Power Engineers (5043) | Visited the site and checked the SFU with rotary handle not working properly. Checked the SFU open the door and use the rotary handle working ok. There is the SFU door problem it not properly aalaye to the SFU roat need to the panel door properly aalaye to the SFU. | Repair |  | 8- Service Completed | 2023-09-10 10:16 |  |  | 15 | INR | 15 | ENM POWER PRODUCTS
WO-11225094 | 103857669 | 2023-09-07 17:28 | 2023-09-07 | site is closed. | 2023-09-07 16:09 | COMX510MG | COMX510MG | COMX510MG | Com X | FW: VIP 4. VIP Country Targeted: Complaint/Request CR-4809368 Reliance- need WO and Case ID Dear Team, Reliance EAA - we are facing communication issue and we need a WO for the FSR visit. Kindly do the needful. We will revert soon with the invoice copy too. 1. Customer Name : Reliance Industries Limited( Jio World Centre BKC) 2. Site location : Reliance Industries Limited Jio World Centre, G BLOCK ,BANDRA KURLA COMPLEX, BANDRA EAST.MUMBAI-400051,MAHARASHTRA INDIA 3. System Supply : Ecostruxure asset advisor system- ED 4. Issue/Problem facing : communication issue since April , ComX 5. Products : Com X 6. Product Model/serial number : -- 7. Subscription : 40130112 8. the customer name, : Jagadish kumar rana 9. mobile no and : 7490011907 10. EMAIL ID : Jagdishkumar1.Rana@ril.com Best Regards Bindu V Thomas Connected Services Hub - EAA ED Services Business Schneider Electric Mobile+91-9980549982 Teams bindu.Thomas@se.com Email bindu.thomas@se.com Bearys Global Research Triangle Sy.no 63/3B, Gorvigere Village Hobli Whitefield Hoskote Road Bangalore - 560115. - India | 2023-09-07 | 2023-09-15 12:00 | No | Warranty | Reliance Jio World Centre | JIO WORLD CENTRE, DAICEC, RG7, G Block, BKC | Mumbai | 400051 | Maharashtra | India FS ED&I CSP West Team Alliance Controls Pvt Ltd Pune | Shmabhu Bone_Alliance Controls Pvt. Ltd | Alliance Controls Pvt. Ltd. (7966) | (1)First Connected Ebx510 with laptop through it's web page and in the webpage found that the connect window gets in Red condition in schneider electric services. That means the DSP server is unreachable. (2) Also checked with manual publication and result found failed. Checked robusted router communication through the LAN it's working fine. (3) After that we have replaced the SIM card from my mobile for testing purpose after replacing the SIM card, we have checked again connect window in Schneider electric services. Found it in green condition and manual publication has been done successfully. (4) Problem found with the SIM card, EBX510 product is working OK site is closed. | Repair |  | 9- Service Validated | 2023-09-15 17:45 | =S= Consig Fill up 226042336 |  | 147 | INR | 147 | ENM POWER PRODUCTS
WO-11225200 | 103860000 | 2023-09-07 20:14 | 2023-09-08 |  | 2023-09-07 16:53 | NA00634V | NA00634V | NA00634V |  | RE: T-Helper Kit for ATS Voltage-Range configuration Dear Team, Kindly arrange new case & WO for bellow sites, Under Assessment-Inspection catagory WO-11174037 Rancy Developres, Guwahati. Regards, _____________________________________________________________________________________ Goutam Dutta | 2023-09-07 | 2023-09-09 19:30 | No | Warranty | Rancy Developres | Rianshi World First Floor Sundarpur Main Road Zoo Rd near PNB Bank | Guwahati | 781005 | Assam | India FS ED&I CSP East Team SHIV ELECTRICALS Guwahati | Parwez Alam SHIV ELECTRICALS GUWAHATI | SHIV ELECTRICALS | Adjust the voltage of ATS and it's working satisfactorily. | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-10 19:34 |  |  | 16 | INR | 16 | ENM POWER PRODUCTS
WO-11225214 | 103860256 | 2023-09-07 20:11 | 2023-09-08 |  | 2023-09-07 17:01 | NA01004V | NA01004V | NA01004V |  | RE: T-Helper Kit for ATS Voltage-Range configuration Dear Team, Kindly arrange new case & WO for bellow sites, Under Assessment-Inspection catagory 2) WO-11163256 PROTECH GREEN, Guwahati. Regards, _____________________________________________________________________________________ Goutam Dutta ¦ Schneider Electric India Pvt Ltd ¦ Field Services - CS ¦ Mobile: +91 9903251104 ¦ Email: g | 2023-09-07 | 2023-09-09 00:30 | No | Warranty | PROTECH GREEN | NAMGHAR PATH,PANJABARI ROAD, | Guwahati | 781023 | Assam | India FS ED&I CSP East Team SHIV ELECTRICALS Guwahati | Parwez Alam SHIV ELECTRICALS GUWAHATI | SHIV ELECTRICALS | Adjust the voltage of ATS and now it's working satisfactorily. | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-10 19:39 |  |  | 25 | INR | 25 | ENM POWER PRODUCTS
WO-11225297 | 103861071 | 2023-09-09 13:43 | 2023-09-07 |  | 2023-09-07 17:32 | MEHVCSDY200A44PB | MEHVCSDY200A44PB | MEHVCSDY200A44PB |  | Complaint Pls.note that the following product are faulty and not working properly. 1. Gv2me08 Sr.no. TH1736 Phase missing 2. Cap 20kvar Sr.no. ME L19633167 modelno. MEHVCSDY200A44PB two pc So,please take necessary action to resolve this issue. We enclosed copy of bill. For Singhautomation GULLARPUR ROAD NISSING District Karnal HARYANA Ph. 7988646137 Following attachments are linked to this email: 1.Accounting Voucher-1.pdf | 2023-09-07 | 2023-09-09 16:58 | No | Warranty | Singh automation | Gularpur road Nissing distt. Karnal hr | Karnal | 132024 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | checked the capacitor found lekage issue. and mpcb found phase missing. Hence faulty, but out of warranty from serial number. Hence no replacement given to customer | Repair |  | 9- Service Validated | 2023-09-09 17:02 |  |  | 140 | INR | 140 | ENM POWER PRODUCTS
WO-11225351 | 103862251 | 2023-09-07 21:26 | 2023-09-07 |  | 2023-09-07 17:53 | 51213 | 51213 | 51213 |  | Complaint asgainst APFC RELAY We have supplied 51213 - 12 Stage APFC Relay--1 no to below customer.Invoice dated 22-Nov-2022.Complaint type there is a malfunction in the relay for details please contact Mr.Prasad sir--91 94400 84889. CUSTOMER ADDRESS:- AARAJAVARAM TECHFAB PVT LTD PLOT NO -27,SY.NO.163,CHANDANVELLY MANCHANPALLY(V) HYTHABAD,BESIDE AMAZON DATA CENTER RANGA REDDY DIST,501501 NOTE:-PICTURES FOR YOUR REFERENCE | 2023-09-07 | 2023-09-12 12:00 | No | Warranty | AARAJAVARAM TECHFAB PVT LTD | PLOT NO -27,SY.NO.163,CHANDANVELLY MANCHANPALLY(V) HYTHABAD,BESIDE AMAZON DATA CENTER | Rangareddy | 501501 | Telangana | India FS ED&I CSP South Team Sumanth Electrical Services Hyderabad | Venkata Prasad_SUMANTH ELECTRICAL SERVICES HYDERABAD | Sumanth Electrical Services | Visited Site and inspected schneider electric Varlogic RT12 Controller 51213 in our observation we found some Control Wiring Issues and CT Mounting issues so we have educated Panel Builder to whare to be mounted CT on Panel Busbars and Out Going side and we have suspected problem in Varlogic RT12 51213 But same Varlogic We Have Made Program as per site condition we have informed same to panel builder and end customer so as per schneider electric standards it is working in good condition and work order is closed and RT 12 51213 is with CSP ASC As a Good Stock | Repair |  | 9- Service Validated | 2023-09-12 13:29 |  |  | 65 | INR | 65 | ENM POWER PRODUCTS
WO-11229122 | 103879682 | 2023-09-08 11:37 | 2023-09-08 |  | 2023-09-08 10:55 | C16S4 | C16S4 | C16S4 |  | NC MATERIAL Switchgear and Control Technics Private Limited "Plot No. 152, Bommasandra Industrial Area,Hosur Road, Anekal Taluk,Bengaluru-560 099" Karnataka LAVANTHESH 7760129042 CS16S4 Schneider Electric MCCB not turning on(tripping mechanism broken) LAVANTHESH/7760129042 | 2023-09-08 | 2023-09-09 15:00 | No | Warranty | Switchgear and Control Technics Pvt.Ltd. | 152, Bommasandra Ind Area, Hosur Road, Anekal Taluk, | Bangalore | 560099 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | C Gunasekaran_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported mccb basic frame the problem found was mccb not getting ON, due to main mechanism's external trip lever got broken. We repaired it from our stock and checked found working ok. The same explained to the customer. | Repair |  | 9- Service Validated | 2023-09-09 22:30 |  |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11229325 | 103881810 | 2023-09-08 12:58 | 2023-09-08 |  | 2023-09-08 12:33 | NW10H14PML5EWHH | NW10H14PML5EWHH | NW10H14PML5EWHH | 10223540694 | NTT _DC3_ 2F Electrical Room - A, B & C UOP panel out put, bus coupler and wrapper round breaker's micrologic control need to be disabled. Please refer approval in trail mail and create WO under assessment category. Product : NW10H14P, SL :10223540694, Issue : Micrologic Nuisance Tripping. Customer : NTT DC3 Bangalore Address: Konadasapura, Bengaluru, Karnataka 560067 Mr.Ramesh , 9019022265 Regards, P.BALAKUMAR, Field Service Team, Schneider Electric , PH: 7428380635, Bangalore. | 2023-09-08 | 2023-09-08 15:25 | No | Warranty | NTT GLOBAL DC & CI INDIA P LTD | Survey No 146,WHITEFEILD HOSKOTE ROAD KHAJISONENAHALLI VILLAGE, BIDARAHALLI HOBLI | Bangalore | 560067 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Santhosh DP_P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | As requested by NTT team & Schneider UPS Team in below feeders micrologic practices in ACB have been by passed 1)Panel :2F-UIP-A = 05 Nos, 11F2, 11F4, 10F2, 10F4, 9F3 Panel: 2F-UIP-B = 04 No's, 10F2, 10F4, 11F2, 11F4 Panel: 2F-UIP-C = 05 No's, 11F2, 11F4, 10F2, 10F4, 9F3 | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-08 15:27 |  |  | 42 | INR | 42 | ENM POWER PRODUCTS
WO-11229370 | 103881343 | 2023-09-08 14:31 | 2023-09-08 | NA | 2023-09-08 12:47 | A9N4P32D | A9N4P32D | A9N4P32D | DD-2022-W29-4-3 | Please give the complaint no Please give the complaint no. Customer - CtrlS Datacenters Ltd Address - EL 72/1/A, TTC Industrial Area, Mahape MIDC, Navi Mumbai 400701 Contact Person - Mr.Anand Contact No. - 8591552415 Equipment Details -A9N4P32D Equipment Sr. No. - DD-2022-W29-4-3 Problem Reported - MCB ON / OFFD operation Problem -- Thanks & Regards, Ghanshyam Gavade 9594884883 / 9422633908 East India Power Engineers Schneider Electric Authorized Service Partner LV MV Spares And Services (GST NO: 27AHTPG7634G1ZY) | 2023-09-08 | 2023-09-08 15:03 | No | Warranty | Ctrls Datacenters Ltd. | Plot No Gen 72/1/A, MIDC, TTC Industrial Area Mahape, | Mumbai | 400710 | Maharashtra | India FS ED&I CSP West Team East India Power Engineers Mumbai | Sandeep Ingavale East India Power engineers Mumbai | East India Power Engineers (5043) | Visited the site & checked the MCB 04 Nos MCB ON / OFF operating dolly free. Hence the 04 Nos MCB needs to be replace with a new one. | Repair |  | 8- Service Completed | 2023-09-11 17:45 | VIP FSR= No 3. FSR Request: Unavailability of the preferred FSR, need to depute Non VIP FSR(nitin dhadve). =S= Consig Fill up 226035518 |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11229579 | 103885590 | 2023-09-09 14:26 | 2023-09-08 |  | 2023-09-08 13:58 | LC1D32M7 | LC1D32M7 | LC1D32M7 |  | Invoice date : 10 August 2023 Deffected Product details: 4 mcb , 1 contactor, 1 mccb not working Contactor 3pc Mcb A9kf71320 1 pc not working Mcb a9kf71463 RCCB: A9KR12225 MCCB : EZC100N4100 Rishab 9782828397 Shop # 5, 6 Road # 9A Vishwakarma Industrial Area opp:- Auto Lite India Ltd Jaipur Rajasthan Jaipur 302039 Rajasthan India | 2023-09-08 | 2023-09-15 15:34 | No | Warranty | Goel Agencies | Shop # 5, 6 Road # 9A Vishwakarma Industrial Area opp:- Auto Lite India Ltd Jaipur Rajasthan | Jaipur | 302039 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Sunny Sharma Sharma Electric Jaipur | Sharma Electric Works | Checked the mcb found dolly free and contactor found screw free, Hence faulty replaced. A9N4P63C - 1 nos A9N3P20C - 1 nos LC1D32M7 - 3 nos Email : | Repair |  | 9- Service Validated | 2023-09-15 15:36 |  |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11229818 | 103886419 | 2023-09-09 10:42 | 2023-09-08 |  | 2023-09-08 15:28 | DM3110 | DM3110 | DM3110 | 54231130426 | P margin-top:0;margin-bottom:0; Dear sir , Please log the complaint Item model - 3002385 (DM3110) Serial no. - 54231130426 Problem - Display Dead Purchase date; 16/08/2023 Costumer name - The Leprosy mission hospital - Address: Faizabad highway Barabanki Uttar Pradesh Pin code - 225001 Contact person - Mr. Dilip Contact no. - +91 88535 56522 Regards Dalip Burman Dy. Superintendent (Admin) The Leprosy Mission Hospital BarabankiUttar Pradesh 225001, India 8853556522 / 7985606425 This email and any attachments to it may be confidential and are intended solely for the use of the individual to whom it is addressed. If you are not the intended recipient of this email, do not copy or show it to anyone. Please contact the sender if you believe you have received this email in error. | 2023-09-08 | 2023-09-09 15:23 | No | Warranty | THE LEPROSY MISSION HOSPITAL | Barabanki, Faizabad main road | Barabanki | 225204 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Aman Khare_Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found meter having display issue so we replaced. | Repair |  | 9- Service Validated | 2023-09-09 15:26 |  |  | 50 | INR | 50 | ENM POWER PRODUCTS
WO-11234182 | 103908825 | 2023-09-09 12:00 | 2023-09-09 |  | 2023-09-09 11:00 | LC1E40M7 | LC1E40M7 | LC1E40M7 |  | Product : LC1E40M7 , LAEX3M7 ---Complaint LC1E40M7 , LAEX3M7 Sr No. WH2221 , DOM : May 2022 Warranty: YES with in Warranty Problem : Coil Open / Not getting ON / Charged | 2023-09-09 | 2023-09-09 12:02 | No | Warranty | ESS A Electric Store | Payeen Chowk New Airport Road, | Srinagar | 190001 | Jammu and Kashmir | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Rakesh Kumar Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the contactor found not getting on due to phase missing problem. Hence faulty replaced. LC1E40M7 - 1 Nos. email : mdshabir.jk@gmail.com | Repair |  | 9- Service Validated | 2023-09-09 14:07 |  |  | 650 | INR | 650 | ENM POWER PRODUCTS
WO-11211286 |  | 2023-09-04 16:22 | 2023-09-04 |  | 2023-09-04 15:20 | TDAV1321AN002 | TDAV1321AN002 | TDAV1321AN002 | C21852000369 | PM | 2023-09-04 | 2023-09-06 13:26 | No | Contract | KPMG | Tower C, DLF Cyber City, Ph-II ,Tower C, DLF Cyber City, Ph-II | Gurgaon | 122001 | Haryana | India FS North1 Cooling CSP Smart Engineering Services Delhi | Taranjeet Singh_Smart Engineering Services Delhi | Smart Engineering Services | SHUTDOWN ACTIVITY | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-06 13:29 |  |  | 33 | INR | 33 | ENM SECURE POWER
WO-11234279 | 103908793 | 2023-09-10 19:21 | 2023-09-09 |  | 2023-09-09 12:28 | NA01004V | NA01004V | NA01004V |  | Dear Team Please register the attached complain. ?Site / Company name: Protech Site complete address with Pin Code Protech Planners, 604 Protech Center, GS Road, Guwhaati - 781005 Name of contact person: Sukanta Debnath Contact Phone / Mob. No: 9859939237 Product Part reference NA01004V - 7 Nos Nature of Problem/ Support required Change over not taking place Serial No. of Product PURCHASE INVOICE DETAILS (Invoice no., Date, Supplier name .. If possible, submit Scan Copy of Invoice) Attached. Invoice Date 24 July 2023 Invoice Number : GE/2324/B/1369 Goutam: As discussed kindly co ordinate to done it on 11th September, Regards -------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------- Debmalya Dutta ¦ National sales ¦ India ¦ Mobile: +91 9831476041 ,Site: www.schneider-electric.com ¦ Address: Roodraksha Mall, 7th Floor, Co Working Studio, Bhangagarh, GS Road, Guwahati ? 781005, Assam ----------------------------------------------------------------------------------------------------------------------------------- ?Please note, any mails I may send outside of your standard working hours do not require an immediate reply? Internal Internal | 2023-09-09 | 2023-09-11 22:30 | No | Warranty | Protech | Protech Planners, 604 Protech Center, GS Road, null | Guwhaati | 781005 | Assam | India FS ED&I CSP East Team SHIV ELECTRICALS Guwahati | Partha Basar SHIV ELECTRICALS GUWAHATI | SHIV ELECTRICALS | Adjust the voltage and now its working properly | Repair |  | 9- Service Validated | 2023-09-11 20:46 |  |  | 25 | INR | 25 | ENM POWER PRODUCTS
WO-11211288 |  | 2023-09-04 16:24 | 2023-09-04 |  | 2023-09-04 15:20 | TDAV1321AN002 | TDAV1321AN002 | TDAV1321AN002 | C21852000370 | PM | 2023-09-04 | 2023-09-06 13:30 | No | Contract | KPMG | Tower C, DLF Cyber City, Ph-II ,Tower C, DLF Cyber City, Ph-II | Gurgaon | 122001 | Haryana | India FS North1 Cooling CSP Smart Engineering Services Delhi | Taranjeet Singh_Smart Engineering Services Delhi | Smart Engineering Services | SHUTDOWN ACTIVITY | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-06 13:34 |  |  | 33 | INR | 33 | ENM SECURE POWER
WO-11025273 | 102742971 | 2023-07-24 13:03 | 2023-07-24 |  | 2023-07-24 12:44 | APC Easy UPS Online 5000VA Indian Outlet Rackmount 230V India | SRV5KL-IN | SRV5KL-IN | 9S2020A53193 | DOP: 10 June 2023 P: Installation S: Installation Note: Site ready Dealer Call 9778810810 Priyadharshini Enterprises | 2023-07-24 | 2023-09-08 10:20 | No | Commercial Action - Sales | Biju Patnaik Indoor Stadium | Khariar Main Road null | Nuapada | 766104 | Odisha | India FS East HBN CSP Micronix Services Sambalpur | GOBARDHAN SARAF_Micronix Services Sambalpur | Micronix Services - Sambalpur - Kolkata | ups and battery installation done and ups tested ok | Commissioning & Installation | Start-up | 10- Closed | 2023-09-08 13:09 |  |  | 200 | INR | 200 | ENM SECURE POWER
WO-11234426 | 103910139 | 2023-09-11 17:33 | 2023-09-09 |  | 2023-09-09 17:13 | CAE40M5 | CAE40M5 | CAE40M5 |  | Dear Sir, Reference attached Purchase Inv. Item Sr. no.-2 Aux. Contactor CAE40M5 ,Coupling Screw fail you are requested please arrange for replacement for the same. ?? Regards pradeep kumar pal M: +91 7048972716 Kandi Electrical Solutions Pvt. Ltd. Office & Works: Khasra No 981/330, Block No - 03, Basai Village, Near Basai Flyover, Basai Road, Gurugram-122006-Haryana (INDIA) Regd Off: Pocket G4/23-24, FF, Sector-11, Rohini, Delhi-110085(INDIA) GST NO: 06AAFCK1048L1ZI, PAN NO: AAFCK1048L, CIN NO: U31900DL2013PTC249820 Deals in : · LV & MV switchboards, C&R Panels, Bus Ducts (NSBD, SPBD & Bus Trunking) · EPC Turnkey Solutions (Internal & External Electrification, Substation Equipments) Visit our website: http://www.kandi-electrical.com/ | 2023-09-09 | 2023-09-18 14:16 | No | Warranty | Kandi Electrical Solutions PVT. Ltd. | Khasra No. 981/330 , Block -3 Basai Industrial area village Basai Near Basai Flyover Basai . . | Gurgaon | 122006 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the auxilary contactor found not working , Hence faulty replaced. CAE40M5 - 1 nos Email : id not provided by customer | Repair |  | 8- Service Completed | 2023-09-19 14:19 | 226047924 zfre booked. |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11211287 |  | 2023-09-04 16:26 | 2023-09-04 |  | 2023-09-04 15:20 | TDAV1321AN002 | TDAV1321AN002 | TDAV1321AN002 | C21852000368 | PM | 2023-09-04 | 2023-09-06 13:35 | No | Contract | KPMG | Tower C, DLF Cyber City, Ph-II ,Tower C, DLF Cyber City, Ph-II | Gurgaon | 122001 | Haryana | India FS North1 Cooling CSP Smart Engineering Services Delhi | Taranjeet Singh_Smart Engineering Services Delhi | Smart Engineering Services | SHUTDOWN ACTIVITY | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-06 13:37 |  |  | 33 | INR | 33 | ENM SECURE POWER
WO-11211289 |  | 2023-09-04 16:31 | 2023-09-04 |  | 2023-09-04 15:20 | TDAV1321AN002 | TDAV1321AN002 | TDAV1321AN002 | C21852000371 | PM | 2023-09-04 | 2023-09-06 13:23 | No | Contract | KPMG | Tower C, DLF Cyber City, Ph-II ,Tower C, DLF Cyber City, Ph-II | Gurgaon | 122001 | Haryana | India FS North1 Cooling CSP Smart Engineering Services Delhi | Taranjeet Singh_Smart Engineering Services Delhi | Smart Engineering Services | SHUTDOWN ACTIVITY | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-06 13:26 |  |  | 33 | INR | 33 | ENM SECURE POWER
WO-11239942 | 103798459 | 2023-09-14 13:54 | 2023-09-11 |  | 2023-09-11 09:17 |  |  |  |  | COMPLAINT FOR TRANSIT DAMAGE PRODUCTS Inv --9008684942 Line No : 20/1 LDF36600U33XAAUOMO 12pcs--- 1Pc Received invisible damage(BROKEN) Line No : 40/3 LDF36400U33XAABDUN 33pcs--2Pcs Received invisible damage(BROKEN) Line No : 50/4 LDF36400U33XAAUNMD 10 pcs --4pcs Received invisible damage(BROKEN) DOCKET NO: 4207909 | 2023-09-11 | 2023-09-14 13:56 | No | Warranty | Durga Bhai & Co. | Khasra No 474, 25 Foota Road,LALDORA OF VILLAGE,AJIT VIHAR,BURARI | Delhi | 110006 | Delhi | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | 1 ) Visited the site and checked and found Mccb LDF36400U33XAAUNMD - 3 nos and LDF36400U33XAABDUN- 1 nos . Serial No. : 10-2023-W20-1 found base damaged . 2 ) Packing box found ok. Detail : 1. Invoice no.: AA3330121858 2. Invoice Dt. 22/8/2023 3. O.A no.: 300750535 4. P.O date : 5/3/2023 5. P.O no.: PO-DBC-230302 6. Transport - Premier Road Carriers Ltd. 7.Vehicle No. : HR38W1816 8.Receiving Date : 26/8/2023 | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-14 13:59 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11241801 | 103920729 | 2023-09-12 15:44 | 2023-09-11 |  | 2023-09-11 15:09 | METSEEM1220HCL1 | METSEEM1220HCL1 | METSEEM1220HCL1 |  | FW: 01 No. Schneider makes energy meter EM1000H LCD 01 screw not working (free) METSEEM1220HCL1 DOM: 140723 EM1000H LCD 01 screw not working (free) at current inputs side | 2023-09-11 | 2023-09-16 16:36 | No | Warranty | Neeraj Sharma | Plot No.1A, Sector-8C, Integrated Industrial Estate, Ranipur- | Haridwar | 249403 | Uttarakhand | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the meter found display not showing. Hence faulty , replaced. METSEEM1220HCL1 - 1 Nos. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-16 16:37 |  |  | 210 | INR | 210 | ENM POWER PRODUCTS
WO-11241924 | 103928523 | 2023-09-13 12:27 | 2023-09-11 |  | 2023-09-11 16:11 | GCR_MVS | GCR_MVS | GCR_MVS |  | Complaint - 4000A 4 Pole ACB 1 Company Name & Complete Address with pin code - Where product is installed "Delta Roto Tech Pvt Ltd New No.3/152-1/ Old No.3A/330 Near Nagar Putrukan Sairam Nagar, Sankari Main Road Nethimedu, Salem-636002 " 2 Contact Person at Site : Name & Mobile No. Delta Roto Tech Pvt Ltd unit-2,7305022031 Alternate Mobile No : 7305022035 3 Contact Person at Site - Email Address** drtstore1@gmail.com 4 Defective Product Model/Part No (Pls refer FAQ sheet ) MVS40N4EW6A 5 Nature of Defect* - Defects Video and Photographs Hardware issue 6 Shutdown availability if applicable yes 7 POP - SE Authorised Partner Invoice soft copy VPN Agencies. Inv.no.GST1750 dt.05.06.2023 8 Photograph of product where Serial No/Batch Code or Date of Manufacturing printed - Please refer FAQ sheet 9 Name & phone No: of person registering the complaint Delta Roto Tech Pvt Ltd unit-2,7305022031 | 2023-09-11 | 2023-09-15 12:51 | No | Warranty | Delta Roto Tech Private Limited | SALEM : 3A/330, Near Nagarputrukan, Sairam Nagar, Sankari Main Road, Nethimedu, | salem | 636002 | Tamil Nadu | India FS ED&I CSP South Team Power Pro Engineering Services Coimbatore | KV ARUNKUMAR_POWER PRO ENGINEERIG SERVICES COIMBATORE | Powerpro Engineering Services | WE HAVE VISITED THE SITE AND INSPECTED WE FOUND ACB CHASSIS SIDE PLATE ISSUE WE HAVE RECTIFIED THE SAME TESTED AND FOUND OK TESTED RACK IN / OUT FOUND OK AND INFORMED TO CUSTOMER | Repair |  | 9- Service Validated | 2023-09-15 12:54 |  |  | 190 | INR | 190 | ENM POWER PRODUCTS
WO-11247897 | 103963780 | 2023-09-14 14:32 | 2023-09-12 |  | 2023-09-12 16:24 |  |  |  |  | Re: Received Damaged Boxes- 9008705112, 9008705111 We have found some boxes in damaged conditions against 2 invoices 9008705112 & 9008705111. The boxes are not in a good and proper condition. Continually we are receiving material in Such condition and no action taken by Gati as well as Schneider. Rexel India Pvt. Ltd. Mob:8956367478----Himanshu Ground Floor, Plot no. 20, Udyog Vihar Phase-VII, Sector-35, Begampur Khatola, Haryana, 122001 | 2023-09-12 | 2023-09-14 17:24 | No | Warranty | Rexel India Private Limited | Ground Floor, Plot No 20, Udyog Vihar Phase - VII, sector- 35, Begampura Khatola | Gurgaon | 122001 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | 1.Visited the site and checked the Product : LVR07X00A44CU Serial Number : N3340063C,N3340062C ,N3450466C , N3450467C, found that boxes damage outside and terminal bended of reactor as per customer. 2. Boxes received damaged condition. Serial Number- N3340063C- three terminal bend Serial Number - N3340062C - one terminal bend Serial Number - N3450466C - one terminal bend Serial Number - N3450467C - two terminal bend courrier detail not given by customer. | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-14 17:25 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11248017 | 103965707 | 2023-09-12 17:36 | 2023-09-12 |  | 2023-09-12 16:56 | GCR_NW_CB | GCR_NW_CB | GCR_NW_CB | 10223630 | FW: WO-11130570 from Schneider Electric ¦ Good will Hi Abhijit, Please make WO under good will as per below approval. Sudhir Power Ltd. Plot No.1 ¦E.H.T.P.¦Sector 34 ¦Gurgaon-122001 ¦Haryana¦ India Birendra Shukla? DGM (Service) Mob.: +91-9599294801 NW32H14PEDO6.0A S. No. : 10223630 Chassis mechanism is not working. Regards, Brahm Prakash Pandey | 2023-09-12 | 2023-09-12 17:39 | No | Warranty | Sudhir Power Ltd. | Plot No.1 ¦E.H.T.P.¦Sector 34 ¦Gurgaon-122001 ¦Haryana¦ India | Gurgaon | 122001 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | chasis booked and replace. | Repair |  | 9- Service Validated | 2023-09-12 17:45 |  |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11248078 | 103965556 | 2023-09-13 10:39 | 2023-09-12 |  | 2023-09-12 17:22 | METSEEM6400NGRSCL1 | METSEEM6400NGRSCL1 | METSEEM6400NGRSCL1 | 44780 | Fwd: Case : 103788493 dt. 5.9.23 MANKIND PHARMA SP-1/3, RIICO, Industrial Area, Kaladwas Udaipur Mr Satender Singh 9268682112 Product :- METSEEM6400NGRSCL1 DOM:- 07-08-2022 Meter is not showing the accurate values, Ampere value in meter display and Ct secondary is different. | 2023-09-12 | 2023-09-13 10:44 | No | Warranty | MANDKIND PHARMA | SP-1/3, RIICO, Industrial Area, Kaladawas | Udaipur | 313003 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | Checked the meter found working ok. Email : id not provided by customer . | Repair |  | 9- Service Validated | 2023-09-15 17:04 |  |  | 395 | INR | 395 | ENM POWER PRODUCTS
WO-11249170 | 103824516 | 2023-09-19 10:34 | 2023-09-12 |  | 2023-09-12 20:26 |  |  |  |  | RMA 103824516_RO 61367621 | 2023-09-12 | 2023-09-21 10:54 | No | Warranty | Deltoncontrol & Switchgears LLP | 3-43A, 1st Main Road, Off, Mysore Rd, near Karnataka Bank, New Timberyard Layout, | Bangalore | 560026 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Nagaraja G_P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | As per RMA complaint customer sent the below mentioned materials. we have checked, meter 1) Ref:METSEPM1130HCL05 RD S/N:540470026092 [DDM 281222] = 1 No meter. We have tested the meter ON/OFF working found ok. 2) Ref: LC1D09FD S/N: 1023242 = 1 No contactor not holding properly. Because of contractor inside coil was open circuit issue. Hence we will give the same new contactor warranty replacement ASAP. | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-21 10:54 |  |  | 8 | INR | 8 | ENM POWER PRODUCTS
WO-11249219 | 103847246 | 2023-09-13 12:32 | 2023-09-12 |  | 2023-09-12 20:44 |  |  |  |  | RMA 103847246_RO 61365877 | 2023-09-12 | 2023-09-21 16:14 | No | Warranty | VPN Agenciies - 500017482 | 5, Ground Floor 1, Midland Complex | Salem | 636009 | Tamil Nadu | India FS ED&I CSP South Team Power Pro Engineering Services Coimbatore | KV ARUNKUMAR_POWER PRO ENGINEERIG SERVICES COIMBATORE | Powerpro Engineering Services | WE HAVE INSPECTED THE REPORTED CONTACTOR WW FOUND CONTACTOR CHATTERING ISSUE WE HAVE RECTFIED THE SAME TESTED AND FOUND OK TESTED ELECTRICALLY FOUND WORKING OK | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-21 16:16 |  |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11249473 | 103895365 | 2023-09-13 09:49 | 2023-09-12 |  | 2023-09-12 21:56 |  |  |  |  | RMA 103895365_RO 61369376 | 2023-09-12 | 2023-09-18 12:00 | No | Warranty | Perfect Enterprises(500004439) | 4, Maharaja Chambers, Verai pada Pole, Khadia Char rasta | Ahmedabad | 380001 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Mistri Anik Engineering Ahmedabad | Anik Engineering (554) | All material booked as per reprot and attached invoices. =S= Free Order 226060769 has been saved | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-18 13:50 | =S= Free Order 226060769 has been saved =S= Free Order 226064273 has been saved |  | 10 | INR | 10 | ENM POWER PRODUCTS
WO-11252993 | 103991398 | 2023-09-14 11:41 | 2023-09-13 |  | 2023-09-13 11:45 | GCR_NW_CB | GCR_NW_CB | GCR_NW_CB | 10221230052 | Problem in ACB Make: Schneider ACB got stuck during auto power changeover and cannot operate manually during that time. 1) Model NO: NW40H14PED06.OE GCR_NW_CB 2) SR. NO.: 10221230052 | 2023-09-13 | 2023-09-14 13:32 | No | Warranty | Eva Grow Medicaps Private Limited | WRX5+QQX, Near Auro Bindo school, Opp union bank Sai road Gullarwala, | Baddi | 173205 | Himachal Pradesh | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Vinod Kumar_Sharma Electric Chandigarh | Sharma Electric works(1003) | shut down not provided by the customer for checking ACB. Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-14 13:37 |  |  | 55 | INR | 55 | ENM POWER PRODUCTS
WO-11253954 | 104003169 | 2023-09-13 18:31 | 2023-09-15 |  | 2023-09-13 17:51 | GCR_NW_CB | GCR_NW_CB | GCR_NW_CB | 1022154 | Re: WO-11130570 from Schneider Electric Main Installed Product Name : GCR_NW_CB Main IP Serial Number : 1022154 Work Order Reason:FW: Engineer require for Schneider ACB repairing work a/c of VISHAKHA GLASS PVT. LTD. As Per The serial number The Product Is In Warranty. Kindly Arrange The Site Visit. Site Address:- Vishakha Glass Pvt.Ltd. SURVEY NO 180/P IND-30A AND 30B ,ADANI PORTS AND SPECIAL ECONOMIC ZONE, MUNDRA KUTCH KACHCHH 370421 Gujarat India Contact Person Details:- Contact Detail : MR DINESH KHAIK - 9509671926 Ritesh---8826555645 | 2023-09-13 | 2023-09-15 16:55 | No | Warranty | Vishakha Glass Pvt.Ltd. | SURVEY NO 180/P IND-30A AND 30B ,ADANI PORTS AND SPECIAL ECONOMIC ZONE, MUNDRA KUTCH | KACHCHH | 370421 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | Jayesh J_JKS Rajkot | JKS Engineering Co. | We visit at site and observation check and found drawot astembly not working.proper dueto gear teeth damage.then instart new assemble and button plate check and found in the safeaty shutter in side on the custor contart nut and wa shree found this can also cause the breaken not to go in atter replace above aslembly check 4-6 time working found ok | Repair |  | 9- Service Validated | 2023-09-15 17:04 |  |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11255466 | 103968508 | 2023-09-29 11:45 | 2023-09-29 |  | 2023-09-13 22:57 |  |  |  |  | RMA 103968508_RMA 61360186 | 2023-09-13 | 2023-09-29 16:30 | No | Warranty | ENTEX PRIVATE LIMITED | New No. 661 (Old No 2 / 219) Kundrathur Road Gerugambakkam | Chennai | 600122 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | RMA Num 61360186 | Assessment/ Inspection | Data Collection | 8- Service Completed | 2023-09-29 16:39 |  |  | 20 | INR | 20 | ENM POWER PRODUCTS
WO-11256835 | 104024569 | 2023-09-14 11:16 | 2023-09-14 |  | 2023-09-14 09:50 | 30002055 | 30002055 | 30002055 | 54512241 | Complaint number required Dear Team, M/S Taj Forgin (1) Ltd. Plot no. 41 Sec. 68 Imt faridabad haryana Mr. H.S 9811268206 Product : 30002055 Serial No : 54512241 / 5 Nov. 2022 not power up -- *WITH REGARDS-* Sarabjit Singh | 2023-09-14 | 2023-09-14 12:25 | No | Warranty | Taj Forgin (1) Ltd. | Plot no. 41 Sec. 68 Imt faridabad haryana null | Faridabad | 121004 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the meter found working ok. Email : id not provided by customer . | Repair |  | 8- Service Completed | 2023-09-14 14:25 |  |  | 52 | INR | 52 | ENM POWER PRODUCTS
WO-11258859 | 104027791 | 2023-09-15 12:48 | 2023-09-14 |  | 2023-09-14 13:03 | MVS12N3MW6L | MVS12N3MW6L | MVS12N3MW6L |  | RE: Complain for faulty ACB Incomer side [ thread::43EJ4XzSe5CROBTDEGotpj4:: ] 1. Invoice copy for warranty validation : Attached 2. Complete model ref :- MVS12N3MW6L 3.Complete proper site address with end user mail id - Power House Road, Rourkela, Odissa, Mail ID :- rkl_zigma@rediffmail.com We have supplied one ACB to Zigma Tech Control, Rourkela, Orissa. But Customer is facing problem in terminal side. Some terminal screw is slipping, it is not opening. | 2023-09-14 | 2023-09-18 12:34 | No | Warranty | Zigma Tech Control | Opp. Hotel Nidhi, Power House Road, Sundargarh | Rourkela | 769001 | Odisha | India FS ED&I CSP East Team UNIVERSAL ELECTRIC POWER SOLUTION BHUBANESWAR | Banty Kumar_UNIVERSAL ELECTRIC POWER SOLUTION BHUBANESWAR | Universal Electric Power Solution(500012032) | screw replaced at site customer didn't sing the report | Repair |  | 9- Service Validated | 2023-09-18 12:34 |  |  | 356 | INR | 356 | ENM POWER PRODUCTS
WO-11258988 | 104028752 | 2023-09-14 14:24 | 2023-09-14 |  | 2023-09-14 13:59 | GV5P220H | GV5P220H | GV5P220H | PP22094 | Dear Team, Bathinda Chemical & Infrastructure Ltd. Sangat mandi,Bathinda,Punjab Mr. Gaurav Benerji 9815716522 Product : GV5P220H - (1 Nos.) Serial number:- PP22094 Phase Missing *WITH REGARDS*Sarabjit Singh*ANANYAA ELECTRICALS I PLOT NO-279, INDUSTRIAL AREA PHASE-II,CHANDIGARH-16002 I ADMIN. AUTH. SERVICE & SPARES DEALER : C&S ELECTRIC ABBINDIA LIMITED, EPCOS & SCHNEIDER ELECTRIC INDIA*E MAIL : ananyaa.ae@gmail.com, MOBILE NO - 7355622336 | 2023-09-14 | 2023-09-20 15:46 | No | Warranty | Bathinda Chemical & Infrastructure Ltd. | Sangat mandi | Bathinda | 151001 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | checked the mpcb found phase missing. Hence faulty, replaced. GV3P65 - 1 Nos. GV5P220H - 2 Nos. Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-22 15:51 |  |  | 2 | INR | 2 | ENM POWER PRODUCTS
WO-11263653 | 104055254 | 2023-09-16 16:21 | 2023-09-15 |  | 2023-09-15 10:51 | NA00634V | NA00634V | NA00634V |  | Re: Open cases - EPS - Need to Address the call on same Day...!!! Wo TAT Crossed....!!!! Switch 1 mains and Switch 2 DG #Whenever mains fail DG start automatically but change over not shift from switch 1 to switch 2, only shift to zero position. #And sometimes is reverse not shift from switch-2 to switch -1 #Sometimes it works Normally. Please send the Schneider engineer visit address as per given below. NS ADYAR Navy Office Port Complex Varuna Salai Chennai - 600 009 Contact Person - Mr Rakesh - 81308 93814. | 2023-09-15 | 2023-09-26 23:00 | No | Warranty | Navy Office Port | Navy Office Port Complex Rajajai Salai | Chennai | 600009 | Tamil Nadu | India FS ED&I CSP South Team Electro Power Systems Chennai | VIJAY KUMAR Electro Power Systems Chennai | Electric Power System | NA00634V 63 A ATS was replaced on warranty basis, checked the ATS by giving EB power supply, transferring of Ats from 0 to 1 is working due to voltage fluctuation, power indicator source1 is blinking. So we instructed customer to Reset the Ats after fluctuation was normalized. | Repair |  | 8- Service Completed | 2023-09-26 19:21 |  |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11220204 |  | 2023-09-13 13:51 | 2023-09-16 |  | 2023-09-06 10:59 | Easy UPS 3S 40 kVA 400 V 3:3 UPS for external batteries | E3SUPS40KH | E3SUPS40KH | 9E2149T11081 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-06 | 2023-09-26 19:28 | No | Contract | Fugro Survey (India) Pvt. Ltd. | Fugro House D222/30 TTC Industrial Area MIDC Nerul, Navi Mumbai, Maharashtra 400706 Near Lokmat Press MIDC Nerul | Mumbai | 400706 | Maharashtra | India FS West1 HBN CSP_Mahavir Sys Power Pvt Ltd Vashi | Sanju Chauthmol_Mahavir Sys Power Pvt Ltd Vashi | Mahavir Sys Power Pvt Ltd -Vashi | Engineer had done the PM activity of ups and checked its working fine on both mode with load | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-26 19:34 |  |  | 13 | INR | 13 | ENM SECURE POWER
WO-11264385 | 104057210 | 2023-09-15 15:59 | 2023-09-15 | As per sr. no. product in warranty raise ZVO for replacement. | 2023-09-15 12:12 | METSEEM6436HCL10RS | METSEEM6436HCL10RS | METSEEM6436HCL10RS |  | Meter Complaint the multi function meter (METSEEM6436HCL10RS EM6436 WITH RS485 CL.1) is not working ,kindly debut the service for multi energy meter Date of Purchase 25.02.2023 Surat Municipal Corporation STP, Sneh Rashmi Botanical Garden, Ugat, Bhesan Road, Jahangirabad, Surat, Gujarat -395005. Contact Person & No : Muthukannan. A 6379661775 venkat@vatechindia.com | 2023-09-15 | 2023-09-16 16:22 | No | Warranty | Surat Municipal Corporation STP | Sneh Rashmi Botanical Garden, Ugat, Bhesan Road, Jahangirabad, null | Surat | 395005 | Gujarat | India FS ED&I CSP West Team VARDHAMAN ELECTROSOFT Vadodara | MAHENDRA SINGH VARDHAMAN ELECTROSOFT Vadodara | VARDHAMAN ELECTROSOFT | we visited the site and check the meter and found that 1.NO/NC connect and freeze so its not working in operating condition. 2. phase: when i check the equipment and found that there is no pole to pole continuity in on condition . | Repair |  | 9- Service Validated | 2023-09-16 16:34 | =S= Consig Fill up 226060659 |  | 0 | INR | 0 | ENM POWER PRODUCTS
WO-11264437 | 104037698 | 2023-09-15 13:24 | 2023-09-15 |  | 2023-09-15 12:26 | LC1D09BL | LC1D09BL | LC1D09BL |  | Complaint - Ace Designers Ltd LC1D09BL - 02 NOS .. LC1D09BL 2 102306 102247 Screw Issue | 2023-09-15 | 2023-09-15 16:05 | No | Warranty | Ace Designers Ltd. | Plot No. 7 & 8, 80 Feet Road, Peenya II Phase, Peenya, | Bangalore | 560058 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | MANOJ GANESAN SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site- pooja power products and checked the customer reported contactors by giving 24vdc auxillary to A1&A2 checked the continuity, on and off working properly. There is no issue. Requested distributor to send the materials to customer place to check in the site with the load. | Repair |  | 9- Service Validated | 2023-09-15 20:58 |  |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11265249 | 104064347 | 2023-09-16 15:13 | 2023-09-15 |  | 2023-09-15 17:31 | 30003005D | 30003005D | 30003005D |  | Complaint Registration 2325-DEL-ECS DELTA ELCTRONICS INDIA PVT LTD PLOT NO 15 SEC-33 INFOCITY 2 NEAR BY HERO HONDA CHOWK GURUGRAM 122003 Chaman Ranga -9212796973 9910015705 30003005D=01, LC1DT55ED=01, A9N4P32D=01 Energy power display not on, mechnical interlok problem, Lock Free 1 YEAR ELECTRICAL CONTROL SYSTEMS,INV N0- 9008530481 dt. 20/04/23, 9008640857 dt. 12/07/23, 9008667112 dt. 03/08/23 Ashish Malik : 9910015705 | 2023-09-15 | 2023-09-16 15:25 | No | Warranty | Delta Elctronics India Pvt Ltd | Plot No 15 Sec-33 Infocity 2 Near By Hero Honda Chowk | Gurgaon | 122003 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the meter found display not showing and contactor and mcb found stucking issue , dolly free, Hence faulty replaced. 30003005D - 1 nos A9N4P32D - 1 nos LC1DT55ED - 1 nos Email : | Repair |  | 8- Service Completed | 2023-09-19 14:36 |  |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11268149 | 104076772 | 2023-09-16 11:49 | 2023-09-16 |  | 2023-09-16 10:43 | LRE22 | LRE22 | LRE22 |  | Product : LRE22 Overload relay Sr no 8C22102 DOM Mar 2022 NC Contact Permanently Open Product details are mentioned above Product : LRE22 Overload relay Sr no 8C22102 DOM Mar 2022 NC Contact Permanently Open Hitesh electricals Shop no--3 ajanta chowk bhiwadi district Alwar Rajasthan Mr. Parveen Ji 8955238725 | 2023-09-16 | 2023-09-16 14:20 | No | Warranty | Hitesh electricals | Shop no--3 ajanta chowk bhiwadi district null | Alwar | 301019 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Sunny Sharma Sharma Electric Jaipur | Sharma Electric Works | Checked the relay found nc/no point not working, Hence faulty replaced. LRE22 - 1 nos LRD06 - 1 nos Email : id not provided by customer. | Repair |  | 8- Service Completed | 2023-09-16 16:52 |  |  | 160 | INR | 160 | ENM POWER PRODUCTS
WO-11269439 | 104077170 | 2023-09-16 14:39 | 2023-09-16 | NA | 2023-09-16 14:13 | INA_10NA4PFM0E1 | INA_10NA4PFM0E1 | INA_10NA4PFM0E1 |  | Company Name & Complete Address with pin code - Where product is installed ARROW ELECTRICALS INDIA PVT. LTD Arrow House, 11A/11B, K.T. Industrial Park, Goraipada, Vasai, Dist. Palghar, Maharashtra 401208. Contact Person at Site : Name & Mobile No. Jayesh Mhatre (8237393903) Alternate Mobile No : 8237393903 Contact Person at Site - Email Address** arrowsales@arrowelectricals.in Defective Product Model/Part No (Pls refer FAQ sheet ) INA_10NA4PFM0E1 - 1 No Nature of Defect* - Defects Video and Photographs Mechanical ON operation fail. Shutdown availability if applicable POP - SE Authorised Partner Invoice soft copy INVOICE NO.9008715935 (DATE- 15 Sep 2023) Photograph of product where Serial No/Batch Code or Date of Manufacturing printed - Please refer FAQ sheet Name & phone No: of person registering the complaint Jayesh Mhatre | 2023-09-16 | 2023-09-17 20:12 | No | Warranty | Arrow Electricals India Pvt. Ltd. | Arrow House (11A/11B), K.T. Industrial Park, Goraipada,, Vasai E, Dist. Palghar | Vasai | 401208 | Maharashtra | India FS ED&I CSP West Team Kanekar Consulting Engineers Pvt Ltd Thane | Nitin Arote_Kanekar Consulting Mumbai | Kanekar Consulting Engineers Pvt. Ltd. | Internal main mechanism problem, solved the problem then check on/off ok | Repair |  | 9- Service Validated | 2023-09-17 20:13 |  |  | 27 | INR | 27 | ENM POWER PRODUCTS
WO-11269448 | 104077281 | 2023-09-16 15:09 | 2023-09-16 |  | 2023-09-16 14:18 | LRE03 | LRE03 | LRE03 |  | P margin-top:0;margin-bottom:0; Dear Sir, Compian for Relay and Auxiliary Contactor not working now, Party Name : Precimeasure Controls Pvt ltd Shed No.c1b-235/C1-239/4 GIDC POR RAMANGAMDI VADODARA-391243 MODEL : LRE03 1 NOS & CAD32FD 1 NOS. NOT WORKING NOW INVOICE NO.409 DTD.31.07.23 (LRE03) INVOICE NO.256 DTD.13.06.23 (CAD32FD) CONTACT PERSON : DAXESH BHAI PATEL MOB.NO.8469895620 SAWANT K G Office Mobile : 8141913437 WhatsApp - 9099793665 Land Line - Tel: 0265 2361025 Thanking youYours truly Industrial Marketing Inc.55-Paradise Complex,Sayajigunj,Baroda - 390020 GST NO : 24AADFI0578C1ZS Since 1989 Authorized Distributors | 2023-09-16 | 2023-09-19 11:11 | No | Warranty | PRECIMEASUE CONTROL PVT LTD | PLOT NO.SHED NO.C1B 235/4 C1 239/4 GIDC POR RAMANGAMDI | Vadodara | 391243 | Gujarat | India FS ED&I CSP West Team Jay Services Vadodara | Ghanshyam Kachiya_Jay Services Vadodara | Jay Services | We visited at site & checked that tesys control relay CAD32FD physically ok. Manually ON-OFF Operation found ok. But it is not operate due to LAD4TGDL not working. It is replace and tested ok. Replace from distributor stock. We also checked LRE03 relay found R & B phase continuity open & as per sr no. It is out side warranty sr 8C18375 2018 so return to customer. | Repair |  | 9- Service Validated | 2023-09-19 11:12 | =S= Consig Fill up 226061186 |  | 22 | INR | 22 | ENM POWER PRODUCTS
WO-11269482 | 104077468 | 2023-09-16 16:03 | 2023-09-16 |  | 2023-09-16 15:19 | METSEEM6436HCL10RS | METSEEM6436HCL10RS | METSEEM6436HCL10RS | 200223 | Fwd: Case : 103925171 dt. 13.9.23 Khurja Super Thermal Power Plant, Khurja Bulandshahar, Uttar Pradesh. Mr Jugal Ji 9958669146 Product : METSEEM6436HCL10RS Serial Number : 200223 Display issue -- *WITH REGARDS-* Sarabjit Singh | 2023-09-16 | 2023-09-18 16:49 | No | Warranty | Khurja Super Thermal Power Plant |  | Khurja | 203131 | Uttar Pradesh | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the meter found not power up, Hence faulty replaced METSEEM6436HCL10NC - 1 nos Email : id not provided by customer. | Repair |  | 8- Service Completed | 2023-09-18 16:53 |  |  | 80 | INR | 80 | ENM POWER PRODUCTS
WO-11269514 | 104077422 | 2023-09-16 18:47 | 2023-09-16 |  | 2023-09-16 16:13 | LC1E0910M7 | LC1E0910M7 | LC1E0910M7 |  | Dear sir / madam, We have purchased 09A 3P AC-3DUTY CONTACTOR (LC1E0910M7) - 1No from M/s. Maiyar Techno Systems. Wide their invoice no: 4267 dated 13.09.2023. We are facing issue with contactor does not get energized. We request you to send your service person to rectify/replace at the earliest to our Factory located in below address. Kindly do the needful at the earliest. Note:- Attached Invoice Copy & Contactor Images FYR. ?Invoice date 13 09 23 Address :- Rampo controls # 19-20, "Ram's Techno Tower" Rajagopalanagar Main Road, 7th Main, Opp: Nagalingeshwara Temple, Between Rajagopalanagar Police Station & Peenya II stage Bus stand, Bangalore-560058 phone: +91 7899411592 phone: 080 - 28360993 web: www.rampocontrols.com With Regards, B.Naveen Kumar RampoControls. +91 7899411592. 080 28360993. | 2023-09-16 | 2023-09-22 14:28 | No | Warranty | Rampo controls | # 19-20, "Ram's Techno Tower" Rajagopalanagar Main Road,7th Main, Opp: Nagalingeshwara Temple, Near Rajagopalanagar Police Station, Bangalore - | Bangalore | 560058 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | MANOJ GANESAN SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported contactor the problem found was continuity issue, so we had arranged the replacement and new material handed over to the customer. | Repair |  | 9- Service Validated | 2023-09-22 14:33 | Hi Team, Material booked zfre Zvo : 226064919 |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11071596 | 102988953 | 2023-08-03 18:16 | 2023-08-03 | NA | 2023-08-03 18:01 | GCR_NSX100_630 | GCR_NSX100_630 | GCR_NSX100_630 |  | Regarding 1 no motor mechanism faulty 400A FP at Jyotirindra Nath Nandy Metro Station ITD RVNL site of Kolkata Metro. Dear Team, Please refer the attached SFR and arrange to depute your service engineer for 1 no 400A FP MCCB Motor mechanism faulty -1nos. Limit switch is not working at Jyotirindra Nath Nandy.Metro station ITD RVNL site of Kolkata Metro. For more information please refer to the attached pictures or you can speak to Mr Abhay Kumar @ 92058 83471 Please arrange to visit site, urgently. Contact Person- Mr Abhay Kumar Contact No- 92058 83471 Site Address- Jyotirindra Nath Nandy.Metro Station, Kolkata Metro. | 2023-08-03 | 2023-09-04 14:15 | No | Warranty | Jyotirindra Nandi Metro Station | NH12 Purba Diganta Mukundapur null | Kolkata | 700099 | West Bengal | India FS ED&I CSP East Team B.D Electroservices Kolkata | RAHUL RAY_B.D Electroservices Kolkata | B.D Electroservices(500017330) | We close this complain and we will do the physically work customer confirm. | Repair |  | 9- Service Validated | 2023-09-05 18:21 |  |  | 25 | INR | 25 | ENM POWER PRODUCTS
WO-11269567 | 104077567 | 2023-09-19 08:25 | 2023-09-19 |  | 2023-09-16 17:48 | GCR_NW_CB | GCR_NW_CB | GCR_NW_CB | 102321463 | FW: CONVERSION ACCOUNT _MADURA COATS _SUPPORT SOUGHT FOR ACB Dear team With reference to the trailing mail Special Approval from MKS to visit site, available. kindly create work order against assessment / inspection category Customer Details : Madura Coats Private Limited , Papavinasam Mills , Tirunelveli Dist -627 422 . Contact person : Mr .Rahim Babu ( Elec.Engg ) Contact Number : 9677725437 Product - NW08H13PED06.0A Date code ? 102321463 Regards M Venkatesan 9962940722 | 2023-09-16 | 2023-09-20 15:06 | No | Warranty | Madura Coats Private Limited | Papavinasam Mills , null | Tirunelveli | 627422 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | George KJ_Omicon Engineering Madurai | Omicon Engineering | Inspected the Site | Assessment/ Inspection | Data Collection | 8- Service Completed | 2023-09-20 15:09 |  |  | 250 | INR | 250 | ENM POWER PRODUCTS
WO-11269596 | 104077285 | 2023-09-19 13:48 | 2023-09-16 |  | 2023-09-16 18:23 | LV510315_C | LV510315_C | LV510315_C |  | P margin-top:0;margin-bottom:0; Dear Team, Please see below defective list and arrange to replace/ repair on urgent basis. Sr. No. Item No. Item Description Manufacturer Party Ref. No. QTY Invoice no INV. DATED Supplier Reason of Defective 1038 307525 MCCB 63A FP 25KA TMD FOR CVS SCHNEIDER LV510315 1 AA2730115427 03.08.23 SCHNEIDER ELECTRIC INDIA PRIVATE LIMITED NUTRAL POLE NOT WORKING Best Regards Jonum(IQC) Asst. Manager 8077190713 Novateur Electrical & Digital Systems Pvt. Ltd. Works :- Delhi-Rohtak-Road, Decora Station Road, Behind IUP Jindal, Rohad, Jhajjar, Haryana-124501 Ce message, ainsi que tous les fichiers joints à ce message, peuvent contenir des informations sensibles et/ ou confidentielles ne devant pas être divulguées. Si vous n'êtes pas le destinataire de ce message (ou que vous recevez ce message par erreur), nous vous remercions de le notifier immédiatement à son expéditeur, et de détruire ce message. Toute copie, divulgation, modification, utilisation ou diffusion, non autorisée, directe ou indirecte, de tout ou partie de ce message, est strictement interdite. This e-mail, and any document attached hereby, may contain confidential and/or privileged information. If you are not the intended recipient (or have received this e-mail in error) please notify the sender immediately and destroy this e-mail. Any unauthorized, direct or indirect, copying, disclosure, distribution or other use of the material or parts thereof is strictly forbidden. | 2023-09-16 | 2023-09-19 13:54 | No | Warranty | Novateur Electrical & Digital Systems Pvt. Ltd | Delhi-Rohtak-Road, Decora Station Road, Behind IUP Jindal, Rohad null | Jhajjar | 124501 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Pradeep Sharma_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the Mccb found nc point not countinuity showing, Hence faulty replaced. LV510315 - 1 nos Email : | Repair |  | 8- Service Completed | 2023-09-19 16:03 |  |  | 65 | INR | 65 | ENM POWER PRODUCTS
WO-11269604 | 104076928 | 2023-09-19 07:56 | 2023-09-16 |  | 2023-09-16 18:28 | LC1D18M7 | LC1D18M7 | LC1D18M7 |  | Dear Sir, Kindly find the attachment complaint registration form. Name of Customer M/s. MUTHAIYA ENGINEERING Site Address 857/3E, RAMAR KOVIL STREET, RG PUDUR, CHINNIYAMPALAYAM, COIMBATORE - 641062 Name of contact person at site Mr. NARAYANAN Contact Phone / Mob. No: 9894016253 Customer's email I'd vpncbe@gmail.com Defective product details( Complete Product ref) LC1D18M7 - 1NO Product Make Schneider Nature of Defect NOT WORKING Shutdown availability if applicable YES Commissioned / Installed date Serial No: or DOM of the product/OA no./Invoice Details S.NO : 1023312 Name & phone No: of person registering the complaint CHITHRA N 0422 - 4379941 Thanks & Regards, REKHA M Elite Partner & System Integrator Of VPN AGENCIIES No: 5, Corporation Shopping Complex, Avinashi Road, Coimbatore ? 641 018 Phone: +91 422 4379941, 42 ¦ Fax: + 91 422 2234568 ¦ Mobile: +91 90031 47288, +91 98940 16253 Email:vpncbe@gmail.com, vpncbe5@gmail.com Website: www.vpnagenciies.com | 2023-09-16 | 2023-09-21 15:44 | No | Warranty | MUTHAIYA ENGINEERING | 857/3E, RAMAR KOVIL STREET, RG PUDUR, CHINNIYAMPALAYAM null | COIMBATORE | 641062 | Tamil Nadu | India FS ED&I CSP South Team Power Pro Engineering Services Coimbatore | KV ARUNKUMAR_POWER PRO ENGINEERIG SERVICES COIMBATORE | Powerpro Engineering Services | WE HAVE VISITED THE SITE AND INSPECTED WE FOUND CONTACTOR 3L3 -TERMINAL SCREW NOT TIGHT SCREW THERED SPOILED WE HAVE COLLECTED THE DETAILS FOR FURTHER ACTION AND ARRAGING FOR FREE REPALCEMENT FOR THIS COLLECTED THE DEFECTIVE | Repair |  | 8- Service Completed | 2023-09-21 15:46 |  |  | 21 | INR | 21 | ENM POWER PRODUCTS
WO-11275318 | 104077850 | 2023-09-20 10:48 | 2023-09-18 |  | 2023-09-18 10:33 | LVR07250A44CU | LVR07250A44CU | LVR07250A44CU |  | FW: Heavy Humming in Schneider make Detuned Copper Reactor, Site -RTM Bhawani Mandi Rajasthan, Case: 102555323 This is to inform you that, we have supplied 500 KVAR, Qty - 03 Nos APFC Panel in Sutlej Textiles and Industries Limited, Unit-Rajasthan Textile Mills, Bhawanimandi-326502 Dist. Jhalawar ( Rajasthan) on dated 29/05/2023. When we installed one APFC Panel on 10/07/23, we found that a lot of humming noise is coming out from the Detuned reactor connected to the capacitors. One 50 KVAR reactor is taking very high current and 125 Amp MCCB gets tripped . So we request you to please depute your service engineer to resolve this issue on urgent basis because Sutlej Textiles and Industries Limited is a 24x7x365 days running unit. We can't stop this for a second & power factor is also low 0.81 . Some reactor name plate pics are attached for your reference . The reactor details are mentioned below.... 1. 5 KVAR -01 , Sales Unit - LVR07050A44CU 2. 10 KVAR -01 , Sales Unit - LVR07100A44CU 3. 20 KVAR -01 , Sales Unit - LVR07200A44CU 4. 15 KVAR -01 , Sales Unit - LVR07150A44CU 5. 25 KVAR -01 , Sales Unit - LVR07250A44CU--M3867504C 6. 25 KVAR -01 , Sales Unit - LVR07250A44CU 7. 25 KVAR -01 , Sales Unit - LVR07250A44CU 8. 25 KVAR -01 , Sales Unit - LVR07250A44LO 9. 50 KVAR -01 , Sales Unit - LVR07500A44CU 10. 50 KVAR -01 , Sales Unit - LVR07500A44LO 11. 110 KVAR -01 , Sales Unit - LVR0X00A44LO | 2023-09-18 | 2023-09-25 17:30 | No | Warranty | Sutlej Textile and Industries Limited | Unit : Rajasthan Textile Mills Pachpahar Road, Bhawani Mandi | Bhawani | 326502 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | checked the reactors found coils heated and not working. Hence faulty, need replacement. LVR07050A44CU - 1 Nos. LVR07500A44CU - 1 Nos. Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-27 16:30 |  |  | 370 | INR | 370 | ENM POWER PRODUCTS
WO-11276852 | 104083287 | 2023-09-18 13:14 | 2023-09-18 |  | 2023-09-18 12:36 | GCR_MVS | GCR_MVS | GCR_MVS | 10-231360226 | Complaint No. reqd. Dear Sir, Please issue Complaint No. M/s Verka Milk Plat Site No. 1, Phase 6, Mohali Mr Rajeev 9988299413 Product : MVS20N4NW6N Sr No. 10-231360226 DOM March 2023 Problem: Not Getting ON after Fault Tripping Regards Mukesh Kumar | 2023-09-18 | 2023-09-18 13:15 | No | Warranty | Verka Milk Plant | Site No. 1, Phase 6, null | Mohali | 160055 | Punjab | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Karnail Singh Sharma Electric Chandigarh | Sharma Electric works(1003) | checked the ACB found tripping issue due to micrologic relay setting not set proper as per customer load according. Micrologic relay setting done, now ACB working properly. Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-18 15:37 |  |  | 25 | INR | 25 | ENM POWER PRODUCTS
WO-11224696 |  | 2023-09-07 14:10 | 2023-09-20 |  | 2023-09-07 13:24 | Leonardo EVDXR407CEC FanTUAV0721AUpflow With Heater & Humidifier | TUAV0721AN003 | TUAV0721AN003 | C21827000861 | PM | 2023-09-07 | 2023-09-20 10:40 | No | Contract | Indraprastha Gas Ltd | Indraprastha Gas Limited IGL Bhawan Plot No. 4, Community Centre Sector 9, R K Puram COMMUNITY CENTER, RK PURAM, SECTOR 9 | New Delhi | 100006 | Delhi | India FS North1 Cooling CSP Hitech solutions New Delhi | Ashwani Kumar_Hitech solutions New Delhi | Hitech Solutions-New Delhi-Delhi | Preventive Maintenance done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-20 10:43 |  |  | 24 | INR | 24 | ENM SECURE POWER
WO-11276890 | 104086623 | 2023-09-18 15:55 | 2023-09-18 |  | 2023-09-18 12:58 | METSEEM6433HCL10RS | METSEEM6433HCL10RS | METSEEM6433HCL10RS |  | Product : MEHVCSDY250A44 Power Capacitor Sr No.ME-M2074057 DOM May 2022 Derated , Not maintaining Power Factor Please replace the same Urgently Hotel Shalimar Main Market, Abu road, Sirohi, Rajasthan PIN 307001 Mr Sunny 8860118009 Email: sunny_rjs@rediffmail.com | 2023-09-18 | 2023-09-18 15:57 | No | Warranty | Hotel Shalimar | Main Market Abu road, | Sirohi | 307001 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | Checked the meter found reading issue after resetting now meter found working ok. checked the capacitor found derated issue and mccb found phase missing, Hence faulty replaced. MEHVCSDY250A44 - 1 nos LV563620 - 1 nos Email : id not provided by customer . | Repair |  | 8- Service Completed | 2023-09-18 17:31 |  |  | 415 | INR | 415 | ENM POWER PRODUCTS
WO-11224700 |  | 2023-09-07 14:20 | 2023-09-20 |  | 2023-09-07 13:25 | LEONARDO EVDXR22/R407CEC FANTDAV0711A (ZR108KCE-TFD)DNFLW WITH "H" VERSION ( FRA | TDAV0711AN003 | TDAV0711AN003 | C21829000105 | PM | 2023-09-07 | 2023-09-20 11:06 | No | Contract | CTBC Bank Co. Ltd | Gnd and 2 Nd Floor,Aria Tower, JW Marriott Hotel,Aerocity null | New Delhi | 110037 | Delhi | India FS North1 Cooling CSP Hitech solutions New Delhi | RAJESH YADAV_Hitech solutions New Delhi | Hitech Solutions-New Delhi-Delhi | Preventive Maintenance done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-20 11:08 |  |  | 25 | INR | 25 | ENM SECURE POWER
WO-11277178 | 104086241 | 2023-09-18 15:57 | 2023-09-18 |  | 2023-09-18 14:59 | LV431165 | LV431165 | LV431165 |  | Complaint No. Required a/c Satia Please Issue Complaint No. M/s SATIA INDUSTRIES LIMITED, MUKTSAR MALOUT ROAD, RUPANA, Sri Muktsar Sahib, Punjab. MR. PARVEEN JOSHI 9815979275 Product : C25N3MA220 ( MODEL NO:- NSX250N ) (MCCB 220A MA , 3Pole , 50KA) SR No. 10-2022-W11-5 MCCB not working ( Phase Missing ) | 2023-09-18 | 2023-09-18 15:59 | No | Warranty | SATIA INDUSTRIES LTD | SATIA INDUSTRIES LTD, MUKATSAR, PUNJAB | Muktsar | 152026 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | checked the mccb found working ok. Email id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-18 16:05 |  |  | 150 | INR | 150 | ENM POWER PRODUCTS
WO-11224697 |  | 2023-09-07 14:11 | 2023-09-20 |  | 2023-09-07 13:24 | Leonardo EVDXR407CEC FanTUAV0721AUpflow With Heater & Humidifier | TUAV0721AN003 | TUAV0721AN003 | JK2051003912 | PM | 2023-09-07 | 2023-09-20 10:56 | No | Contract | Indraprastha Gas Ltd | Indraprastha Gas Limited IGL Bhawan Plot No. 4, Community Centre Sector 9, R K Puram COMMUNITY CENTER, RK PURAM, SECTOR 9 | New Delhi | 100006 | Delhi | India FS North1 Cooling CSP Hitech solutions New Delhi | RAJESH YADAV_Hitech solutions New Delhi | Hitech Solutions-New Delhi-Delhi | Preventive Maintenance done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-20 11:01 |  |  | 24 | INR | 24 | ENM SECURE POWER
WO-11277330 | 104093317 | 2023-09-18 17:05 | 2023-09-18 |  | 2023-09-18 16:19 | METSEEM6438HCL10RS | METSEEM6438HCL10RS | METSEEM6438HCL10RS |  | Fw: Cancel and reassign new case_Case : 103819614 dt. 9.9.23_Taskus Dear Sir, Taskus Building No 404,405 4th Floor, Sector 20, Phase -III Gurugram Haryana Mr.Saddam 9650668510 Product : METSEEM6438HCL10RS Communication issue with the meter -- *WITH REGARDS-* Sarabjit Singh | 2023-09-18 | 2023-09-18 17:10 | No | Warranty | Taskus | Building No 404,405 4th Floor, Sector 20, Phase -III | Gurugram | 122016 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the meter found working ok. Email : id not provided by customer. | Repair |  | 8- Service Completed | 2023-09-18 17:13 |  |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11224698 |  | 2023-09-07 14:15 | 2023-09-14 |  | 2023-09-07 13:25 | 4LGC21000000BAA Uniflair LEONARDO DX Unit - Air Cooled - Downflow - Radial fans | TDAR1321A00003 | TDAR1321A00003 | NUCU3440 | PM | 2023-09-07 | 2023-09-14 15:34 | No | Contract | SEW Engineering (India) Pvt. Ltd. | C/o BARC West Block 7 R K Puram null | New Delhi | 110066 | Delhi | India FS North1 Cooling CSP Hitech solutions New Delhi | Arvind Kumar_Hitech solutions New Delhi | Hitech Solutions-New Delhi-Delhi | Preventive Maintenance done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-14 15:39 |  |  | 27 | INR | 27 | ENM SECURE POWER
WO-11224699 |  | 2023-09-07 14:18 | 2023-09-14 |  | 2023-09-07 13:25 | 4LGC21000000BAA Uniflair LEONARDO DX Unit - Air Cooled - Downflow - Radial fans | TDAR1321A00003 | TDAR1321A00003 | NUCU3439 | PM | 2023-09-07 | 2023-09-14 15:41 | No | Contract | SEW Engineering (India) Pvt. Ltd. | C/o BARC West Block 7 R K Puram null | New Delhi | 110066 | Delhi | India FS North1 Cooling CSP Hitech solutions New Delhi | RAJESH YADAV_Hitech solutions New Delhi | Hitech Solutions-New Delhi-Delhi | Preventive Maintenance done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-14 15:45 |  |  | 27 | INR | 27 | ENM SECURE POWER
WO-11280663 | 104115111 | 2023-09-19 15:13 | 2023-09-19 | Part Order request against WO-11280663, Case No. 102818260 validated by Mr. Pradeep Patil sir | 2023-09-19 14:28 | NW40H14PEDO6_0P | NW40H14PEDO6_0P | NW40H14PEDO6_0P |  | Warning: Email body is too large and was truncated at 32 000 characters. Information may have been lost. Dear sir/mam, Please find the mentioned below proper site address to your reference. Uflex ltd., L-1, Malanpur Industrial Area, Malanpur, Ghironghi, Bhind, M.P. PIN: 477117 Contact Name : Bhupander Negi, Satish Tiwari Contact No. 7895431558, 9617355004 Regards, MOHD TALHA ¦ GET ¦ Quality +91120-4198000 ¦ +91-9568529872 +91120-4198000 ¦ quality1@ambit.in Ambit Switchgear India Pvt. Ltd. ¦ C-50, Phase ? II, Noida, India 201305 ¦ www.ambit.in From: Bhupander Negi <bhupander.negi@uflexltd.com> Sent: 18 September 2023 17:31To: 'Ambit.Quality1' <quality1@ambit.in>Cc: quality@ambit.in; krishna.parashar@uflexltd.com; sanjay.chauhan@uflexltd.com; 'Jaidev' <jaidev.kumar@uflexltd.com>Subject: RE: ACB. which are not tripping. Case 103795445 Uflex ltd., L-1, Malanpur Industrial Area, Malanpur, Ghironghi, Bhind, M.P. PIN: 477117 Contact Name : Bhupander Negi, Satish Tiwari Contact No. 7895431558, 9617355004 From: Ambit.Quality1 [mailto:quality1@ambit.in] Sent: 18 September 2023 17:10To: 'Bhupander Negi'Cc: quality@ambit.in; krishna.parashar@uflexltd.com; sanjay.chauhan@uflexltd.com; 'Jaidev'Subject: ACB. which are not tripping. Case 103795445 Dear sir, In reference to below trailing mail, due to improper site address Schneider?s engineer unable to attend the complaint. please provide us proper site address. Regards, MOHD TALHA ¦ GET ¦ Quality +91120-4198000 ¦ +91-9568529872 +91120-4198000 ¦ quality1@ambit.in Ambit Switchgear India Pvt. Ltd. ¦ C-50, Phase ? II, Noida, India 201305 ¦ www.ambit.in From: Bhupander Negi <bhupander.negi@uflexltd.com> Sent: 16 September 2023 12:22To: 'Ambit.Quality1' <quality1@ambit.in>Cc: quality@ambit.in; krishna.parashar@uflexltd.com; sanjay.chauhan@uflexltd.com; Jaidev <jaidev.kumar@uflexltd.com>Subject: RE: ACB. which are not tripping. Case 103795445 Please share the update, we are still waiting. From: Ambit.Quality1 [mailto:quality1@ambit.in] Sent: 11 September 2023 16:59To: customercare.in@schneider-electric.com; 'Schneider electric customer care'Cc: quality@ambit.in; krishna.parashar@uflexltd.com; sanjay.chauhan@uflexltd.com; 'Bhupander Negi'Subject: ACB. which are not tripping. Case 103795445 Reminder?1 Dear sir, As per trailing mail, still no action being taken from your side to close this complaint. I request to you please depute your engineer at our site to resolve the issue on immediate basis. Regards, MOHD TALHA ¦ GET ¦ Quality +91120-4198000 ¦ +91-9568529872 +91120-4198000 ¦ quality1@ambit.in Ambit Switchgear India Pvt. Ltd. ¦ C-50, Phase ? II, Noida, India 201305 ¦ www.ambit.in From: Ambit.Quality1 <quality1@ambit.in> Sent: 08 September 2023 12:26To: 'customercare.in@schneider-electric.com' <customercare.in@schneider-electric.com>; 'Schneider electric customer care' <customercare.in@se.com>Cc: 'quality@ambit.in' <quality@ambit.in>; 'krishna.parashar@uflexltd.com' <krishna.parashar@uflexltd.com>; 'sanjay.chauhan@uflexltd.com' <sanjay.chauhan@uflexltd.com>; 'Bhupander Negi' <bhupander.negi@uflexltd.com>Subject: ACB. which are not tripping. Case 103795445 Reminder?1 Dear sir, As per trailing mail, still not resolve the problem. I request to you please depute your engineer at our site to resolve the issue on immediate basis. Regards, MOHD TALHA ¦ GET ¦ Quality +91120-4198000 ¦ +91-9568529872 +91120-4198000 ¦ quality1@ambit.in Ambit Switchgear India Pvt. Ltd. ¦ C-50, Phase ? II, Noida, India 201305 ¦ www.ambit.in From: Ambit.Quality1 <quality1@ambit.in> Sent: 06 September 2023 12:45To: 'customercare.in@schneider-electric.com' <customercare.in@schneider-electric.com>; 'Schneider electric customer care' <customercare.in@se.com>Cc: 'quality@ambit.in' <quality@ambit.in>; 'krishna.parashar@uflexltd.com' <krishna.parashar@uflexltd.com>; 'sanjay.chauhan@uflexltd.com' <sanjay.chauhan@uflexltd.com>; 'Bhupander Negi' <bhupander.negi@uflexltd.com>Subject: ACB. which are not tripping. Dear sir, In reference to below trailing mail, still have not received complaint number. Please log the complaint on a high priority basis. Regards, MOHD TALHA ¦ GET ¦ Quality +91120-4198000 ¦ +91-9568529872 +91120-4198000 ¦ quality1@ambit.in Ambit Switchgear India Pvt. Ltd. ¦ C-50, Phase ? II, Noida, India 201305 ¦ www.ambit.in From: Ambit.Quality1 <quality1@ambit.in> Sent: 05 September 2023 17:29To: 'customercare.in@schneider-electric.com' <customercare.in@schneider-electric.com>; 'Schneider electric customer care' <customercare.in@se.com>Cc: 'quality@ambit.in' <quality@ambit.in>; 'krishna.parashar@uflexltd.com' <krishna.parashar@uflexltd.com>; 'sanjay.chauhan@uflexltd.com' <sanjay.chauhan@uflexltd.com>; 'Bhupander Negi' <bhupander.negi@uflexltd.com>Subject: ACB. which are not tripping. Dear sir, I would like to inform you that our end client is facing problem in 2 no. ACB. which are not tripping. So I request you to please depute your engineer at our site to resolve the issue on a urgent basis. Also find the attached photos for your reference? 1 item detail: ITEM : ACB RATING : 4000A, 65KA, 4P MODEL NO. NW SERIAL NO. 10222671699 MAKE : SCHNEIDER QTY.- 1 NO. 2 item detail: ITEM : ACB RATING : 2000A, 65KA, 3P MODEL NO. NW SERIAL NO. 10220960350 MAKE : SCHNEIDER QTY.- 1 NO. Site address: Uflex Ltd. Malanpur, Madhya Pradesh- 477117 Contact person: Mr.Bhupander Negi Contact number: 7885431558 Regards, MOHD TALHA ¦ GET ¦ Quality | 2023-09-19 | 2023-09-21 16:09 | No | Warranty | U Flex LTD | L 1, Ghirongi Industrial Area | Malanpur | 477117 | Madhya Pradesh | India FS ED&I CSP West Team ABR Technical Service Indore | Lalu Sen_ABR Tecneical Services Indore | ABR Technical Services (9574) | Reached at site and checked ACB and found its not tripped after main power OFF (incoming supply OFF) Then we checked UV coil and found its not fixed properly then we fixed it in proper direction and proper location then we checked ACB ON /OFF operation 5-7 times it's working properly so as per our observation it's not product issue ACB not tripped due to the UV coil not fixed properly so we resolved this issue and now we are close this case. UV COIL - 380 - 480 VAC MX2 - 24 VAC /DC XF - 208- 240 VAC MCH - 200-240 VAC | Repair |  | 9- Service Validated | 2023-09-21 16:18 | =S= Consig Fill up 226068978 |  | 650 | INR | 650 | ENM POWER PRODUCTS
WO-11224701 |  | 2023-09-07 14:22 | 2023-09-20 |  | 2023-09-07 13:25 | LEONARDO EVDXR22/R407CEC FANTDAV0711A (ZR108KCE-TFD)DNFLW WITH "H" VERSION ( FRA | TDAV0711AN003 | TDAV0711AN003 | C21827004091 | PM | 2023-09-07 | 2023-09-20 11:10 | No | Contract | CTBC Bank Co. Ltd | Gnd and 2 Nd Floor,Aria Tower, JW Marriott Hotel,Aerocity null | New Delhi | 110037 | Delhi | India FS North1 Cooling CSP Hitech solutions New Delhi | Arvind Kumar_Hitech solutions New Delhi | Hitech Solutions-New Delhi-Delhi | Preventive Maintenance done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-20 11:12 |  |  | 24 | INR | 24 | ENM SECURE POWER
WO-11280969 | 104120136 | 2023-09-20 12:36 | 2023-09-19 |  | 2023-09-19 16:43 | LC1D40AF7 | LC1D40AF7 | LC1D40AF7 |  | LC1D40AF7 not working Sagah Elevators sector 37 J-block Plot number 5 Near Saraswati Enclave Gurgoan 122001 Haryana Mohd Shaharukh 9258117027 mohdshaharukh818@gmail.com A9N3P20C 20A 3P MCB INVOICE NO. F/23-24/3461 DATE ? 31-AUG-23 | 2023-09-19 | 2023-09-20 12:55 | No | Warranty | Sagah Elevators | sector 37 J-block Plot number 5 Near Saraswati Enclave | Gurgoan | 122001 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the Add on block found not getting hold , Hence faulty replaced. LADN11 - 1 nos Email : id not provided by customer. | Repair |  | 8- Service Completed | 2023-09-23 17:10 |  |  | 70 | INR | 70 | ENM POWER PRODUCTS
WO-11284739 | 104144461 | 2023-09-20 11:57 | 2023-09-20 |  | 2023-09-20 10:57 | LC1E1210M7 | LC1E1210M7 | LC1E1210M7 | 10-2205 5 | complaints Product : LC1E1210M7 Sr No. 10-2205 5 , Jan - 2022 Yes In warranty Mechanism Jam / Unable to switch ON / OFF Coil Melted | 2023-09-20 | 2023-09-20 11:59 | No | Warranty | Surinder KUMAR | # 3261 New jawahar Nagar opposite CM mall | Jalandhar | 144005 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the contactor found Mechanism Jam due to Unable to switch ON / OFF Coil Melted and capacitor found leakage issue and (LX1FH2202) contactor coil found not working. Hence faulty replaced. LAEX12M7 - 1 Nos. MEHVCHDY250A44 - 1 Nos. LX1FH2202 - 1 Nos. email : surinder@nmainda.com | Repair |  | 8- Service Completed | 2023-09-20 15:57 |  |  | 65 | INR | 65 | ENM POWER PRODUCTS
WO-11284986 | 104144066 | 2023-09-21 09:52 | 2023-09-23 |  | 2023-09-20 11:29 | MVS16N4NW6L | MVS16N4NW6L | MVS16N4NW6L |  | Name of Customer Madura Coats Private Limited Site Address Papavinasam Mills , Tirunelveli , Pincode ? 627 422 . Name of contact person at site Mr.Rahim Babu Contact Phone / Mob. No: 9677725437 Defective product details MVS16N4NW6L 1 MVS08N4NW6L 1 MVS08N3NW6L 3 Nature of Defect 1600A ACB not getting Drow out , 800A ACB indicator not indicate . Shutdown availability if applicable Yes Warranty status Yes Commissioned / Installed date New product Serial No: or DOM of the product Invoice copy can be produced Name & phone No: of person registering the complaint " P.Rajeev Gandhi / 7397763892 " product_engg@spares4u.in Invoice Date 10-06-2023 -- Regards P. Rajeevegandhi B.E. ¦ Manager Industrial Sales SPARES 4U # I / 1-C , SIDCO Industrial Estate ¦ K.Pudhur ¦ Madurai - 625 007 Direct Line : 0452 - 3500445 ¦ 91 7397763892 ¦ product_engg@spares4u.in | 2023-09-20 | 2023-09-26 10:10 | No | Warranty | Madura Coats Private Limited | Papavinasam Mills , | Tirunelveli | 627422 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | George KJ_Omicon Engineering Madurai | Omicon Engineering | Micrologic Battery failure | Repair |  | 8- Service Completed | 2023-09-26 10:19 |  |  | 250 | INR | 250 | ENM POWER PRODUCTS
WO-11285037 | 104145793 | 2023-09-20 15:43 | 2023-09-20 |  | 2023-09-20 11:59 | LC1D32M7 | LC1D32M7 | LC1D32M7 |  | LC1D32M7 389110351088 Invoice Date : 19/09/2023 Invoice Number : SVE/23-24 04941 Vijay Shankar 9660458506 vijayshankarpanchal1995@gmail.com Goyal Handicraft E-307 Sitapura Industrial Area, Satarala Circle Jaipur 302022 Rajasthan | 2023-09-20 | 2023-09-20 16:12 | No | Warranty | Goyal Handicraft | E-307 Sitapura Industrial Area, Satarala Circle null | Jaipur | 302022 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Sunny Sharma Sharma Electric Jaipur | Sharma Electric Works | Checked the contactor found coil burnt due to high voltage, Hence no replacement given to customer. Email : id not provided by customer. | Repair |  | 8- Service Completed | 2023-09-21 15:11 |  |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11224961 | 103855915 | 2023-09-07 18:23 | 2023-09-07 |  | 2023-09-07 14:59 | Easy UPS 3S 40 kVA 400 V 3:3 UPS for external batteries | E3SUPS40KH | E3SUPS40KH | 9E2231T12966 | Warranty P; UPS Not Working S: Onsite | 2023-09-07 | 2023-09-08 15:56 | No | Warranty | Sigma Imaging & Diagnostics | LGF Leela Tower 120, Raipur, IIM Road, IIM Lucknow | LUCKNOW | 226013 | Uttar Pradesh | India FS North2 HBN CSP BK Technologies Kanpur | Mitesh Singh B.K. Technologies Kanpur | BK Technologies | UPS all parameteres are ok but 1 no.Exide 42AH battery having lrakage and faulty. Need to replace immediate . | Repair |  | 10- Closed | 2023-09-08 19:00 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two persons is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 26 | INR | 26 | ENM SECURE POWER
WO-11226177 |  | 2023-09-28 17:47 | 2023-09-10 |  | 2023-09-07 18:51 | APC Smart-UPS VT 40kVA 400V, w/Internal Maintenance Bypass & Parallel Capability | SUVTP40KH | SUVTP40KH | PS1052240342 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-07 | 2023-09-26 14:01 | No | Contract | HDFC Bank Ltd | Sai Nagar Devendra Nagar Radaur, Dist ? Yamunanagar, | Raipur | 492001 | chhattisgarh | India FS East HBN CSP K.G.N.Computers Raipur | Neelkamal Sahu_K.G.N.Computers Raipur | KGN COMPUTERS | pm service done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-28 19:07 |  |  | 10 | INR | 10 | ENM SECURE POWER
WO-11287376 | 104089861 | 2023-09-21 11:36 | 2023-09-20 |  | 2023-09-20 20:54 |  |  |  |  | RMA 104089861_RO 61371618 | 2023-09-20 | 2023-09-22 12:00 | No | Warranty | Power Control Agency | B-10, Suryam Industrial Park, Station Nikol,Nr.Torrent Power Sub, Nr. Kathwada,GIDC, Odhav to Nikol Ring Road, | Ahmedabad | 382350 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Mistri Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physically observed ok. LV525343 SR NO : 10 2021 W14 obsered mccb pole open. so we open the front cover and check screw but no any flash observed. so customer provide invoice as per invoice we book the material. =S= Free Order 226078463 has been saved | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-22 15:21 | =S= Free Order 226078463 has been saved |  | 10 | INR | 10 | ENM POWER PRODUCTS
WO-11287441 | 104039073 | 2023-09-21 16:08 | 2023-09-20 |  | 2023-09-20 21:59 |  |  |  |  | RMA 104039073_RO 61371199 | 2023-09-20 | 2023-09-23 12:43 | No | Warranty | VPN Agenciies - 500017482 | 5, Ground Floor 1, Midland Complex | Salem | 636009 | Tamil Nadu | India FS ED&I CSP South Team Power Pro Engineering Services Coimbatore | KV ARUNKUMAR_POWER PRO ENGINEERIG SERVICES COIMBATORE | Powerpro Engineering Services | WE HAVE INSPECTED WE FOUND CONTACTOR COIL CHATTERING ISSUE WE HAVE RECTIFY THE SAME TESTD AND FOUND WORKING OK | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-23 12:44 |  |  | 1 | INR | 1 | ENM POWER PRODUCTS
WO-11290307 | 104154287 | 2023-09-21 14:46 | 2023-09-21 | MPCB Handle not fitted properly | 2023-09-21 13:29 | SQD-GV3APN02 | SQD-GV3APN02 | SQD-GV3APN02 |  | Dear Sir, We have received GV3APN01 against So.no.- 225589273 & Invoice no.-9008518930 1.Handle GV3APN01 - 1 [Screw problem.] Handle screw not adjusted on MPCB. Site address- Simply Electrifying Pvt. Ltd. 201 Varsha Avenue, 104 Anand Park Aundh, Pune 411007 Contact person- Ms. Mohini (8805008503) Please find the attached Schneider Invoice & GV3APN01 Image. Thanks & Regards, Mohini Bali 8805008503 A B Controls / Simply Electrifying Pvt. Ltd. 201 Varsha Avenue, 104 Anand Park Aundh, Pune 411007 Tel : +91- 20- 25890010 / 25890030 Tollfree : +91 - 1800 233 4333 Please do visit us at www.simply-electrifying.com | 2023-09-21 | 2023-09-22 12:20 | No | Warranty | SIMPLY ELECTRIFYING PVT. LTD. + A B CONTROLS | 201 Varsha Avenue, 104 Anand Park Aundh | Pune | 411007 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Samadhan S_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the MPCB Handle not fitted properly. MPCB handle screw mounting not matched with MPCB fitted 6 hole. MPCB is not fitted impossible. So problem observed in MPCB. It's Needs to be Replaced. Required material : GV3APN01 - 01 nos | Repair |  | 9- Service Validated | 2023-09-23 11:24 | =S= Consig Fill up 226079010 |  | 35 | INR | 35 | ENM POWER PRODUCTS
WO-11290761 | 104178497 | 2023-09-23 12:09 | 2023-09-21 |  | 2023-09-21 16:58 | LC1D12BD | LC1D12BD | LC1D12BD | INV NO : 9007848080 | Dear Sir, Kindly find the attachment complaint registration form. Name of Customer M/s. VERSA DRIVES PRIVATE LIMITED Site Address 38-B VADAKKU THOTTAM PART, IDIKARAI COIMBATORE - 641022 Name of contact person at site Mr. PURCHASE DEPARTMENT Contact Phone / Mob. No: 0422 - 2972798 Customer's email I'd contact@versadrives.com Defective product details( Complete Product ref) LC1D12BD - 6NOS (SCREW PROBLEM) LC1D25BD - 34NOS (NC PROBLEM SCREW PROBLEM INPUT SPRING DAMAGE) LC1D32BD - 3NOS (SCREW PROBLEM) LC1D09BD - 13NOS (SCREW PROBLEM) A9N1P63C - 15NOS (SCREW PROBLEM) A9N2P01C - 10NOS (SCREW PROBLEM) LC1D32N7 - 1NO (SCREW PROBLEM) LADN22 - 3NOS (DID NOT ON) Product Make SCHNEIDER Nature of Defect Screw Problem, NC Problem screw problem Input problem spring damage, screw problem, screw problem, screw problem, screw problem, Did not on Shutdown availability if applicable YES Commissioned / Installed date Serial No: or DOM of the product/OA no./Invoice Details INV NO : 9008674137,9008721751, 9008706888, 9008712035, 9008622522, 9008696351, 9008711016, 9008710422 vpncbe1@gmail.com Thanks & Regards, REKHA M Elite Partner & System Integrator Of VPN AGENCIIES No: 5, Corporation Shopping Complex, Avinashi Road, Coimbatore ? 641 018 Phone: +91 422 4379941, 42 ¦ Fax: + 91 422 2234568 ¦ Mobile: +91 90031 47288, +91 98940 16253 Email:vpncbe@gmail.com, vpncbe5@gmail.com Website: www.vpnagenciies.com | 2023-09-21 | 2023-09-30 21:55 | No | Warranty | Versa Drives Pvt Ltd | 38B, Vadakkuthottam Part, Idikarai, Coimbatore Tamil Nadu | Coimbatore | 641022 | Tamil Nadu | India FS ED&I CSP South Team Power Pro Engineering Services Coimbatore | KV ARUNKUMAR_POWER PRO ENGINEERIG SERVICES COIMBATORE | Powerpro Engineering Services | WE HAVE VISITED THE SITE AND INSPECTE WE FOUND MCB POLE CIRCUITED & MCB ON & OFF DOLLY FREE WE COLLECTED THE DETAILS FOR FURTHER ACTION AND ARRAGING FOR THIS | Repair |  | 8- Service Completed | 2023-09-30 21:57 |  |  | 21 | INR | 21 | ENM POWER PRODUCTS
WO-11290786 | 104183967 | 2023-09-21 17:51 | 2023-09-21 | WE required approval from marketing for replacement | 2023-09-21 17:13 | MEHVCHDY281A48PB | MEHVCHDY281A48PB | MEHVCHDY281A48PB |  | Dear Sir, Please find below details. 1. Model number of the product ---------- MEHVCHDY281A48PB 2. Serial number of the product ----------- M0770264 3. Invoice Details ----------------------------- From Bengal Electricals, Kolkata, Invoice No:664, 21/05/2023 4. Complete site address with pin-code ------ Standard Electricals, Plot No: 41 & 42, Ground Floor, Mahavir Small Scale Industrial Estate, Vadod Bamroli Road, Vadod Gam, Surat - 395023 5. Contact person"s name and contact details ---------- Anil Kumar Singhi, 93747 22574 6. Email ID -------- standard_electricals2004@yahoo.co.in Anil Singhi, Standard Electricals, Plot No: 41 & 42, Ground Floor, Mahavir Small Scale Industrial Estate, Vadod Bamroli Road, Vadod Gam, Surat - 395023 +91- 8799589787 +919374722574. GST Provisional ID: 24AUQPS2078A1ZK ARN No : AA2406170338436 MSME No: UDYAM-GJ-22-0018891 Authorised Dealer For:- On Saturday, 16 September, 2023 at 02:36:01 pm IST, Mail2Case India <customercare.in@schneider-electric.com> wrote: Hello Sir/Mam.Greetings of the day.We have received your complain request , We would like to tell you that the details which you have sheared with us is not sufficient for filing the complain .So we request you that please share the mentioned details:1. Model number of the product2. Serial number of the product3. Invoice Details4. Complete site address with pin-code5. Contact person"s name and contact details6. Email IDThank YouRegards,Ankur SinghCustomer Care Centre ¦ Schneider Electric India ¦ Toll Free: 18001030011 / 18004254272 / 18004194272 ¦ Email:Customercare.in@schneider-electric.com ¦ Site: www.schneider-electric.com--------------- Original Message ---------------From: [standard_electricals2004@yahoo.co.in]Sent: 16/9/2023 1:46 pmTo: customercare.in@schneider-electric.comSubject: Capacitor Failure Dear Sir, We have purchased 35 Nos of 28.1 KVAR capacitors from Bengal Electricals, Kolkata on 21st May 2022 & we have received a complaint from our end user that 1 No of the capacitors is failed. DATE CAPACITOR CAT NO MAKE SR NO 26.05.2022 POWER LOGIC PFC-HDUTY MEHVCHDY281A48PB SCHNEIDER M0770264 FAULTY Anil Singhi, Standard Electricals, Plot No: 41 & 42, Ground Floor, Mahavir Small Scale Industrial Estate, Vadod Bamroli Road, Vadod Gam, Surat - 395023 +91- 8799589787 +919374722574. GST Provisional ID: 24AUQPS2078A1ZK ARN No : AA2406170338436 MSME No: UDYAM-GJ-22-0018891 Authorised Dealer For:- No Attachments linked to the emailthread::8J9Gh6xbeom29lIOLKVrpj4:: | 2023-09-21 | 2023-09-23 16:12 | No | Warranty | Standard Electricals | Plot No 41 & 42 Ground Floor Mahavir Small Scale Industrial Estate Vadod Bamroli Road Vadod Gam | Surat | 395023 | Gujarat | India FS ED&I CSP West Team VARDHAMAN ELECTROSOFT Vadodara | MAHENDRA SINGH VARDHAMAN ELECTROSOFT Vadodara | VARDHAMAN ELECTROSOFT | we visited the site and check the capacitor and found capacitor terminal contact burned when i checked the value of capacitor it is RU -192.6 uf UB- BR value is not getting it .This is not the manufacturer's issue | Repair |  | 8- Service Completed | 2023-09-23 16:13 |  |  | 60 | INR | 60 | ENM POWER PRODUCTS
WO-11290886 | 104176201 | 2023-09-22 10:51 | 2023-09-21 | Na | 2023-09-21 17:58 | LV432895 | LV432895 | LV432895 |  | Dear Schneider electric team, Please find attached photos of NSX 630H breaker for your reference. Kindly lock the compliant against breaker. Issues:- Breaker castle lock not getting operated not fixed in frame please find attached video. LV432895 TC-2023-W66-7-U1 Site address:- Lodha Park, Tower 5, Gate No. 2, Pandurang Budhkar Marg, Worli, Mumbai, Maharashtra 400018. Site Contact Person :- Shinu Sir PEPL- Contact No :- 98693 35345 | 2023-09-21 | 2023-09-22 18:42 | No | Warranty | Shinu Sir | Lodha Park, Tower 5, Gate No. 2, Pandurang Budhkar Marg, Worli | Mumbai | 400018 | Maharashtra | India FS ED&I CSP West Team East India Power Engineers Mumbai | Ratnesh Shigvan East India Power engineers Mumbai | East India Power Engineers (5043) | Visited the site and checked the locking assembly in losse condition also found interlocking assembly checknut was free. Open the motor mechanism from MCCB removed the MCCB front cover of the motor mechanism fix the lock assembly as per Schneider standard. Done the fitment of MCCB and checked the key operation working ok. | Repair |  | 8- Service Completed | 2023-09-22 18:57 |  |  | 27 | INR | 27 | ENM POWER PRODUCTS
WO-11293771 | 104148663 | 2023-09-22 15:04 | 2023-09-22 |  | 2023-09-22 08:51 | LV525313 | LV525313 | LV525313 |  | RE: MCCB Issue : AEON Noida, Case: 102343095, [ thread::aVaV6lwyeMOtdO0SQ7BgrT4:: ] In July, we have replaced the MCCB for which SIR is attached with mail. As per customer, again the same MCCB is faulty(customer mail attached). Please log the complaint for the below issue, Invoice is attached with the mail-- MCCB not working LV525313 CVS250B TM250D 4P3D Qty 1 Site details- AEON Integrated Ltd. A-22 Sector -136 Noida Cont. Person. Mr. Santosh 9911918512 Regards Vinay Kumar DGM Prescription National Sales Schneider Electric D 0124-6899000 M 9810533041 | 2023-09-22 | 2023-09-25 18:04 | No | Warranty | AEON Consultant | A-122, 6th Floor, Sector 136 | Noida | 201305 | Uttar Pradesh | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mccb found not giving output, Hence faulty replaced. C25F3TM200 - 1 nos Email :santosh.prasad@aeonconsultants.in | Repair |  | 8- Service Completed | 2023-09-26 15:07 |  |  | 65 | INR | 65 | ENM POWER PRODUCTS
WO-11226316 |  | 2023-09-25 12:40 | 2023-12-16 |  | 2023-09-07 19:10 | SYMMETRA PX 40KW FRAME, 400V | SYCF40KH | SYCF40KH | PD0811160199 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-07 | 2023-09-25 12:55 | No | Contract | Central Board of Excise & Customs-CBEC | Nacen Complex Sector-29 Faridabad null | Faridabad | 121001 | Haryana | India FS North1 HBN CSP Prokon Hi Tech Systems Gurgaon | Subodh Pasupat Prokon Hi-Tech Systems Faridabad | Prokon Hi-Tech Systems-Faridabad-Haryana | Stand by ups PM done now ups working is okay. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-25 13:07 |  |  | 25 | INR | 25 | ENM SECURE POWER
WO-11293827 | 104174150 | 2023-09-22 10:40 | 2023-09-22 | Contactor not switching | 2023-09-22 09:30 | LC1D25BD | LC1D25BD | LC1D25BD |  | Pls arrange service engineer on site Dear Team Pls arrange to attend below faulty product urgently : LC1D25BD Refer attached photos of Schneider Make contactor & Diode which is found faulty during testing 1. Diode :- When 24VDC is applied to diode is getting short . 2. Contactor:- 25 A contactor is not getting on after 24VDC is applying. Thanks & Regards, --------------------------------------------------- Mr.Nikhil Rathwadkar Oneness ControlPanels Pvt.Ltd. Plot no.1A, GAT.No. 108/1, At post Ranje Shivapur- Kondhanpur Rd. Tal Bhor Dist Pune PIN 412205 Email : <oneness.store6@onenesscontrolpanels.com> MOB NO ? 8796627253 | 2023-09-22 | 2023-09-23 12:27 | No | Warranty | Oneness Controlpanels pvt. Ltd. | Plot No.1A,Gat No.108/1,At Post Ranje, Shivapur Kondhanpur Road,Tal Bhor, Dist-Pune- | PUNE | 412205 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Amit Patil_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the Contactor not switching. we given supply to contactor but contactor not getting On. we checked another product diode found short & tripped main MCB. So problem observed in above products, So Required Material : LC1D25BD- 01 nos, RXM040W- 01 nos | Repair |  | 9- Service Validated | 2023-09-25 12:12 |  |  | 55 | INR | 55 | ENM POWER PRODUCTS
WO-11295192 | 104205740 | 2023-09-23 17:28 | 2023-09-22 |  | 2023-09-22 11:28 | GCR_LV_APFC | GCR_LV_APFC | GCR_LV_APFC | ME-E-N040020/21/22 | Dear Sir Please find the attached file of Invoice Copy of APFC Panel. Thanks & Regards Sachin Panwar Electrical Manager E-20 Greenfuels Pvt. Ltd. (Mob-7503107872) On Thu, 21 Sept 2023 at 09:56, Schneider Electric Customer care <customercare.in@schneider-electric.com> wrote: Hi Sir /Mam Greetings from Schneider Electric Customer care !!!! Please share us the below requirement details for warranty validation & complain registration 1) Schneider Supply invoice copy Regards , Anupam Bhattacharjee Customer Care Centre ¦ Schneider Electric India ¦ Toll Free: 18001030011 / 18004194272 ¦ Email:Customercare.in@schneider-electric.com ¦ Site: www.se.com/in --------------- Original Message --------------- From: [electrical_dep@e20greenfuels.com] Sent: 20/9/2023 4:28 pm To: customercare.in@schneider-electric.com Subject: Complain Dear Customer Care Team, Please depute service engineer to address below customer complaint: Product Code:800 KVAr APFC Panel Serial No: ME-E-N040020/21/22 Problem: Not working in auto mode & one panel continuously showing panel temp high, some mcb tripping in control section, Company Name: E-20 Greenfuels Private Limited Company Address with Pin: E-20 Greenfuels Private Limited Village Panniwala Ruldu Dabwali Kalanwali Road Tehsil Mandi Dabwali Distt-Sirsa Haryana Pin-125104 Contact Person: Sachin Panwar Contact No: 7503107872 Alternate No. Thanks & Regards Sachin Panwar Electrical Manager E-20 Greenfuels Pvt. Ltd. (Mob-7503107872) Invoice Date : 28/02/2023 Invoice Number : 9008453045 No Attachments linked to the email thread::_eL5HyVkfwiQR7orb0sW0j4:: | 2023-09-22 | 2023-09-23 17:33 | No | Warranty | E-20 Greenfuels Private Limited | Village Panniwala Ruldu Dabwali Kalanwali Road Tehsil Mandi Dabwali | Sirsa | 125104 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Ram Ashish Sharma Electric Chandigarh | Sharma Electric works(1003) | checked the apfc penal found and resolved the auto operation issue now PF is .99. Resolved and repair. Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-23 17:36 |  |  | 259 | INR | 259 | ENM POWER PRODUCTS
WO-11295360 | 104158992 | 2023-09-22 12:37 | 2023-09-22 |  | 2023-09-22 12:33 |  |  |  |  | RMA 104158992_RO 61371936 | 2023-09-22 | 2023-09-22 12:00 | No | Warranty | Power Electricals | S.M.TOWERS,5-1-12,13,71 & 72, R.P.ROAD, SECUNDERABAD ? 500003 | Secunderabad | 500003 | Telangana | India FS ED&I CSP South Team Sumanth Electrical Services Hyderabad | Venkata Prasad_SUMANTH ELECTRICAL SERVICES HYDERABAD | Sumanth Electrical Services | =S= Free Order 226079162 has been saved | Assessment/ Inspection | Data Collection | 8- Service Completed | 2023-09-22 21:51 | =S= Free Order 226079162 has been saved |  | 6 | INR | 6 | ENM POWER PRODUCTS
WO-11295417 | 104209030 | 2023-09-22 13:19 | 2023-09-22 |  | 2023-09-22 12:52 | UNS161SW1M_WE | UNS161SW1M_WE | UNS161SW1M_WE |  | Required Complaint Number Dear Team, MR. UTTAM YADAV JI GANGARAM KI DHANI DHAWAS JAIPUR MR. UTTAM YADAV JI 9828078118 Product : UNS32DP2M-WE - 1 , UNS161SW1M-WE- 2 NOS DOP - 21/Sep/2022 Broken issue invoice attached -- *WITH REGARDS-* Sarabjit Singh | 2023-09-22 | 2023-09-22 13:26 | No | Warranty | UTTAM YADAV | GANGARAM KI DHANI DHAWAS | Jaipur | 302043 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Sunny Sharma Sharma Electric Jaipur | Sharma Electric Works | Checked the switch found not giving output and mcb found phase missing, Hence faulty replaced. UNS32DP2M_WE - 4 UNS6SK3P2MNS - 1 nos UNS61SW1M_WE - 6 nos UNS161SW1M_WE - 5 nos EZ9S66463 - 1 nos EZ9F71463 - 1 nos Email : | Repair |  | 8- Service Completed | 2023-09-22 15:40 |  |  | 30 | INR | 30 | ENM POWER PRODUCTS
WO-11226283 |  | 2023-09-28 17:49 | 2023-09-10 |  | 2023-09-07 19:04 | Symmetra PX 20kW Scalable to 40kW N+1, 400V | SY20K40H | SY20K40H | PD0751260061 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-07 | 2023-09-29 14:34 | No | Contract | Central Board of Excise & Customs-CBEC | Tikarapara Raipur null | Raipur | 492001 | chhattisgarh | India FS East HBN CSP K.G.N.Computers Raipur | Neelkamal Sahu_K.G.N.Computers Raipur | KGN COMPUTERS | Pm services done. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-29 21:37 |  |  | 10 | INR | 10 | ENM SECURE POWER
WO-11226669 | 103869484 | 2023-09-08 09:36 | 2023-09-07 |  | 2023-09-07 21:32 | Leonardo EVDXR407cEC FanTDAV1021ADownflow With Heater & Humidifier | TDAV1021AN002 | TDAV1021AN002 | C21721000354 | P : water Leak | 2023-09-07 | 2023-09-08 10:01 | No | Contract | Novac Technology Solutions Private Limited | No : 275 RK Mutt Road, Mylapore | Chennai | 600004 | Tamil Nadu | India FS South4 Cooling CSP Unity Air conditioning Engineers Chennai | G Vinoth Unity Air-conditioning Engineers Chennai | UNITY AIRCONDITIONING ENGINEERS | Water leakage : Now we checked and found the water block in main header line. Now we clear the blockage and observe unit working normal. | Repair |  | 10- Closed | 2023-09-08 10:30 |  |  | 15 | INR | 15 | ENM SECURE POWER
WO-11226676 | 103869566 | 2023-09-08 09:38 | 2023-09-08 |  | 2023-09-07 21:36 | Leonardo EVDXR407cEC FanTDAV1021ADownflow With Heater & Humidifier | TDAV1021AN002 | TDAV1021AN002 | C21725000728 | P : water Leak | 2023-09-07 | 2023-09-08 12:00 | No | Contract | Novac Technology Solutions Private Limited | No : 275 RK Mutt Road, Mylapore | Chennai | 600004 | Tamil Nadu | India FS South4 Cooling CSP Unity Air conditioning Engineers Chennai | V Ramkumar_ Unity Air conditioning Engineers Chennai | UNITY AIRCONDITIONING ENGINEERS | Water Leakage : Now we checked and found blockage in main drain line. Now we cleaned the blockage and vacuum the main drain line. observe unit working normal. | Repair |  | 10- Closed | 2023-09-08 16:12 |  |  | 15 | INR | 15 | ENM SECURE POWER
WO-11227882 |  | 2023-09-11 13:38 | 2023-09-11 |  | 2023-09-08 02:52 | APC Symmetra LX 12kVA Scalable to 16kVA N+1 Rack-mount, 220/230/240V or 380/400/ | SYA12K16RMI | SYA12K16RMI | QD0827260377 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-08 | 2023-09-11 15:18 | No | Contract | Central Board of Excise & Customs-CBEC | NCR Building, Statue Circle Jaipur Rajasthan 302005 NCR Building, Statue Circle Jaipur Rajasthan 302005 | Jaipur | 302005 | Rajasthan | India FS North1 HBN CSP Legacy Systems Jaipur | Kuldeep Kumawat Legacy Systems Jaipur | Legacy Systems | PM done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-11 15:22 |  |  | 6 | INR | 6 | ENM SECURE POWER
WO-11227883 |  | 2023-09-11 13:29 | 2023-09-02 |  | 2023-09-08 02:52 | APC Symmetra LX 12kVA Scalable to 16kVA N+1 Rack-mount, 220/230/240V or 380/400/ | SYA12K16RMI | SYA12K16RMI | QD0827260115 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-08 | 2023-09-11 15:28 | No | Contract | Central Board of Excise & Customs-CBEC | NCR Building, Statue Circle Jaipur Rajasthan 302005 NCR Building, Statue Circle Jaipur Rajasthan 302005 | Jaipur | 302005 | Rajasthan | India FS North1 HBN CSP Legacy Systems Jaipur | Rudresh Kumawat Legacy Systems Jaipur | Legacy Systems | PM done | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-11 15:31 |  |  | 6 | INR | 6 | ENM SECURE POWER
WO-11227832 |  | 2023-09-12 11:39 | 2023-09-02 |  | 2023-09-08 02:47 | APC Symmetra LX 12kVA Scalable to 16kVA N+1 Rack-mount, 220/230/240V or 380/400/ | SYA12K16RMI | SYA12K16RMI | QD0824160099 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-08 | 2023-09-18 15:02 | No | Contract | Central Board of Excise & Customs-CBEC | Systems Manager, ICES, Jawaharlal Nehru Custom House (JNCH), Nhava Sheva, Post Uran,District, Raigad, Maharashtra null | Raigad | 400707 | Maharashtra | India FS West1 HBN CSP_Mahavir Sys Power Pvt Ltd Vashi | Sanju Chauthmol_Mahavir Sys Power Pvt Ltd Vashi | Mahavir Sys Power Pvt Ltd -Vashi | Engineer had done the PM of ups at customer site and checked found that out of 6 battery module 4qty battery modules showing off & failed | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-18 15:11 |  |  | 43 | INR | 43 | ENM SECURE POWER
WO-11227833 |  | 2023-09-12 11:38 | 2023-09-02 |  | 2023-09-08 02:47 | APC Symmetra LX 16kVA N+1 Ext. Run Tower Frame, 220/230/240V or 380/400/415V | SYAF16KXR9I | SYAF16KXR9I | QD0824160091 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-08 | 2023-09-16 20:32 | No | Contract | Central Board of Excise & Customs-CBEC | Systems Manager, ICES, Jawaharlal Nehru Custom House (JNCH), Nhava Sheva, Post Uran,District, Raigad, Maharashtra null | Raigad | 400707 | Maharashtra | India FS West1 HBN CSP_Mahavir Sys Power Pvt Ltd Vashi | Sanju Chauthmol_Mahavir Sys Power Pvt Ltd Vashi | Mahavir Sys Power Pvt Ltd -Vashi | Engineer had done the PM of ups at customer site and found that out of 6 battery module 3 nos battery module are showing low capacity ups is working normal | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-16 20:35 |  |  | 43 | INR | 43 | ENM SECURE POWER
WO-11227834 |  | 2023-09-12 13:49 | 2023-09-02 |  | 2023-09-08 02:47 | APC Symmetra LX 16kVA N+1 Ext. Run Tower Frame, 220/230/240V or 380/400/415V | SYAF16KXR9I | SYAF16KXR9I | QD0827260092 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-08 | 2023-09-18 15:40 | No | Contract | Central Board of Excise & Customs-CBEC | Jawaharlal Nehru Custom House (JNCH) ? Uran null | Uran | 410206 | Maharashtra | India FS West1 HBN CSP_Mahavir Sys Power Pvt Ltd Vashi | Sanju Chauthmol_Mahavir Sys Power Pvt Ltd Vashi | Mahavir Sys Power Pvt Ltd -Vashi | Engineer ha done the PM of ups at customer site and checked found that out of 6 battery module 3qty battery module are showing Low capacity, Ups is working normal | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-18 17:00 |  |  | 43 | INR | 43 | ENM SECURE POWER
WO-11227839 |  | 2023-09-27 18:31 | 2023-09-02 |  | 2023-09-08 02:47 | APC Symmetra LX 16kVA N+1 Ext. Run Tower Frame, 220/230/240V or 380/400/415V | SYAF16KXR9I | SYAF16KXR9I | QD0826260119 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-08 | 2023-09-27 18:34 | No | Contract | Central Board of Excise & Customs-CBEC | Ganges Ink Bldg., 110 1st floor, Opp.Cipla, L.B.S.Marg,Vikhroli(West) null | Mumbai | 400083 | Maharashtra | India FS West1 HBN CSP_Mahavir Sys Power Pvt Ltd Vashi | Sanju Chauthmol_Mahavir Sys Power Pvt Ltd Vashi | Mahavir Sys Power Pvt Ltd -Vashi | Engineer visited the customer site for ups PM and found that ups was in disconnect condition since past 2 years , Battery modules are totally discharged ups is not powering on reqyure battery module to power on the UPS. Also Ups body is corrosion | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-27 18:39 |  |  | 21 | INR | 21 | ENM SECURE POWER
WO-11227921 |  | 2023-09-14 11:34 | 2023-09-02 |  | 2023-09-08 02:58 | APC Symmetra LX 16kVA N+1 Tower Frame, 220/230/240V or 380/400/415V | SYAF16KI | SYAF16KI | QD0807280376 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-08 | 2023-09-14 11:37 | No | Contract | Central Board of Excise & Customs-CBEC | Deputy Commissioner, Khodiyar Jamuna Palej Gav Nr. Vaishno Devi, Gandhinagar Highway null | Ahmedbad | 3882243 | Gujarat | India FS West2 HBN CSP_Mahavir Sys Power Pvt Ltd Ahmedabad | Dhaval Chauhan_Mahavir Sys Power Pvt Ltd Ahmedabad | Mahavir Sys Power Pvt Ltd | Engineer Visited the site and Done PM activity, batteries and UPS working fine on mains and battery mode. No fault present in the System. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-14 11:39 |  |  | 15 | INR | 15 | ENM SECURE POWER
WO-11227867 |  | 2023-09-11 14:05 | 2023-09-20 |  | 2023-09-08 02:50 | APC Symmetra LX 16kVA N+1 Ext. Run Tower Frame, 220/230/240V or 380/400/415V | SYAF16KXR9I | SYAF16KXR9I | QD0913160053 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-08 | 2023-09-20 16:54 | No | Contract | CBEC | Mahavir Jain Vidalaya, C.D., Barfiwala, Lane, Andheri null | Mumbai | 400058 | Maharashtra | India FS West1 HBN CSP_United Solutions Mumbai | Rohan Kamble United Solutions Mumbai | UNITED SOLUTIONS - MUMBAI | Preventive maintains has been done. Check all parameter are ok. not found any issue. UPS is working fine. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-20 16:59 |  |  | 4 | INR | 4 | ENM SECURE POWER
WO-11227873 |  | 2023-09-11 14:08 | 2023-09-22 |  | 2023-09-08 02:51 | SYAF16KXR9I | SYAF16KXR9I | SYAF16KXR9I | AD1713120749 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-08 | 2023-09-22 14:54 | No | Contract | Central Board of Excise & Customs-CBEC | Piramal Chambers 9th Floor Jijibhoy Lane Lalbaug null | Mumbai | 400012 | Maharashtra | India FS West1 HBN CSP_United Solutions Mumbai | Rohan Kamble United Solutions Mumbai | UNITED SOLUTIONS - MUMBAI | Preventive Maintenance has been done. Check online UPS found 1 nos power module faulty. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-22 14:59 |  |  | 16 | INR | 16 | ENM SECURE POWER
WO-11227874 |  | 2023-09-11 14:09 | 2023-09-22 |  | 2023-09-08 02:51 | SYAF16KXR9I | SYAF16KXR9I | SYAF16KXR9I | AD1719320470 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-08 | 2023-09-22 16:00 | No | Contract | Central Board of Excise & Customs-CBEC | Piramal Chambers 9th Floor Jijibhoy Lane Lalbaug null | Mumbai | 400012 | Maharashtra | India FS West1 HBN CSP_United Solutions Mumbai | Rohan Kamble United Solutions Mumbai | UNITED SOLUTIONS - MUMBAI | Online preventive Maintenance has been done. Check all parameter are ok but 10 no's SYBT5 and 1 no's power module faulty. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-22 16:03 |  |  | 16 | INR | 16 | ENM SECURE POWER
WO-11227875 |  | 2023-09-11 14:10 | 2023-09-13 |  | 2023-09-08 02:51 | APC Symmetra LX 16kVA N+1 Tower Frame, 220/230/240V or 380/400/415V | SYAF16KI | SYAF16KI | QD0740180874 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-08 | 2023-09-13 10:34 | No | Contract | Central Board of Excise & Customs-CBEC | Piramal Chambers 9th Floor Jijibhoy Lane Lalbaug null | Mumbai | 400012 | Maharashtra | India FS West1 HBN CSP_United Solutions Mumbai | Rohan Kamble United Solutions Mumbai | UNITED SOLUTIONS - MUMBAI | Preventive Maintenance has been done. Check all parameter are ok. Check power module and battery module working ok condition not found issue. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-13 10:40 |  |  | 18 | INR | 18 | ENM SECURE POWER
WO-11227878 |  | 2023-09-12 10:10 | 2023-09-02 |  | 2023-09-08 02:51 | APC Symmetra RM 4kVA Scalable to 6kVA N+1 220-240V | SYH4K6RMI | SYH4K6RMI | QD0826360017 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-08 | 2023-09-12 15:15 | No | Contract | Central Board of Excise & Customs-CBEC | Kendriya Bhavan Gadkari Chowk Old Mumbai Agra Road null | Nashik | 423502 | Maharashtra | India FS West1 HBN CSP_RACCA INFOTECH PVT LTD Nasik | Nitin Aher RACCA INFOTECH PVT LTD Nasik | Racca Infotech Pvt Ltd | Preventive Maintenance Done. UPS & Battery Working Ok | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-12 18:50 |  |  | 6 | INR | 6 | ENM SECURE POWER
WO-11227880 |  | 2023-09-12 11:36 | 2023-09-02 |  | 2023-09-08 02:51 | APC Symmetra LX 16kVA N+1 Ext. Run Tower Frame, 220/230/240V or 380/400/415V | SYAF16KXR9I | SYAF16KXR9I | QD0827260114 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-08 | 2023-09-16 20:24 | No | Contract | Central Board of Excise & Customs-CBEC | Jawaharlal Nehru Custom House (JNCH) ? Uran null | Uran | 410206 | Maharashtra | India FS West1 HBN CSP_Mahavir Sys Power Pvt Ltd Vashi | Sanju Chauthmol_Mahavir Sys Power Pvt Ltd Vashi | Mahavir Sys Power Pvt Ltd -Vashi | Engineer had done the PM of ups at customer site and found that out of6 battery module 4qty battery module is showing Low capacity and heating issue ups is shifting to bypass mode | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-16 20:28 |  |  | 43 | INR | 43 | ENM SECURE POWER
WO-11227892 |  | 2023-09-11 14:24 | 2023-09-02 |  | 2023-09-08 02:53 | SYA12K16RMI | SYA12K16RMI | SYA12K16RMI | QD0913160060 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-08 | 2023-09-15 11:47 | No | Contract | Central Board of Excise & Customs-CBEC | Central GST and Central Excise Division Building, Shri Ram Colony, Haidergarh Road, Barabanki null | Barabanki | 225001 | Uttar Pradesh | India FS North2 HBN CSP Shriddha Power Solutions Pvt Ltd Lucknow | Anand Tiwari_Shriddha Power Solutions Pvt Ltd Lucknow | Shriddha Power Solutions Pvt. Ltd | FSE visited the site and done the PM. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-16 11:53 |  |  | 45 | INR | 45 | ENM SECURE POWER
WO-11227893 |  | 2023-09-11 11:41 | 2023-09-02 |  | 2023-09-08 02:53 | APC Symmetra LX 12kVA Scalable to 16kVA N+1 Rack-mount, 220/230/240V or 380/400/ | SYA12K16RMI | SYA12K16RMI | QD0824160097 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-08 | 2023-09-14 14:39 | No | Contract | Central Board of Excise & Customs-CBEC | 202 Wing A C G O Complex II Kamla Nehru Nagar null | Ghaziabad | 201206 | Uttar Pradesh | India FS North2 HBN CSP JDM Technologies Pvt Ltd Gaziabad | Rakesh Rathor JDM Technologies Pvt. Ltd Gaziabad | JDM Power Technologies | PM service done ,ups working ok | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-14 14:40 |  |  | 0 | INR | 0 | ENM SECURE POWER
WO-11227894 |  | 2023-09-11 11:40 | 2023-09-02 |  | 2023-09-08 02:53 | APC Symmetra LX 16kVA N+1 Ext. Run Tower Frame, 220/230/240V or 380/400/415V | SYAF16KXR9I | SYAF16KXR9I | QD0826360008 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-08 | 2023-09-14 14:44 | No | Contract | Central Board of Excise & Customs-CBEC | 202 Wing A C G O Complex II Kamla Nehru Nagar null | Ghaziabad | 201206 | Uttar Pradesh | India FS North2 HBN CSP JDM Technologies Pvt Ltd Gaziabad | Rakesh Rathor JDM Technologies Pvt. Ltd Gaziabad | JDM Power Technologies | PM service done ,ups working ok | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-14 14:51 |  |  | 0 | INR | 0 | ENM SECURE POWER
WO-11227895 |  | 2023-09-11 12:26 | 2023-09-02 |  | 2023-09-08 02:54 | APC Symmetra LX 16kVA N+1 Ext. Run Tower Frame, 220/230/240V or 380/400/415V | SYAF16KXR9I | SYAF16KXR9I | QD0826360370 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-08 | 2023-09-14 16:36 | No | Contract | Central Board of Excise & Customs-CBEC | No 38 MG Marg Civil Lines Allahabad HO null | Allahabad | 211002 | Uttar Pradesh | India FS North2 HBN CSP Sun Power Systems Varanasi | Aman Gupta Sun Power Systems Varanasi | Sun Power Systems | PM has been done. UPS working fine. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-14 16:39 |  |  | 132 | INR | 132 | ENM SECURE POWER
WO-11227904 |  | 2023-09-25 10:21 | 2023-09-02 |  | 2023-09-08 02:55 | APC SYMMETRA LX 16kVA N+1 Rack-mount Frame, 220/230/240V OR 380/400/415V | SYAF16KRMI | SYAF16KRMI | QD1046260114 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-08 | 2023-09-25 17:07 | No | Contract | Central Board of Excise & Customs-CBEC | Systems Manager ICES Custom House Beach Road null | Kakinada | 533007 | Andhra Pradesh | India FS South3 HBN CSP SatyaveniS LaserComputers Kakinada | G.Sai Kumar LaserComputers Kakinada | Laser Computers-Kakinada- Hyderabad | VISITED THE SITE UPS MAINS MODE ONLY BATTREY MODE TESTED UPS CHARGING VOLTAGE O/C NOW PM DONE | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-25 17:11 |  |  | 15 | INR | 15 | ENM SECURE POWER
WO-11227907 |  | 2023-09-20 14:53 | 2023-09-02 |  | 2023-09-08 02:56 | APC Symmetra LX 16kVA N+1 Ext. Run Tower Frame 220/230/240V or 380/400/415V | SYAF16KXR9I | SYAF16KXR9I | QD1538160064 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-08 | 2023-09-20 15:00 | No | Contract | Central Board of Excise & Customs-CBEC | House NBR 10-3-301 to 303, 2nd Floor, Serene Heights, Humayun Nagar, Masab Tank null | Hyderabad | 500028 | Telangana | India FS South3 HBN CSP CENTRALDATASYSTEMS HYDERABAD | Nagesh CENTRALDATASYSTEMS HYDERABAD | Central Data Systems Pvt Ltd | checked ups on battery mode for 20 min with 15% load found batteries are weak visited site checked input output and battery voltages all power modules are working fine found 2bm are failed 3 modules are weak condition total 7 bm available ups pm activity done ups working normal. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-20 15:08 |  |  | 13 | INR | 13 | ENM SECURE POWER
WO-11227908 |  | 2023-09-11 13:04 | 2023-09-11 |  | 2023-09-08 02:56 | SYA8K16IXR | SYA8K16IXR | SYA8K16IXR | AD1713120650 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-08 | 2023-09-12 12:02 | No | Contract | Central Board of Excise & Customs-CBEC | Nehru Place and 14-15, Farm Bhawan, Nehru Place null | Delhi | 110019 | Delhi | India FS North1 HBN CSP HITEK BUSINESS SYSTEMS PVT LTD Delhi | Mangal M_Hitek Business Systems New Delhi | Hitek Business Systems Pvt Ltd | Engineer this site UPS PM done UPS working ok | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-12 12:13 |  |  | 15 | INR | 15 | ENM SECURE POWER
WO-11227925 |  | 2023-09-20 12:31 | 2023-09-27 |  | 2023-09-08 02:59 | SURT10000XLI-CC | SURT10000XLI-CC | SURT10000XLI-CC | NS0826001620 | Preventive Maintenance/Regular Preventive Maintenance/Preventive Maintenance | 2023-09-08 | 2023-09-27 10:30 | No | Contract | Metropolitan Stock Exchange of India Ltd. | 205(A), 2nd floor, Piramal Agastya Corporate Park, Kamani Junction, LBS Road, Kurla (West) null | Mumbai | 400070 | Maharashtra | India FS West1 HBN CSP_United Solutions Mumbai | Rohan Kamble United Solutions Mumbai | UNITED SOLUTIONS - MUMBAI | Online PPM has been done. Check all parameter are ok no found fault. UPS working good. | Preventive Maintenance | Regular Preventive Maintenance | 10- Closed | 2023-09-27 10:36 |  |  | 11 | INR | 11 | ENM SECURE POWER
WO-11228357 | 103877838 | 2023-09-08 11:23 | 2023-09-08 |  | 2023-09-08 09:06 | Leonardo EV,DX,R407c,EC Fan,TDAV1321A,Downflow With Heater & Humidifier & With D | TDAV1321AN007 | TDAV1321AN007 | NUCW4721 | AMC P: Outdoor fan issue S: AMC | 2023-09-08 | 2023-09-08 21:45 | No | Contract | optum global solutions india pvt ltd | SEZ Unit, Site -2, Pheonix Infocity Private Limited | hyderabad | 500034 | Telangana | India FS South3 Cooling CSP ERIC HVAC SYSTEM Hyderabad | Samir Prasad ERIC HVAC SYSTEM Hyderabad | ERIC HVAC SYSTEM | Condensor fan is not working so we have replaced a new condensor fan now the unit is working in normal condition. | Repair |  | 8- Service Completed | 2023-09-08 18:19 |  |  | 30 | INR | 30 | ENM SECURE POWER
WO-11173257 | 103595760 | 2023-09-01 10:47 | 2023-08-28 |  | 2023-08-28 16:26 | A9N2P32C | A9N2P32C | A9N2P32C |  | A9N2P32C Sr : DD-2023-W04-7-11 Pole output missing | 2023-08-28 | 2023-09-04 13:10 | No | Warranty | Shivam electricals | 1d 66 A ground floor , NIT faridabad | faridabad | 121001 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mcb found phase missing, Hence faulty replaced . A9N2P32C - 1 nos Email : shivam_elec@yahoo.com | Repair |  | 9- Service Validated | 2023-09-05 11:13 |  |  | 45 | INR | 45 | ENM HOME DISTRIBUTION
WO-11229330 | 103882630 | 2023-09-08 13:53 | 2023-09-08 |  | 2023-09-08 12:36 | Amico 3 TrR407cDownflow with Heater & Hum. | SDA0351AN002 | SDA0351AN002 | C21922008772 | DOP : AMC P : Outdoor fan problem S : AMC | 2023-09-08 | 2023-09-09 09:46 | No | Contract | Kuantum Paper Limited | Saila Khurd, Railway Road, Railway Road | Hoshiarpur | 146000 | Punjab | India FS North2 Cooling CSP Freezeotech Airconditioning & Refrigeration GZB | Abhishek Sharma Freezeotech Airconditioning & Refrigeration Chandigarh | Freezeotech Refrigeartion & Air Conditioning Corporation | We visited the site and found Condenser fan faulty we replaced it now unit is working ok | Repair |  | 10- Closed | 2023-09-09 09:49 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two persons is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 105 | INR | 105 | ENM SECURE POWER
WO-11176985 | 103598988 | 2023-08-29 11:07 | 2023-08-29 |  | 2023-08-29 09:48 | A9N26948 | A9N26948 | A9N26948 |  | Company Name & Complete Address with pin code - Where product is installed FABTECH INDIA. No.5 & assessment # 24,manjunatha industrial area behind of janapriya apartment , mahadeshwara nagar ,herohalli sunkadakatte main road Viswaneedam post/Bangalore-560 091 Contact Person at Site : Name & Mobile No. Kumar A Mo:-8310773491 / 9845044691 PH:- 080 29557226 Alternate Mobile No : Contact Person at Site - Email Address** Product Issue Type (Please select from drop down of column C-9) Are you ready to troubleshoot the issue remotely ? Yes/NO. If Yes, Our technical support engineer will call back to troubleshoot the issue remotely. No Defective Product Model/Part No (Pls refer FAQ sheet ) A9N26948 -1 NO defective and not working properly Nature of Defect* - Defects Video and Photographs Shutdown availability if applicable Photograph of product where Serial No/Batch Code or Date of Manufacturing printed - Please refer FAQ sheet to find the Batch code details on the products BB-2022-W40-1 | 2023-08-29 | 2023-09-13 10:13 | No | Warranty | FABTECH INDIA | No.5 & assessment # 24, manjunatha industrial area behind of janapriya apartment , mahadeshwara nagar , herohalli sunkadakatte main road Viswaneedam post | Bangalore | 560091 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Swamy HJ_P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | Inspected and found below mentioned 1)Ref:A9N26948 S/N:BB - 2022 = 2 No'S, shunt trip dolly free issue. Hence we will give same new shunt trip warranty replacement ASAP. | Repair |  | 9- Service Validated | 2023-09-13 10:15 |  |  | 11 | INR | 11 | ENM HOME DISTRIBUTION
WO-11177056 | 103617714 | 2023-08-31 09:14 | 2023-09-02 | Validated By Prashant | 2023-08-29 10:29 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Customer need visit on Saturday Wiser door bell--1 no Invoice : 02/04/2022--SEI Not operating properly Wiser door bell--1 no Invoice : 02/04/2022--SEI Not operating properly Site : Ashok Towers, 3002, BabaSahib Ambedkar Marg, Parel Mumbai 400001 Mr.Hemant : 9867554478 9820419300 | 2023-08-29 | 2023-09-02 17:00 | No | Warranty | Mr. Hemant | Ashok Towers, A 3007, BabaSahib Ambedkar Marg, Parel null | Mumbai | 400001 | Maharashtra | India FS ED&I CSP West Team S K SERVICES Mumbai | Ganesh Tati_S K SERVICES Mumbai | S.K. Services (10237) | We Visited Site IH100WFVDP-2Nos Smart Door Bell Operating Ok My Phone But Customer Phone Devices Not Showing We Add Devices Now Operating Ok We Solved & Closed | Repair |  | 9- Service Validated | 2023-09-02 18:37 |  |  | 18 | INR | 18 | ENM HOME DISTRIBUTION
WO-11181291 | 103650483 | 2023-08-30 14:00 | 2023-08-30 |  | 2023-08-30 09:20 | IN8486/32>SZ-OS | IN8486/32>SZ-OS | IN8486/32>SZ-OS |  | Model : 32 amp Zencelo--1 no Invoice : Kumar electric--3 month back Not operating | 2023-08-30 | 2023-09-01 10:20 | No | Warranty | Sharad | 254, Rajouri Apartment opp:- Maypuri Bus Depot Mayapuri | Delhi | 110064 | Delhi | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the switches and found switches have stuck issue, We replace the faulty switches with new. | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-02 10:21 |  |  | 38 | INR | 38 | ENM HOME DISTRIBUTION
WO-11181300 | 103634715 | 2023-08-31 14:47 | 2023-08-30 |  | 2023-08-30 09:34 | IH14000100 | IH14000100 | IH14000100 |  | Immediate technician visit, automation not working: Mr. Manav Dhawan, Ambala Wiser home automation is not working at customer site. According to customer all relays stopped working. The lights of his house is unable to operate with switch and mobile. Kindly consider this as a special emergency case and arrange an immediate technician visit. The details of customer and copy of bill is attached below. 1. Customer Name : Mr. Manav Dhawan 2. Customer Address : House no - 91, Model Town , ambala city, 134003 3. Installation Type : Done 4. Product : A) Wiser Home Automation Relay 4 channel : 05 No Gateway: 01 5. Contact Number : +91 89299 99998 6. Site Status: Automation Not working Invoice : Prakash Electricals--12 July 2022 | 2023-08-30 | 2023-09-05 14:55 | No | Warranty | Mr. Manav | House No-91, Model Town,Nr Prshuram Temple, | Ambala | 134003 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Ram Ashish Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the 4 channel relay found no communication issue. Hence faulty replaced. IH14000100 - 5 Nos. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-05 15:03 |  |  | 55 | INR | 55 | ENM HOME DISTRIBUTION
WO-11181335 | 103651192 | 2023-09-01 11:36 | 2023-08-30 |  | 2023-08-30 10:11 | UNSMTSTART2M_WE | UNSMTSTART2M_WE | UNSMTSTART2M_WE |  | Model : Unica pure Fan regulator--2 nos Invoice : 2 months--Padmavati Sales Not operating properly Model : Unica pure Fan regulator--2 nos Invoice : 2 months--Padmavati Sales Not operating properly Site : Plot No-170, Kesar Nagar, Mohana Mandi Road, Nr Kesar Choraha Jaipur Raj 302029 Mr.Tilak Raj Chabda : 9983148147 | 2023-08-30 | 2023-09-07 16:19 | No | Warranty | Tilak Raj Chabda | Plot No-170, Kesar Nagar, Mohana Mandi Road, Nr Kesar Choraha | Jaipur | 302029 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | Checked the fan regulator found step variation issue, Hence faulty replaced. UNSMTSTART2M_WE - 2 nos Email : id not provided by customer. | Repair |  | 9- Service Validated | 2023-09-07 16:21 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11229687 |  | 2023-09-09 14:18 | 2023-09-09 |  | 2023-09-08 14:41 | TDCVQ | TDCVQ | TDCVQ | C21845000497 | PM | 2023-09-08 | 2023-09-25 15:23 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 15:26 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11229717 |  | 2023-09-09 14:21 | 2023-09-09 |  | 2023-09-08 14:46 | TDCVQ | TDCVQ | TDCVQ | C21845003726 | PM | 2023-09-08 | 2023-09-25 15:29 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 15:32 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11183485 | 103660105 | 2023-09-04 20:06 | 2023-08-30 | Validated By Prashant | 2023-08-30 15:05 | IN8486_20_SZ | IN8486_20_SZ | IN8486_20_SZ |  | IN8486/20 Invoice : 22 Aug 2023 Not operating IN8486/20 Invoice : 22 Aug 2023 Not operating Divya Shukla F-1403, Godrej The Trees, Vikhroli (east) Off Eastern Express Highway MUMBAI, Maharashtra, 400079 India T: 9833603825 | 2023-08-30 | 2023-09-05 12:29 | No | Warranty | Divya Shukla | F-1403, Godrej The Trees, Vikhroli (east) Off Eastern Express Highway | MUMBAI | 400079 | Maharashtra | India FS ED&I CSP West Team S K SERVICES Mumbai | Ganesh Tati_S K SERVICES Mumbai | S.K. Services (10237) | We Visited the site Product Ref No- IN8486/20-1Nos Serial No - 171532 We check the material 20A DP Switch is properly not operating because of terminal contact is loose the connection problem We repair the product take action properly tight now operating ok. | Repair |  | 9- Service Validated | 2023-09-05 12:30 |  |  | 10 | INR | 10 | ENM HOME DISTRIBUTION
WO-11229695 |  | 2023-09-09 14:15 | 2023-09-09 |  | 2023-09-08 14:42 | TDCVQ | TDCVQ | TDCVQ | C21845000493 | PM | 2023-09-08 | 2023-09-25 15:16 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 15:18 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11229711 |  | 2023-09-09 14:20 | 2023-09-09 |  | 2023-09-08 14:44 | TDCVQ | TDCVQ | TDCVQ | C21845000496 | PM | 2023-09-08 | 2023-09-25 15:27 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 15:29 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11229715 |  | 2023-09-09 12:17 | 2023-09-09 |  | 2023-09-08 14:45 | TDCVQ | TDCVQ | TDCVQ | C21839004198 | PM | 2023-09-08 | 2023-09-25 14:25 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 14:27 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11229720 |  | 2023-09-09 14:16 | 2023-09-09 |  | 2023-09-08 14:47 | TDCVQ | TDCVQ | TDCVQ | C21845002953 | PM | 2023-09-08 | 2023-09-25 15:19 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 15:22 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11229722 |  | 2023-09-09 14:00 | 2023-09-09 |  | 2023-09-08 14:48 | PRODUCT UNIFLAIR LEONARDO CHW LEO EV CW TDCV4300 R3G630 FAN 2WAY PIBCV WITHOUT H | TDCVQ | TDCVQ | C21905009025 | PM | 2023-09-08 | 2023-09-25 14:28 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 14:30 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11188102 | 103691260 | 2023-09-01 11:31 | 2023-09-01 | Validated By Prashant | 2023-08-31 14:55 | IN8408HC(SZ)-A | IN8408HC(SZ)-A | IN8408HC(SZ)-A |  | Complaint from Arham Electric site. Add- Viraj Tower, Pokharan Rd Number 2, near Bethany Hospital and, Devdaya Nagar, Thane West, Thane, Maharashtra 400606 Issue. PRODUCT - IN8408HC(SZ) CONTACT NO. - 9833454557 9008371775---26.12.2022 | 2023-08-31 | 2023-09-08 16:28 | No | Warranty | Pin Kumar | Viraj Tower, Pokharan Rd Number 2, near Bethany Hospital and, Devdaya Nagar, Thane West | Thane | 400606 | Maharashtra | India FS ED&I CSP West Team S K SERVICES Mumbai | Ganesh Tati_S K SERVICES Mumbai | S.K. Services (10237) | We Visited Site Zencelo Cover Plates Colour Shades Diffrent Dark Shades 2021 Batches IN8401C(SZ)-5Nos, IN8402C(SZ)-6Nos, IN8404C(SZ)-3Nos, IN8406C(SZ)-11Nos, IN8408HC(SZ)-2Nos, IN84012C(SZ)-2Nos Light Shades 2022 Batches IN8402C(SZ)-5Nos,IN8403C(SZ)-7Nos, IN8406C(SZ)-12Nos, IN8408HC(SZ)-15Nos Escalated To Schneider | Repair |  | 9- Service Validated | 2023-09-12 16:28 | =S= Consig Fill up 226019005 |  | 16 | INR | 16 | ENM HOME DISTRIBUTION
WO-11229724 |  | 2023-09-09 14:10 | 2023-09-09 |  | 2023-09-08 14:49 | TDCVQ | TDCVQ | TDCVQ | C21842003785 | PM | 2023-09-08 | 2023-09-25 14:34 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 14:35 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11188363 | 103686189 | 2023-09-01 20:22 | 2023-09-01 | Validated By Prashant | 2023-08-31 16:50 | E8432/2-OS | E8432/2-OS | E8432/2-OS |  | COMPLAINT E8432/2-OS :- 1 NOS NOT WORKING Dear All, Laxmi Raheja, 4 Hari Bhavan, 4th floor, Peddar road, Next to villa Theresa school, Mumbai 400026, Contact # 9820660265 Bill # 1351 Dt:- 14.07.2022 | 2023-08-31 | 2023-09-01 18:30 | No | Warranty | Laxmi Raheja | 4 Hari Bhavan, 4th floor, Peddar road, Next to villa Theresa school | Mumbai | 400026 | Maharashtra | India FS ED&I CSP West Team S K SERVICES Mumbai | Ganesh Tati_S K SERVICES Mumbai | S.K. Services (10237) | We Visited Site Zencelo British 2 Gang 2 Way Switch is 1Nos Not Operating So Inside Direct Contact So Dolly Free We Open Thw Switch Inside Dolly Operating Now Operating Ok We Solved & Closed The Complaint | Repair |  | 9- Service Validated | 2023-09-01 20:43 |  |  | 28 | INR | 28 | ENM HOME DISTRIBUTION
WO-11229726 |  | 2023-09-09 14:13 | 2023-09-09 |  | 2023-09-08 14:50 | PRODUCT UNIFLAIR LEONARDO CHW LEO EV CW TDCV4300 R3G630 FAN 2WAY PIBCV WITHOUT H | TDCVQ | TDCVQ | C21905009419 | PM | 2023-09-08 | 2023-09-25 14:38 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 14:40 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11188390 | 103693703 | 2023-08-31 19:57 | 2023-08-31 |  | 2023-08-31 16:59 | A9N4P63C | A9N4P63C | A9N4P63C |  | #COMPLAIN LETTER COMPANY NAME - Ahmedabad Electric Corporation ADDRESS- 1492 MAHADEV NO KHANCHO, MAMUNAYAK, POLE,GANDHI ROAD,AHMEDABAD Gujarat - 380001, India CON NUM- +91 98248 65283 ?MCB house--2 May 2023 CATALOG NUM SERIAL NUM PROBLEM A9N4P63C 9631455 POLE PROBLEM | 2023-08-31 | 2023-09-01 12:59 | No | Warranty | JD Sales Corporation | 1492/2, Mahadev No Khacho, Mamu Nayaki Pole, Gandhi Road, | Ahmedabad | 380001 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | Parthiv Patel JKS Ahmedabad | JKS Engineering Co. | visited & check mcb on off not working, physically ok so give one time replacemtnt | Repair |  | 9- Service Validated | 2023-09-04 15:59 | =S= Consig Fill up 226014217 |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11229731 |  | 2023-09-09 14:03 | 2023-09-09 |  | 2023-09-08 14:51 | PRODUCT UNIFLAIR LEONARDO CHW LEO EV CW TDCV4300 R3G630 FAN 2WAY PIBCV WITHOUT H | TDCVQ | TDCVQ | C21905009024 | PM | 2023-09-08 | 2023-09-25 14:31 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 14:33 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11191385 | 103716778 | 2023-09-01 22:23 | 2023-09-01 |  | 2023-09-01 09:36 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | IH100WFVDP Smart Doorbell VDP door bell--1 no Invoice : Amazon---12 July 2022 P: SD card not showing , bell notification not coming IH100WFVDP Smart Doorbell VDP door bell--1 no Invoice : Amazon---12 July 2022 P: SD card not showing , bell notification not coming Site:- Tower A 2504 Nikoo Homes 2 Bharitya city Bangalore 560064 9871789955--Sajith Email id:- sajith.venugopal@gmail.com | 2023-09-01 | 2023-09-04 12:33 | No | Warranty | Sajith Sajith | Tower A 2504 Nikoo Homes 2 Bharitya city | Bangalore | 560064 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | C Gunasekaran_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported vdp, the problem found was in app, vdp sd card removed, due to internal issue. so we had replaced new and checked found working ok thru live video and bell button. the same shown to the customer. | Repair |  | 9- Service Validated | 2023-09-04 19:51 |  |  | 20 | INR | 20 | ENM HOME DISTRIBUTION
WO-11229732 |  | 2023-09-09 14:12 | 2023-09-09 |  | 2023-09-08 14:52 | TDCVQ | TDCVQ | TDCVQ | C21844002460 | PM | 2023-09-08 | 2023-09-25 14:36 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 14:38 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11191505 | 103717570 | 2023-09-01 11:14 | 2023-09-01 | NA | 2023-09-01 10:35 | IN8401_N | IN8401_N | IN8401_N |  | Zencelo switches--10 nos Not operating Zencelo switches--10 nos Not operating Invoice : Hamunth Electrical--Aug 2023 Site : 1, Paikpara Row, Kolkata , 700037 Mr.Santosh Lal : 9333181818 | 2023-09-01 | 2023-09-04 01:45 | No | Warranty | Santosh Lal | 1, Paikpara Row | Kolkata | 700037 | West Bengal | India FS ED&I CSP East Team B.D Electroservices Kolkata | KOUSHIK MONDAL_B.D Electroservices Kolkata | B.D Electroservices(500017330) | We close this complain and we will do the physically work 06.09.2023 | Repair |  | 9- Service Validated | 2023-09-04 13:42 |  |  | 20 | INR | 20 | ENM HOME DISTRIBUTION
WO-11229737 |  | 2023-09-09 12:03 | 2023-09-09 |  | 2023-09-08 14:53 | PRODUCT UNIFLAIR LEONARDO CHW LEO EV CW TDCV4300 R3G630 FAN 2WAY PIBCV WITHOUT H | TDCVQ | TDCVQ | C21905009420 | PM | 2023-09-08 | 2023-09-25 14:13 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 14:15 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11192785 | 103718459 | 2023-09-01 12:56 | 2023-09-01 | Switch not operating | 2023-09-01 11:49 | U201SPM/1>B00-OS | U201SPM/1>B00-OS | U201SPM/1>B00-OS |  | Please Issue complaint no 1. Name of Customer: Castel Royale 2. Site Address: - Castel Royale Tower No 7, Sr No 186 to 190, Bopodi Pune 411020 3. Name of contact person at site :- Mr. Nilesh Gajmal 4. Contact Phone / Mob. No: -9881229776 5. Defective product details:- U201SPM/1>B00-OS - 01 qty 6. Product Make:-Schneider Electric 7. Nature of Defect: This Switch not operating properly 8. Shutdown availability if applicable :nil 9. Serial No: or DOM of - TV2022-48 | 2023-09-01 | 2023-09-01 16:44 | No | Warranty | Nilesh Gajmal | Castel Royale Tower No 7 Flat No G1-902 Tower No 7 Sr No 186 to 190, Bopodi | Pune | 411020 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Sachin Jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the Switch not operating. this switch already removed by customer. we taken continuity by multi meter not getting continuity. this problem observed in switch. It's needs to be replaced. Required material : U201SPM/1>B00-OS -01 nos | Repair |  | 9- Service Validated | 2023-09-01 16:44 | =S= Consig Fill up 226023150 |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11229739 |  | 2023-09-09 12:09 | 2023-09-09 |  | 2023-09-08 14:54 | PRODUCT UNIFLAIR LEONARDO CHW LEO EV CW TDCV4300 R3G630 FAN 2WAY PIBCV VALVE WIT | TDCVQ | TDCVQ | C21905021008 | PM | 2023-09-08 | 2023-09-25 14:16 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 14:17 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11193566 | 103720030 | 2023-09-04 15:23 | 2023-09-01 |  | 2023-09-01 12:28 | A9N4P63C | A9N4P63C | A9N4P63C |  | Model : A9n4p63c 4p 63amp Nuisance Tripping Sr no : D2204 Model : A9n4p63c 4p 63amp Nuisance Tripping Sr no : D2204 Site : Plot No-54, Sururpur Industrial Area, Gali No-9B, Faridabad Haryana 121004 Mr.CM Savri: 9310135623 | 2023-09-01 | 2023-09-04 15:27 | No | Warranty | CM Savri | Plot No-54, Sururpur Industrial Area, Gali No-9B | Faridabad | 121004 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mcb found dolly free due to high duting on , Hence no replacement given to customer . Email : id not provided by customer . | Repair |  | 9- Service Validated | 2023-09-04 15:32 |  |  | 45 | INR | 45 | ENM HOME DISTRIBUTION
WO-11229758 |  | 2023-09-09 12:00 | 2023-09-09 |  | 2023-09-08 14:59 | PRODUCT UNIFLAIR LEONARDO CHW LEO EV CW TDCV4300 R3G630 FAN 2WAY PIBCV WITHOUT H | TDCVQ | TDCVQ | C21843007934 | PM | 2023-09-08 | 2023-09-25 14:07 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 14:09 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11194844 | 103724704 | 2023-09-02 10:54 | 2023-09-01 |  | 2023-09-01 15:02 | A9KR11240 | A9KR11240 | A9KR11240 |  | A9KR11240 Sr : DD-2022-W31-2-2 Dolly free A9KR11240 Sr : DD-2022-W31-2-2 Dolly free Site : Ambaince Mall, Vasant kunj Delhi Amit : 9795052241 | 2023-09-01 | 2023-09-11 13:54 | No | Warranty | Ambiance Mall | vasant kunj null | Delhi | 110070 | Delhi | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the Rccb found phase missing, Hence faulty replaced. A9N16204 - 1 nos Email : id not provided by customer . | Repair |  | 9- Service Validated | 2023-09-12 14:00 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11229760 |  | 2023-09-09 11:56 | 2023-09-09 |  | 2023-09-08 15:00 | PRODUCT UNIFLAIR LEONARDO CHW LEO EV CW TDCV4300 R3G630 FAN 2WAY PIBCV VALVE WIT | TDCVQ | TDCVQ | C21905021009 | PM | 2023-09-08 | 2023-09-25 14:03 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 14:06 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11200553 | 103740651 | 2023-09-02 16:24 | 2023-09-04 | Validated By Prashant | 2023-09-02 12:05 | IN84SFR_N | IN84SFR_N | IN84SFR_N |  | Service team kindly do the analysis for failure of this product . Fan regulator IN84SFR Amazon---29/12023 I had shared Amazon invoice with Mr Ganesh Tati your technician on 23rd August and images of blown up fan regulator on 24th August 23 Repeatedly, there are instances of fan regulator failure. Kindly please look into the matter. On changing the fan regulator, when started working, so there was not any short circuit in the fan that could have damaged the fan regulator Dear Madhuri, kindly coordinate with your team and have Ganesh Tati your technician who has come to our house twice to collect the regulator for analysis | 2023-09-02 | 2023-09-05 17:00 | No | Warranty | Dhiren C Gandhi | 1203 , Odyssey 1 , Hiranandani Gardens , Powai | Mumbai | 400076 | Maharashtra | India FS ED&I CSP West Team S K SERVICES Mumbai | Ganesh Tati_S K SERVICES Mumbai | S.K. Services (10237) | We Visited Site Fan Regulator is Not Operating So Burnt Out issue Inside Capacitor Liquid Out Side We Replace The Product From Our Stock Closed The Complaint | Repair |  | 9- Service Validated | 2023-09-05 22:25 | =S= Consig Fill up 226023046 |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-11229764 |  | 2023-09-09 12:13 | 2023-09-09 |  | 2023-09-08 15:03 | PRODUCT UNIFLAIR LEONARDO CHW LEO EV CW TDCV4300 R3G630 FAN 2WAY PIBCV WITHOUT H | TDCVQ | TDCVQ | C21845000495 | PM | 2023-09-08 | 2023-09-25 14:21 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 14:25 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11229766 |  | 2023-09-09 12:11 | 2023-09-09 |  | 2023-09-08 15:04 | PRODUCT UNIFLAIR LEONARDO CHW LEO EV CW TDCV4300 R3G630 FAN 2WAY PIBCV WITHOUT H | TDCVQ | TDCVQ | C21844002458 | PM | 2023-09-08 | 2023-09-25 14:18 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 14:20 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11200779 | 103742786 | 2023-09-02 18:24 | 2023-09-02 | Validated By Prashant | 2023-09-02 17:25 | X1001WH_N | X1001WH_N | X1001WH_N |  | COMPLAINT X1001 :- 1 NOS NOT WORKING AAKY1232 :- 1 NOS NOT WORKING IN8401 :- 5 NOS NOT WORKING IN8402 :- 1 NOS NOT WORKING IN8486/32 :- 1 NOS NOT WORKING IN8481/16 :- 1 NOS NOT WORKING Dear All, LITE - WAY ELECTRICALS, B-1, PALAN SOJPAL BLDG., 58/60 S.K. BOLE ROAD, DADAR (W),MUMBAI :- 400 028 CONTACT # 98215 76753 BILL # 208 DT:- 15.04.2023 BILL # 4146 DT :- 31.01.2023 | 2023-09-02 | 2023-09-09 17:19 | No | Warranty | LITE - WAY ELECTRICALS | B-1, PALAN SOJPAL BLDG., 58/60 S.K. BOLE ROAD, DADAR (W) null | MUMBAI | 400028 | Maharashtra | India FS ED&I CSP West Team S K SERVICES Mumbai | Ganesh Tati_S K SERVICES Mumbai | S.K. Services (10237) | We Visited the site Product Ref No:-IN8401-2Nos, IN8402-1Nos, IN8486/32-1Nos, AAKX1232-1Nos. Serial No:- 23093-2Nos, 21035L,21174L,17115L We check the material 6A 1Way switch And 6A 2Way Switch is properly not operating because of stuck issue. 32A DP switch is also stuck issue. We replace the product book ZVO. Replacement done. | Repair |  | 9- Service Validated | 2023-09-09 17:21 | =S= Consig Fill up 226031654 |  | 20 | INR | 20 | ENM HOME DISTRIBUTION
WO-11229769 |  | 2023-09-09 11:50 | 2023-09-09 |  | 2023-09-08 15:04 | PRODUCT UNIFLAIR LEONARDO CHW LEO EV CW TDCV4300 R3G630 FAN 2WAY PIBCV VALVE WIT | TDCVQ | TDCVQ | C21905021007 | PM | 2023-09-08 | 2023-09-25 13:52 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 13:55 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11210692 | 103756043 | 2023-09-04 12:48 | 2023-09-04 | VDP is not working | 2023-09-04 12:10 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Smart Doorbell SERVICE at Mr. Ashish Singh - Project V Uptown by Tatvam Constructions Product to be Serviced: Wiser Smart Doorbell ( IH100WFVDP ) ?> Quantity = 1. Project Name: V-Uptown by Tatvam Constructions Location: Ravet Kiwale Link Road, Kiwale Pune Near Jai Ganesh Lawns, Pimpri Chinchwad 412101. Contact: Mr. Ashish Singh ? 7905858979. Radhika Cables--16 Nov 2022 | 2023-09-04 | 2023-09-04 17:34 | No | Warranty | V Uptown by Tatvam Constructions | Ravet Kiwale Link Road, Kiwale Pune Near Jai Ganesh Lawns, Pimpri Chinchwad | Pune | 412101 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Kunal jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the VDP is not working. we observed this VDP is not showing video footage. and showing SD card removed. so this problem is not Repairable. So VDP Needs to be replaced. we installed the new VDP but new VDP are problem is observed it's not showing SD card. So both VDP are replaced.. Required Material : IH100WFVDP - 02 nos | Repair |  | 9- Service Validated | 2023-09-05 10:31 | =S= Consig Fill up 226002085 |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11229855 |  | 2023-09-09 11:54 | 2023-09-09 |  | 2023-09-08 15:52 | PRODUCT UNIFLAIR LEONARDO CHW LEO EV CW TDCV4300 R3G630 FAN 2WAY PIBCV WITHOUT H | TDCVQ | TDCVQ | C21907011439 | PM | 2023-09-08 | 2023-09-25 14:00 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 14:02 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11210736 | 103755767 | 2023-09-04 12:51 | 2023-09-04 | VDP is not working | 2023-09-04 12:18 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Smart Doorbell SERVICE at Project V Uptown by Tatvam Constructions Product to be Serviced: Wiser Smart Doorbell ( IH100WFVDP ) ?> Quantity = 1. Radhika Cables--16 Nov 2022 Project Name: V-Uptown by Tatvam Constructions Location: Ravet Kiwale Link Road, Kiwale Pune Near Jai Ganesh Lawns, Pimpri Chinchwad 412101. Contact: Mr. Amol Dhanokar - 9137599917. | 2023-09-04 | 2023-09-04 17:33 | No | Warranty | V Uptown by Tatvam Constructions | Ravet Kiwale Link Road, Kiwale Pune Near Jai Ganesh Lawns, Pimpri Chinchwad | Pune | 412101 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Kunal jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the VDP is not working. we observed this VDP is not showing video footage. and showing SD card removed. so this problem is not Repairable. So VDP Needs to be replaced. Required Material : IH100WFVDP - 01 nos | Repair |  | 9- Service Validated | 2023-09-05 10:28 | =S= Consig Fill up 226026385 |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11229859 |  | 2023-09-09 11:49 | 2023-09-09 |  | 2023-09-08 15:53 | PRODUCT UNIFLAIR LEONARDO CHW LEO EV CW TDCV4300 R3G630 FAN 2WAY PIBCV WITHOUT H | TDCVQ | TDCVQ | C21908016349 | PM | 2023-09-08 | 2023-09-25 13:44 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 13:51 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11210754 | 103756342 | 2023-09-04 12:53 | 2023-09-04 | VDP is not working | 2023-09-04 12:26 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Smart Doorbell SERVICE at Mr. Niteen Surwase - Project V Uptown by Tatvam Constructions Product to be Serviced: Wiser Smart Doorbell ( IH100WFVDP ) ?> Quantity = 1. Radhika Cables--16 Nov 2022 Project Name: V-Uptown by Tatvam Constructions Location: Ravet Kiwale Link Road, Kiwale Pune Near Jai Ganesh Lawns, Pimpri Chinchwad 412101. Contact: Mr. Niteen Surwase ? 9960255409. | 2023-09-04 | 2023-09-04 18:00 | No | Warranty | V Uptown by Tatvam Constructions | Ravet Kiwale Link Road, Kiwale Pune Near Jai Ganesh Lawns, Pimpri Chinchwad | Pune | 412101 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Sachin Jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the VDP is not working. we observed this VDP is not showing video footage. and showing SD card removed. so this problem is not Repairable. So VDP Needs to be replaced. Required Material : IH100WFVDP - 01 nos | Repair |  | 9- Service Validated | 2023-09-05 10:32 | =S= Consig Fill up 226030330 |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11229860 |  | 2023-09-09 11:52 | 2023-09-09 |  | 2023-09-08 15:55 | PRODUCT UNIFLAIR LEONARDO CHW LEO EV CW TDCV4300 R3G630 FAN 2WAY PIBCV WITHOUT H | TDCVQ | TDCVQ | C21845000499 | PM | 2023-09-08 | 2023-09-25 13:55 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 13:59 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11210762 | 103755694 | 2023-09-04 12:55 | 2023-09-04 | VDP is not working | 2023-09-04 12:30 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Smart Doorbell SERVICES at Project V Uptown by Tatvam Constructions Wiser Smart Doorbell ( IH100WFVDP ) ?> Quantity = 1. Radhika Cables--16 Nov 2022 Project Name: V-Uptown by Tatvam Constructions Location: Ravet Kiwale Link Road, Kiwale Pune Near Jai Ganesh Lawns, Pimpri Chinchwad 412101. Contact: Mr. Sarang Ghodke - 98906 66882. | 2023-09-04 | 2023-09-04 17:09 | No | Warranty | SARANG GHODKE | V-UPTOWN, B-402 ,Near Jai Ganesh Lawns,kiwale | Pune | 412101 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Sachin Jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the VDP is not working. we observed this VDP is not showing video footage. and showing SD card removed. so this problem is not Repairable. So VDP Needs to be replaced. Required Material : IH100WFVDP - 01 nos | Repair |  | 9- Service Validated | 2023-09-05 10:30 | =S= Consig Fill up 226023149 |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11229864 |  | 2023-09-09 12:01 | 2023-09-09 |  | 2023-09-08 15:56 | PRODUCT UNIFLAIR LEONARDO CHW LEO EV CW TDCV4300 R3G630 FAN 2WAY PIBCV VALVE WIT | TDCVQ | TDCVQ | C21905021010 | PM | 2023-09-08 | 2023-09-25 14:10 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 14:11 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11210947 | 103760015 | 2023-09-04 14:07 | 2023-09-04 |  | 2023-09-04 13:12 | A9N1P25C | A9N1P25C | A9N1P25C |  | A9N1P25C Srn : DD 2022-W13-2-6 Knob Free / Mechanism Issue A9N1P25C Srn : DD 2022-W13-2-6 Knob Free / Mechanism Issue Mr Suraj # 324, Hans Market Near Aggarwal Dharamshala Fatehabad Sirsa ,Haryana. 125050 Mr. Suraj / Vikram Kumar 7015104966 | 2023-09-04 | 2023-09-04 14:10 | No | Warranty | Suraj sharma | # 324, Hans Market Fatehabad | Sirsa | 125050 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Rakesh Kumar Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the mcb found phase missing and 4 channel relay found not communication issue and EDLT switch found colour faded from upper side button is broken. Hence faulty replaced. A9N1P25C - 1 Nos. IH14000100 - 3 Nos. 5085EDLW-PW - 1 Nos. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-04 16:26 |  |  | 255 | INR | 255 | ENM HOME DISTRIBUTION
WO-11229873 |  | 2023-09-09 16:14 | 2023-09-09 |  | 2023-09-08 15:58 | TDCVQ | TDCVQ | TDCVQ | C21927004248 | PM | 2023-09-08 | 2023-09-25 17:06 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 17:08 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11210985 | 103760656 | 2023-09-05 12:02 | 2023-09-04 |  | 2023-09-04 13:30 | A9N18369 | A9N18369 | A9N18369 |  | Model :A9N18369 Invoice : JK Electrical--3-4 days back Tripping issue Model :A9N18369 Invoice : JK Electrical--3-4 days back Tripping issue Site : Vardhman Taxo Fab VPO Shahpur, Nr Jawara Railway crossing Haryana Ajay Kashyap : 7404308655 | 2023-09-04 | 2023-09-05 12:53 | No | Warranty | Ajay Kashyap | Vardhman Taxo Fab VPO Shahpur, Nr Jawara Railway crossing | Panipat | 133206 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Ram Ashish Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the mcb found R phase burnt due to loose termination. Hence no replacement given to customer. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-05 13:00 |  |  | 165 | INR | 165 | ENM HOME DISTRIBUTION
WO-11229880 |  | 2023-09-09 16:16 | 2023-09-09 |  | 2023-09-08 16:00 | TDCVQ | TDCVQ | TDCVQ | C21917009986 | PM | 2023-09-08 | 2023-09-25 17:09 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 17:11 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11211116 | 103760226 | 2023-09-04 16:12 | 2023-09-04 | Part order request validated by Mr.Chandrakant Panchal sir | 2023-09-04 14:09 | P1001_N | P1001_N | P1001_N |  | PLEASE REGISTER COMPLAINT Name of Customer SUDHIR BHARGAVA Site Address PLOT NO. 23 SEC. A2, SCH. NO. 136, IDA NIRJANPUR INDORE Name of contact person at site SUDHIR BHARGAVA Contact Phone / Mob. No: 9826289259 Defective products details LIVIA Product Make SCHNEIDER Nature of Defect NOT WORKING Shutdown availability if applicable Warranty status IN WARRANTY Commissioned / Installed date JAN.2023 Serial No: or DOM of the product Vijay Shanti Electricals--28 Jan 2023 | 2023-09-04 | 2023-09-04 18:51 | No | Warranty | SUDHIR BHARGAVA | PLOT NO. 23 SEC. A2, SCH. NO. 136, IDA NIRJANPUR | INDORE | 452001 | Madhya Pradesh | India FS ED&I CSP West Team ABR Technical Service Indore | Mayank Patidar_ABR Technical Services Indore | ABR Technical Services (9574) | Reached at site as per customer 1 nos socket burnt . then we checked and found 1 nos socket (P2106) burnt out. then we checked voltage and found L&N-245VAC, L&E-168VAC, and N&E-74.6VAC. socket burnt may be due to loose termination. benefits of doubt and customer satisfaction we recommend to replace 1 nos socket. | Repair |  | 9- Service Validated | 2023-09-05 14:53 | =S= Consig Fill up 226022248 |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-11229881 |  | 2023-09-09 16:12 | 2023-09-09 |  | 2023-09-08 16:01 | TDCVQ | TDCVQ | TDCVQ | C21927000255 | PM | 2023-09-08 | 2023-09-25 17:03 | No | Contract | Netmagic Solutions Pvt Ltd | Unit No: 4, Ground Floor, Navigator Building, International Techpark Whitefield Road | Bangalore | 560066 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 17:06 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11211266 | 103755912 | 2023-09-04 16:45 | 2023-09-04 | VDP is not working | 2023-09-04 15:14 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Smart Doorbell SERVICE at Mr. Sach GM - Project V Uptown by Tatvam Constructions Product to be Serviced: Wiser Smart Doorbell ( IH100WFVDP ) ?> Quantity = 1. Radhika Cables--16 Nov 2022 Project Name: V-Uptown by Tatvam Constructions Location: Ravet Kiwale Link Road, Kiwale Pune Near Jai Ganesh Lawns, Pimpri Chinchwad 412101. Contact: Mr. Sach GM ? 9923837468. | 2023-09-04 | 2023-09-04 16:53 | No | Warranty | V Uptown by Tatvam Constructions | Ravet Kiwale Link Road, Kiwale Pune Near Jai Ganesh Lawns, Pimpri Chinchwad | Pune | 412101 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Samadhan S_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the VDP is not working. it's getting offline. we observed wi fi router password is change by customer , so that's why problem is occurred . we reset the Password and set up again. and then taken operation it's working found ok. | Repair |  | 9- Service Validated | 2023-09-04 16:57 |  |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11229893 |  | 2023-09-09 16:08 | 2023-09-09 |  | 2023-09-08 16:08 | TDCVQ | TDCVQ | TDCVQ | C21927002481 | PM | 2023-09-08 | 2023-09-25 16:54 | No | Contract | Netmagic Solutions Pvt Ltd | Unit No: 4, Ground Floor, Navigator Building, International Techpark Whitefield Road | Bangalore | 560066 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 16:56 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11229895 |  | 2023-09-09 16:06 | 2023-09-09 |  | 2023-09-08 16:10 | TDCVQ | TDCVQ | TDCVQ | C21927000257 | PM | 2023-09-08 | 2023-09-25 16:51 | No | Contract | Netmagic Solutions Pvt Ltd | Unit No: 4, Ground Floor, Navigator Building, International Techpark Whitefield Road | Bangalore | 560066 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 16:53 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11211674 | 103767798 | 2023-09-04 17:47 | 2023-09-04 |  | 2023-09-04 17:21 | X1001WH_N | X1001WH_N | X1001WH_N |  | Opale switches--2 nos 24/10/2022 invoice date Opale switches--2 nos 24/10/2022 invoice date ADD : FMD OFFICE SOBHA CITY DWARKA EXPRESSWAY GURUGRAM HARYANA 122017 Mail Id : fm.scg@sobha.com M.No : 9810210704 | 2023-09-04 | 2023-09-13 14:07 | No | Warranty | Manoj Kumar | FMD OFFICE SOBHA CITY DWARKA EXPRESSWAY GURUGRAM | Gurgaon | 122017 | Haryana | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the switches and found switches have stuck issue and breaking issue, We replace the faulty switches with new. | Repair |  | 9- Service Validated | 2023-09-13 18:01 |  |  | 53 | INR | 53 | ENM HOME DISTRIBUTION
WO-11229899 |  | 2023-09-09 16:10 | 2023-09-09 |  | 2023-09-08 16:11 | TDCVQ | TDCVQ | TDCVQ | C21927004247 | PM | 2023-09-08 | 2023-09-25 17:00 | No | Contract | Netmagic Solutions Pvt Ltd | Unit No: 4, Ground Floor, Navigator Building, International Techpark Whitefield Road | Bangalore | 560066 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 17:02 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11229903 |  | 2023-09-09 16:09 | 2023-09-09 |  | 2023-09-08 16:12 | TDCVQ | TDCVQ | TDCVQ | C21920000381 | PM | 2023-09-08 | 2023-09-25 16:57 | No | Contract | Netmagic Solutions Pvt Ltd | Unit No: 4, Ground Floor, Navigator Building, International Techpark Whitefield Road | Bangalore | 560066 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 17:00 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11316227 | 104279717 | 2023-09-27 12:01 | 2023-09-27 |  | 2023-09-27 11:14 | ATV340D30N4E | ATV340D30N4E | ATV340D30N4E |  | Dear Sir Greetings from ACE AUTOMATIONS...! Please note that the above drives are not working properly at our customer site , kindly register our complaint & resolve the issue at the earliest. MODEL - ATV340D30N4E UNDER WARRANTY Drive Serial No. - 405030088225113030 FAULT: VFD NOT WORKING - NO DISPLAY Address - Larsen & Toubro Construction , Mahsr project T3 project TSMF opp.Diamond Vill - Sadanapura Anand Gujarat 388320 Contact person - Mr. Chanakaya # 9950388268 Regards Varun Manuja ¦ Ace Automations ¦ +91 9818101899 aceautomations.com ¦ ace.automations@gmail.com ---------- Forwarded message ---------From: PURCHASE AP CRANES <purchase@apcranes.com>Date: Tue, 26 Sept 2023 at 14:30Subject: Dive complaintTo: ace automations <ace.automations@gmail.com>, Ravi PRAKASH <ravi.prakash@se.com> NOTE FOR VENDOR: Way bills as per norms may be generated by your office/transporter indicating delivery address as mentioned on Purchase Order. Penalties/ fine imposed by authority on account of wrong information or address on way to vendor scope. Kindly ensure proper dispatch documents being under your total control. For any further clarification, may please contact undersigned. SAURABH JAINPROCUREMENT HEAD email: purchase@apcranes.comphone: +91-7891088803 ext 208 ¦ mobile: + 91-9799403403 A.P CRANES PVT. LTD, B185 A&B KEHRANI INDUSTRIAL AREA BHIWADI(RJ)-301019 www.apcranes.com Notice: Information contained and transmitted by this email is confidential and proprietary to AP. Information contained is for use only by the recipients. If you are not the intended recipient, you are notified that dissemination or copying of this email or its contents therein is strictly prohibited; you are requested to delete this email immediately and notify the sender. 22439:66344 | 2023-09-27 | 2023-09-29 09:58 | No | Warranty | Larsen & Toubro Construction | Mahsr project T3 project TSMF opp.Diamond Vill - Sadanapura null | Anand | 388320 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Nijesh Patel_Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product physically observed ok. check the igbt and rectifer ok also pa+ and pb obserevd ok. give a run command but drive goes in current limittion. so check the meter thermal error 50.2 and current limitation 92.2 so change 75.0 and trial takne but problem remain same . so check the motor brake and release so the motor brake and trial taken working satisfactory. problem due to the motor brake not properly realease. runtime 9.9h no of state 3476 no any product problem observed. | Repair |  | 8- Service Completed | 2023-09-29 09:59 |  |  | 80 | INR | 80 | Industrial Automation Ops
WO-11215769 | 103787908 | 2023-09-05 17:03 | 2023-09-05 | Validated By Prashant | 2023-09-05 13:50 | IN8401_16_SP | IN8401_16_SP | IN8401_16_SP |  | DOP: 26/4/2023 Zencelo Switches Qty:2 nos P: Not operating | 2023-09-05 | 2023-09-06 15:21 | No | Warranty | Kishore Shah | Flat 301 3rd floor 5th Avenue Building NS Pole 5 JVPD Scheme Pale west | Mumbai | 400049 | Maharashtra | India FS ED&I CSP West Team S K SERVICES Mumbai | Ganesh Tati_S K SERVICES Mumbai | S.K. Services (10237) | We visited the site Product Ref No :-IN8486/32(BZ)-1Nos Serial No:-2303 We check the material 32A DP switch is properly not operating We solve the locking problem. | Repair |  | 9- Service Validated | 2023-09-06 15:21 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11229905 |  | 2023-09-09 16:02 | 2023-09-09 |  | 2023-09-08 16:13 | TDCVQ | TDCVQ | TDCVQ | C21927006050 | PM | 2023-09-08 | 2023-09-25 16:45 | No | Contract | Netmagic Solutions Pvt Ltd | Unit No: 4, Ground Floor, Navigator Building, International Techpark Whitefield Road | Bangalore | 560066 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 16:47 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11216083 | 103791549 | 2023-09-05 16:15 | 2023-09-05 |  | 2023-09-05 15:41 | P1001_N | P1001_N | P1001_N |  | Name of Customer:-Prashant Shah Site Address:-8 Shree Arjav Society Opp Gulmohar Mall, Nr Iskcon Cross Roads, Satellite Ahemdabad PIN CODE:-380015 Name of contact person at site:-Yagnik Contact Phone / Mob. No:-7227899615 Defective product details:-PIN-P216(1 QTY),P1001(1 QTY) Invoice no.:-G00523/23-24(27-JUN-2023) Nature of Defect:-Not getting on and off. | 2023-09-05 | 2023-09-05 17:33 | No | Warranty | Prashant Shah | 8 Shree Arjav Society Satellite | Ahemdabad | 380015 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Mistri Anik Engineering Ahmedabad | Anik Engineering (554) | Visited site and checked the product found physically observed ok. P1181 SR NO : 14202 03 Nos observed physically ok but dolly free. P1001 SR NO : 15234 02 Nos observed ok switch not properly working. IN8486/20 SR NO : 18312 L ok but face cover locking broken. underwarranty so no free replacement. | Repair |  | 9- Service Validated | 2023-09-05 17:34 |  |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11229917 |  | 2023-09-09 16:05 | 2023-09-09 |  | 2023-09-08 16:14 | PRODUCT UNIFLAIR LEONARDO CHW LEO EV CW TDCV4300 R3G630 FAN 2WAY PIBCV WITHOUT H | TDCVQ | TDCVQ | C21931022265 | PM | 2023-09-08 | 2023-09-25 16:48 | No | Contract | Netmagic Solutions Pvt Ltd | Unit No: 4, Ground Floor, Navigator Building, International Techpark Whitefield Road | Bangalore | 560066 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 16:50 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11317247 | 104304218 | 2023-09-28 12:34 | 2023-09-27 |  | 2023-09-27 17:43 | ATV310H075N4E | ATV310H075N4E | ATV310H075N4E |  | Dear Team, Our one of Reputed clients is facing problem in VFDs Run as per following details. 0.75 KW - 01 Nos. VFD Model No. ATV310H075N4E & Sl.No. 8B2233253164 Problem - VFD Display Off & VFD not run (Photo Attached) Please solve the problem as soon as possible. Clients Name & Address :- M/s Shri Ram Solvent Extractions Pvt. Ltd. Kashipur Road, Jaspur (Uttarakhand) Site Contact Person & Contact No.:- Mr. Maruf Khan Mob.7248410008 In case of any query feel free to revert. Abhinav Singh (Mob. -72484-10005) ISO CERTIFIED 9001:2015 KASHIPUR ELECTRICAL ENGG. WORKS 6th. Km. Stone Jaitpur More, Bazpur Road, Kashipur-244713 - Uttarakhand E-Mail : keewcontrol@yahoo.co.in ¦ Web. www.keewcontrol.com ¦ GSTIN - 05AQIPS5523L1ZH Mob. Office : 88688-90004 ¦Technical Query - 72484-10002 ¦ Sale & Purchase - 72484-10003 Accounts - 72484-10004 ¦ Sales & Marketing - 72484-10005 ¦ Automation - 72484-10010 | 2023-09-27 | 2023-09-30 16:28 | No | Warranty | M/s Shri Ram Solvent Extractions Pvt. Ltd. | Kashipur Road, Jaspur null | Udhamsingh Nagar | 244712 | Uttarakhand | India FS ED&I CSP North Team Saffron Automation Delhi | Deepak Pal_Saffron Automation Delhi | Saffron Automation(18001) | Check the drive and found physical condition ok. Check all the input output terminal shorting found ok. Give 3 phase input supply and found drive is power up. But no display saw it. We replace the faulty drive with new. Mail Id. keewcontrol@yahoo.co.in | Repair |  | 8- Service Completed | 2023-09-30 16:31 |  |  | 2 | INR | 2 | Industrial Automation Ops
WO-11216105 | 103790497 | 2023-09-05 17:08 | 2023-09-05 |  | 2023-09-05 15:54 | IH101ZWIFI | IH101ZWIFI | IH101ZWIFI |  | WISER AUTOMATION GATEWAY Name of Customer DR. JANAK.C.PATEL 2 Site Address BILIMORA NEW ATRIK HOSPITAL, 3-SHANTINIKETAN SOCIETY,NEAR ANAVIL WADI, GOHARBAUG-BILIMORA 396321 Prakash Corp--16 may 2022 3 Name of contact person at site DR. JANAK.C.PATEL 4 Contact Phone / Mob. No: 9824113961 5 Defective product details IH101ZWIFI WISER AUTOMATION GATEWAY PROPERLY NOT WORKING 6 Nature of Defect NOT WORKING | 2023-09-05 | 2023-09-09 16:00 | No | Warranty | Janak Patel | 48, Anand nagar Society, College road, Billimora | Navsari | 396321 | Gujarat | India FS ED&I CSP West Team SHIV SAI ELECTRICALS Vapi | Hiral Solanki_SHIV SAI ELECTRICALS VAPI | shivsai electricals | AS PER SITE VISIT WE CHECK THE PRODUCT AND FOUND OK ON VISUAL INSPECTION.THEN WE CHECK INTERNET STATUS AND FOUND OK.THEN WE CONNECTION THE GATEWAY WITH ROUTER AND CHECK FUCTION AND FOUND OK.SO WE CLOSED THE CASE | Repair |  | 9- Service Validated | 2023-09-09 16:02 |  |  | 46 | INR | 46 | ENM HOME DISTRIBUTION
WO-11229919 |  | 2023-09-09 15:58 | 2023-09-09 |  | 2023-09-08 16:15 | TDCVQ | TDCVQ | TDCVQ | C21927006048 | PM | 2023-09-08 | 2023-09-25 16:39 | No | Contract | Netmagic Solutions Pvt Ltd | Unit No: 4, Ground Floor, Navigator Building, International Techpark Whitefield Road | Bangalore | 560066 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 16:42 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11322341 | 104333917 | 2023-09-28 16:34 | 2023-09-28 |  | 2023-09-28 14:58 | ATV310HU15N4E | ATV310HU15N4E | ATV310HU15N4E |  | Dear Sir, Please issue Complaint No. OP Industries, Nakora Road, Bharoliawali, Rania, Sirsa, Haryana. Mr. OP Sharma 9650518877 Email: opsharma871@rediffmail.com Product : ATV310HU15N4E Srn : 8B2148451052 Problem : F020 Fault Unable to run drive Email: opsharma871@rediffmail.com Regards Mukesh Kumar | 2023-09-28 | 2023-09-28 16:36 | No | Warranty | OP Industries | Nakora Road, Bharoliawali, Rania null | Sirsa | 125075 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the MCB & RCCB found dolly free. Hence faulty replaced. EZ9R55463 - 1 Nos. EZ9F76116 - 1 Nos. email : id not provided by the customer. | Repair |  | 8- Service Completed | 2023-09-29 10:15 |  |  | 3 | INR | 3 | Industrial Automation Ops
WO-11216181 | 103793515 | 2023-09-07 12:27 | 2023-09-05 |  | 2023-09-05 16:27 | A9KF71463 | A9KF71463 | A9KF71463 |  | A9KF71463 Invoice : Durga Bhai and Co---25 aug 2023 Screw not opening A9KF71463 Invoice : Durga Bhai and Co---25 aug 2023 Screw not opening Site : H-80, Gali No-8, West Karawal Nagar, delhi 110094 Mr.Munkad Ali(Alam) : 9312729737 Mr.Virender Bist : +919266312516 | 2023-09-05 | 2023-09-07 12:28 | No | Warranty | Munkad Ali | H-80, Gali No-1 , West Karawal nagar | Delhi | 110094 | Delhi | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mcb found phase missing Hence faulty replaced. A9N4P63C - 1 nos Email : id not provided by customer . | Repair |  | 9- Service Validated | 2023-09-07 12:54 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11229921 |  | 2023-09-09 16:00 | 2023-09-09 |  | 2023-09-08 16:16 | TDCVQ | TDCVQ | TDCVQ | C21920000382 | PM | 2023-09-08 | 2023-09-25 16:43 | No | Contract | Netmagic Solutions Pvt Ltd | Unit No: 4, Ground Floor, Navigator Building, International Techpark Whitefield Road | Bangalore | 560066 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 16:44 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11229922 |  | 2023-09-09 15:57 | 2023-09-09 |  | 2023-09-08 16:17 | TDCVQ | TDCVQ | TDCVQ | C21927000256 | PM | 2023-09-08 | 2023-09-25 16:36 | No | Contract | Netmagic Solutions Pvt Ltd | Unit No: 4, Ground Floor, Navigator Building, International Techpark Whitefield Road | Bangalore | 560066 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 16:39 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11229926 |  | 2023-09-09 15:55 | 2023-09-09 |  | 2023-09-08 16:18 | TDCVQ | TDCVQ | TDCVQ | C21927004250 | PM | 2023-09-08 | 2023-09-25 16:34 | No | Contract | Netmagic Solutions Pvt Ltd | Unit No: 4, Ground Floor, Navigator Building, International Techpark Whitefield Road | Bangalore | 560066 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 16:35 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11229928 |  | 2023-09-09 15:53 | 2023-09-09 |  | 2023-09-08 16:19 | TDCVQ | TDCVQ | TDCVQ | C21927000258 | PM | 2023-09-08 | 2023-09-25 16:30 | No | Contract | Netmagic Solutions Pvt Ltd | Unit No: 4, Ground Floor, Navigator Building, International Techpark Whitefield Road | Bangalore | 560066 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 16:33 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11219861 | 103814134 | 2023-09-06 16:30 | 2023-09-06 |  | 2023-09-06 10:48 | A9N3P32C | A9N3P32C | A9N3P32C |  | A9N3p32C DD-2022-W32-5-11 1 Phase missing A9N3p32C DD-2022-W32-5-11 1 Phase missing Site : 121106 Haryana Palwal, Hodal Sarai Khatla Gujrana Road, Nr DCTM College Fibrex Construction Chemical Pvt lTd Mr. Dharmender Rawat : 9991175157 account@fibrexchem.com | 2023-09-06 | 2023-09-12 15:55 | No | Warranty | Dharmender Rawat | Fibrex Construction Chemical ,Hodal Sarai Khatla Gujrana Road, Nr DCTM College | Palwal | 121106 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mcb found phase missing. Hence faulty replaced A9N3P32C - 1 Nos. email : account@fibrexchem.com | Repair |  | 9- Service Validated | 2023-09-12 15:57 |  |  | 90 | INR | 90 | ENM HOME DISTRIBUTION
WO-11229936 |  | 2023-09-09 15:49 | 2023-09-09 |  | 2023-09-08 16:20 | PRODUCT UNIFLAIR LEONARDO CHW LEO EV CW TDCV4300 R3G630 FAN 2WAY PIBCV WITHOUT H | TDCVQ | TDCVQ | C21931022266 | PM | 2023-09-08 | 2023-09-25 16:06 | No | Contract | Netmagic Solutions Pvt Ltd | Unit No: 4, Ground Floor, Navigator Building, International Techpark Whitefield Road | Bangalore | 560066 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 16:08 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11229938 |  | 2023-09-09 15:48 | 2023-09-09 |  | 2023-09-08 16:21 | TDCVQ | TDCVQ | TDCVQ | C21927004246 | PM | 2023-09-08 | 2023-09-25 16:03 | No | Contract | Netmagic Solutions Pvt Ltd | Unit No: 4, Ground Floor, Navigator Building, International Techpark Whitefield Road | Bangalore | 560066 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 16:05 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11221376 | 103815051 | 2023-09-06 19:59 | 2023-09-06 | Validated By Prashant | 2023-09-06 12:57 | IN84SFR_N | IN84SFR_N | IN84SFR_N |  | Re: FAN regulator IN84SFR Amazon--29 Jan 2023 Fan regulator sr no 20495L purchased from Amazon per invoice attached gave SPEED variation in spam of 15 Days of fitting. At night it stopped working am in the morning it started. Please depute your person and replace the same Your company seriously need to look into this matter of product quality - Zencello is a lousy product for sure. Your Technican is also claiming quality is going to get improved but when. Totally 7 regulators were purchased in the month of January 2023 Following is invoice for 3 and there is One or two more invoices which we attach later as we need to download through desktop. | 2023-09-06 | 2023-09-09 19:00 | No | Warranty | Dhiren C Gandhi | 1203 , Odyssey 1 , Hiranandani Gardens , Powai | Mumbai | 400076 | Maharashtra | India FS ED&I CSP West Team S K SERVICES Mumbai | Ganesh Tati_S K SERVICES Mumbai | S.K. Services (10237) | We Visited Site Fan Regulator is Properly Not Operating So 1 Step To 4 Step Speed Variation Prblem We Raise The ZVO Next Visit We Replace The Product Closed The Complaint | Repair |  | 9- Service Validated | 2023-09-09 21:14 | =S= Consig Fill up 226035361 |  | 5 | INR | 5 | ENM HOME DISTRIBUTION
WO-11229941 |  | 2023-09-09 15:51 | 2023-09-09 |  | 2023-09-08 16:22 | TDCVQ | TDCVQ | TDCVQ | C21927004249 | PM | 2023-09-08 | 2023-09-25 16:09 | No | Contract | Netmagic IT Services Pvt. Ltd | 88/A, SVR Platinum, Next to KSSIDC Building, Electronic city , Phase 1, Bangalore 88/A, S V R Platinum, Adjacent to K S S I D C Complex, Electronic City, Phase 1 | Bangalore | 560100 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 16:11 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11229948 |  | 2023-09-09 15:40 | 2023-09-09 |  | 2023-09-08 16:24 | PRODUCT UNIFLAIR LEONARDO CHW LEO EV CW TDCV4300 R3G630 FAN 2WAY PIBCV WITHOUT H | TDCVQ | TDCVQ | C21908016348 | PM | 2023-09-08 | 2023-09-25 15:52 | No | Contract | Netmagic Solutions Pvt Ltd | Unit No: 4, Ground Floor, Navigator Building, International Techpark Whitefield Road | Bangalore | 560066 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 15:54 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11221799 | 103821147 | 2023-09-06 17:14 | 2023-09-06 | Validated By Prashant | 2023-09-06 15:05 | CSS54E_WE | CSS54E_WE | CSS54E_WE |  | Faulty Sensor Kindy arrange for an engineer at below site for faulty sensor (CSS54E_WE). Nylon Electric--1 April 2023 Details : Mr Dinesh 2202, Pinacolo NX, Beverly Park, RBK School lane, Mira Bhyander, Mira road East. Thane 401107. M: 9167036274 | 2023-09-06 | 2023-09-12 15:47 | No | Warranty | Mr Dinesh | 2202, Pinacolo NX, Beverly Park, RBK School lane, Mira Bhyander, Mira road East | Thane | 401107 | Maharashtra | India FS ED&I CSP West Team S K SERVICES Mumbai | Ganesh Tati_S K SERVICES Mumbai | S.K. Services (10237) | We Visited the site Product Ref No:-CSS54E_WE-1Nos Serial No:-2111 We check the sensor found time schedule issue We replace the product book ZVO. The replacement is done. | Repair |  | 9- Service Validated | 2023-09-12 16:02 | =S= Consig Fill up 226034115 |  | 20 | INR | 20 | ENM HOME DISTRIBUTION
WO-11229951 |  | 2023-09-09 15:46 | 2023-09-09 |  | 2023-09-08 16:25 | PRODUCT UNIFLAIR LEONARDO CHW LEO EV CW TDCV4300 R3G630 FAN 2WAY PIBCV VALVE WIT | TDCVQ | TDCVQ | C21913002054 | PM | 2023-09-08 | 2023-09-25 15:58 | No | Contract | Netmagic Solutions Pvt Ltd | Unit No: 4, Ground Floor, Navigator Building, International Techpark Whitefield Road | Bangalore | 560066 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 16:02 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11221925 | 103824029 | 2023-09-06 18:06 | 2023-09-06 | Free replacement of RCCB | 2023-09-06 16:02 | EZ9R35240 | EZ9R35240 | EZ9R35240 |  | EZ9R35240--1 no dd-2021-W42-2-2 Not operating RCCB EZ9R35240--1 no dd-2021-W42-2-2 Not operating Site : Khumansinh Vaghela Dist Patan, Tal Sankheshwar Village Moti Chandur Gujarat 9624532288 | 2023-09-06 | 2023-09-08 10:27 | No | Warranty | Khumansinh Vaghela | Tal Sankheshwar Village Moti Chandur | Patan | 384265 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Ritesh Prajapati_Anik Engineering Ahmedabad | Anik Engineering (554) | Checked the RCCB, Observed dolly free. Free replacement | Repair |  | 9- Service Validated | 2023-09-08 11:04 | =S= Consig Fill up 226035362 |  | 120 | INR | 120 | ENM HOME DISTRIBUTION
WO-11229957 |  | 2023-09-09 15:36 | 2023-09-09 |  | 2023-09-08 16:26 | PRODUCT UNIFLAIR LEONARDO CHW LEO EV CW TDCV4300 R3G630 FAN 2WAY PIBCV WITHOUT H | TDCVQ | TDCVQ | C21908000359 | PM | 2023-09-08 | 2023-09-25 15:45 | No | Contract | Netmagic Solutions Pvt Ltd | Unit No: 4, Ground Floor, Navigator Building, International Techpark Whitefield Road | Bangalore | 560066 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 15:48 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11221941 | 103822521 | 2023-09-07 10:25 | 2023-09-06 | VDP Installation | 2023-09-06 16:22 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Regarding Wiser Smart Doorbell Installation at Bhaktamar - Project Shanti Samarth Please arrange a technician for Installation of Following Components at below Location: Product to be Installed: Wiser Smart Doorbell ( IH100WFVDP ) ?> Quantity = 2. ?New India Cables---21 April 2023 Installation at Following Flat Nos: Mr. Naren Varpe ? 9763262425 -> Flat No: 202. Address: Mate Nagar, Vadgaon Sheri, Opp Jodhpur Sweets, Kharadi, Pune 411014 | 2023-09-06 | 2023-09-08 10:22 | No | Commercial Action - Sales | Naren Varpe | Flat No: 202,Mate Nagar, Vadgaon Sheri, Opp Jodhpur Sweets, Kharadi | Pune | 411014 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Kunal jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the VDP location and Power Supply and wiring work is not completed. then we suggest the customer complete the work and then we will attained the compliant. | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-08 10:26 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11229958 |  | 2023-09-09 15:38 | 2023-09-09 |  | 2023-09-08 16:27 | PRODUCT UNIFLAIR LEONARDO CHW LEO EV CW TDCV4300 R3G630 FAN 2WAY PIBCV VALVE WIT | TDCVQ | TDCVQ | C21913002052 | PM | 2023-09-08 | 2023-09-25 15:49 | No | Contract | Netmagic Solutions Pvt Ltd | Unit No: 4, Ground Floor, Navigator Building, International Techpark Whitefield Road | Bangalore | 560066 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 15:51 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11221948 | 103824565 | 2023-09-07 10:31 | 2023-09-06 | VDP Installation | 2023-09-06 16:26 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Regarding Wiser Smart Doorbell Installation at Bhaktamar - Project Shanti Samarth Please arrange a technician for Installation of Following Components at below Location: Product to be Installed: Wiser Smart Doorbell ( IH100WFVDP ) ?> Quantity = 2. ?New India Cables---21 April 2023 Mr. Rajendra Gawade ? 9970122276 -> Flat No: 402. Address: Mate Nagar, Vadgaon Sheri, Opp Jodhpur Sweets, Kharadi, Pune 411014. | 2023-09-06 | 2023-09-08 10:27 | No | Commercial Action - Sales | Rajendra Gawade | Flat No: 402,Mate Nagar, Vadgaon Sheri, Opp Jodhpur Sweets, Kharadi | Pune | 411014 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Kunal jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the VDP location and Power Supply and wiring work is not completed. then we suggest the customer complete the work and then we will attained the compliant. | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-08 10:30 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11229963 |  | 2023-09-09 15:31 | 2023-09-09 |  | 2023-09-08 16:28 | PRODUCT UNIFLAIR LEONARDO CHW LEO EV CW TDCV4300 R3G630 FAN 2WAY PIBCV VALVE WIT | TDCVQ | TDCVQ | C21913002053 | PM | 2023-09-08 | 2023-09-25 15:42 | No | Contract | Netmagic IT Services Pvt. Ltd | 88/A, SVR Platinum, Next to KSSIDC Building, Electronic city , Phase 1, Bangalore 88/A, S V R Platinum, Adjacent to K S S I D C Complex, Electronic City, Phase 1 | Bangalore | 560100 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 15:45 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11229161 | 103878503 | 2023-09-08 11:52 | 2023-09-08 | Wiser Installation | 2023-09-08 11:20 | IH14000100 | IH14000100 | IH14000100 |  | Regarding Wiser Home Automation Installation on SATURDAY 9th SEP at Multicolor Packaging Industries Please arrange a technician for Installation of Following Components at below Location: Product to be Installed: Wiser IP Gateway ?> Quantity = 2. Wiser 4 Channel Relay -> Quantity = 7. New India Cables--7 Sep 2023 Firm Name: Multicolor Packaging Industries Contact Person: Mr. Shyam Deshmukh Contact: 9766861260 Address: Row House No. A-111, Project Vaarivana, Gat No. 109, 111, 123 & 291, 292 Adhe & Urse, Ambewadi, Sable Farm, Maharashtra 410506. INSTALLATION DATE: 9th SEP 2023. | 2023-09-08 | 2023-09-09 16:41 | No | Commercial Action - Sales | Shyam Deshmukh | Row House No. A-111, Project Vaarivana, Gat No. 109, 111, 123 & 291, 292 Adhe & Urse | KOLHAPUR | 410506 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Kunal jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | We installed the wiser Relay - 07 nos and gateway - 02 nos. first of all we set up the gateway and make a proper wiring for relay installing. we installed all product of switch board and then taken on/off operation it's working found ok. | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-09 16:45 |  |  | 50 | INR | 50 | ENM HOME DISTRIBUTION
WO-11229965 |  | 2023-09-09 15:44 | 2023-09-09 |  | 2023-09-08 16:29 | TDCVQ | TDCVQ | TDCVQ | C21927006049 | PM | 2023-09-08 | 2023-09-25 15:55 | No | Contract | Netmagic IT Services Pvt. Ltd | 88/A, SVR Platinum, Next to KSSIDC Building, Electronic city , Phase 1, Bangalore 88/A, S V R Platinum, Adjacent to K S S I D C Complex, Electronic City, Phase 1 | Bangalore | 560100 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 15:57 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11229386 | 103883505 | 2023-09-08 14:20 | 2023-09-08 |  | 2023-09-08 12:55 | P3200_N | P3200_N | P3200_N |  | Livia regulator--1 no P3200 Invoice : 6 months back--Rajshri Electrcials Not operating | 2023-09-08 | 2023-09-08 18:01 | No | Warranty | Papu Kumar | Shri Amerjyoti Electricals, No 6/1,1st cross, Huriopet | Bengaluru | 560053 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Nagaraja G_P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | Inspected and found below mentioned 1)Ref:P3200 Livia S/N: 19343 = 1 No, Livia fan regulator ON/OFF working issue. Hence we will give same new fan regulator warranty replacement on good will basis. We have replaced the fan regulator from our PSK stock. | Repair |  | 9- Service Validated | 2023-09-08 18:04 |  |  | 10 | INR | 10 | ENM HOME DISTRIBUTION
WO-11229968 |  | 2023-09-09 15:28 | 2023-09-09 |  | 2023-09-08 16:30 | TDCVQ | TDCVQ | TDCVQ | C21937001470 | PM | 2023-09-08 | 2023-09-25 15:33 | No | Contract | Netmagic Solutions Pvt Ltd | Unit No: 4, Ground Floor, Navigator Building, International Techpark Whitefield Road | Bangalore | 560066 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 15:36 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11216302 | 103784086 | 2023-09-07 10:10 | 2023-09-05 |  | 2023-09-05 17:29 | ATV630D90N4Z | ATV630D90N4Z | ATV630D90N4Z | 5.1549e+17 | Site Address PHASE-II, B1-D, SECTOR-81, Block B, Noida, Gautam Buddha Nagar, 201305, Noida Uttar Pradesh, India FW: FW: Schneider VFD sound observed ~Samsung Chennai Plant Warranty certificate attached in case Equipments Name AHU Panel 106 Location : ReComp building VFD serial no.: 515490088213773025 VFD Model no.: Altivar 630 Probelm: VFD sound observed ATV630D90N4Z Ankit K. Gupta +91 9873264234 ankitk.gupta@samsung.com | 2023-09-05 | 2023-09-07 18:20 | No | Warranty | Samsung India Electronics Pvt. Ltd. | P-1, SIPCOT Industrial Complex, Phase-II, Sunguvarchathiram,Sunguvachatram, Kancheepuram District Sriperumpudur | Chennai | 602106 | Tamil Nadu | India FS ED&I CSP South Team Star Automations Chennai | Nobin Balaiah_Star Automations Chennai | Star Automations | Problem reported by customer: VFD getting sound Visited the site and checked the ATV630 physically it was good condition. Checked the input voltage 430V and DC voltage buildup 24VDC , Checked DC between voltage 584V. Dismantle the drive all the PCB was good condition( No flashover or burnt ) not found any abnormality. checked the all the wiring condition inside the VFD all are good condition. Observed no noise from the drive it is a normal sound. Taken all the model number and serial number of drive for install bare data. Finally we closing this case. | Repair |  | 9- Service Validated | 2023-09-07 18:28 |  |  | 150 | INR | 150 | Industrial Automation Ops
WO-11229566 | 103880880 | 2023-09-08 14:45 | 2023-09-08 | Validated By Prashant | 2023-09-08 13:57 | IH14000100 | IH14000100 | IH14000100 |  | Please Register New Complaint 08-09-2023 Name Of Customer Rishabh Ghisulal Jain Site Address Rishabh Ghisulal Jain, 42A1 Lodha world view Lower Parel Mumbai Name Of Contact Person At Site Rishabh Ghisulal Jain Contact Phone / Mob. No: 9920326394 Defective Product Details IH14000100-2Nos, Serial No:-4R230224659831, 4R230224659408 Nature Of Defect Not Working | 2023-09-08 | 2023-09-08 17:50 | No | Warranty | Rishabh Ghisulal Jain | 42A1 Lodha world view Lower Parel | Mumbai | 400013 | Maharashtra | India FS ED&I CSP West Team S K SERVICES Mumbai | Ganesh Tati_S K SERVICES Mumbai | S.K. Services (10237) | We Visited the site Product Ref No:-IH14000100-2Nos Serial No:-4R230224659831, 4R230224659408. We shifted the channel and solve the problem. | Repair |  | 9- Service Validated | 2023-09-08 17:51 |  |  | 20 | INR | 20 | ENM HOME DISTRIBUTION
WO-11229972 |  | 2023-09-09 15:30 | 2023-09-09 |  | 2023-09-08 16:32 | TDCVQ | TDCVQ | TDCVQ | C21938000192 | PM | 2023-09-08 | 2023-09-25 15:39 | No | Contract | Netmagic IT Services Pvt. Ltd | 88/A, SVR Platinum, Next to KSSIDC Building, Electronic city , Phase 1, Bangalore 88/A, S V R Platinum, Adjacent to K S S I D C Complex, Electronic City, Phase 1 | Bangalore | 560100 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-25 15:41 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11247112 | 103958996 | 2023-09-13 10:45 | 2023-09-12 |  | 2023-09-12 13:39 | ATV310HD11N4E | ATV310HD11N4E | ATV310HD11N4E | 8B2323973059 | P:A current path to earth ground has been detected at one or more of the drive output terminals IN-WARRANTY P:A current path to earth ground has been detected at one or more of the drive output terminals F013 7508180022 ATV310HD11N4E 8B2323973059 | 2023-09-12 | 2023-09-13 10:47 | No | Warranty | JW Marriott Hotel | Plot no: 6, Sector 35-B, Dakshin Marg Chandigarh 1600 35 India | Chandigarh | 160035 | Chandigarh | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Vinod Kumar_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the vfd found show's phase missing problem in its output side. Programming issue resolved & now working ok. Hence complaint is closed . email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-13 17:03 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 22 | INR | 22 | Industrial Automation Ops
WO-11230186 | 103892938 | 2023-09-09 10:42 | 2023-09-08 |  | 2023-09-08 17:48 | IN8401_N | IN8401_N | IN8401_N |  | Model : Zencelo switches--25 nos Not operating 30 March 2023---GDS Electricals Model : Zencelo switches--25 nos Not operating 30 March 2023---GDS Electricals Site : PS Esmeralda 12/3, Baliganj Park Road, Kolkata 700019 | 2023-09-08 | 2023-09-13 14:15 | No | Warranty | Debraj banerjee | PS Esmeralda 12/3, Baliganj Park Road | Kolkata | 700019 | West Bengal | India FS ED&I CSP East Team SREYAM SERVICES BHATPARA | AMIT BHATTACHARYA_SREYAM SERVICES BHATPARA | Sreyam Services(8513) | FOUND ZENCELO SWITCH REPACED BY NEW ONE AND DEFFECTIVE MATERIAL IS COLLECTED. | Repair |  | 9- Service Validated | 2023-09-13 14:20 |  |  | 18 | INR | 18 | ENM HOME DISTRIBUTION
WO-11229979 |  | 2023-09-11 13:47 | 2023-09-11 |  | 2023-09-08 16:35 | TDCVQ | TDCVQ | TDCVQ | C21943001693 | PM | 2023-09-08 | 2023-09-27 17:50 | No | Contract | Netmagic Solutions Pvt Ltd | Unit No: 4, Ground Floor, Navigator Building, International Techpark Whitefield Road | Bangalore | 560066 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-27 17:52 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11248041 | 103961778 | 2023-09-13 10:39 | 2023-09-12 |  | 2023-09-12 17:03 | ATV630D15N4 | ATV630D15N4 | ATV630D15N4 | 4005500JM221309046 | FW: Schneider VFD Tripping issues observed~Samsung India Chennai Plant, Case: 103919678, [ thread::md2Y2X5DcrmJzCn7wC3PBT4:: ] 1. Equipments Name AHU Panel 101 Location : ReComp building VFD serial no.: 4005500JM221309046 VFD Model no.: Altivar 630 Probelm: VFD Tripping Samsung Engineering India Pvt. Ltd India SEC I-PJT, Sriperumbudur ,Chennai Plant M : +91 9873264234 Off. Email : ankitk.gupta@samsung.com | 2023-09-12 | 2023-09-15 10:49 | No | Warranty | Samsung India Electronics Pvt. Ltd. | P-1, SIPCOT Industrial Complex, Phase-II, Sunguvarchathiram,Sunguvachatram, Kancheepuram District Sriperumpudur | Chennai | 602106 | Tamil Nadu | India FS ED&I CSP South Team Star Automations Chennai | Nobin Balaiah_Star Automations Chennai | Star Automations | Problem reported by customer : VFD tripping ( DC voltage Over load ) Visit the site checked the drive physically it was working good condition. Checked the input voltage it 380V & output voltage 380 VAC and 24VDC checked build up in control card. The main problem was drive in getting tripping in 40H3 frequency. Checked DC bus voltage it shows 518DC in 30H2 running condition. Checked the motor side all are oaky condition. Checked the all the parameters in the drive. We found some parameter are mismatch as per the application. We changed the parameter are: In ACC & DCC before it was 45H3 & 15 H2 as per the application we changed 80H3 and 80H2 in ACC & DCC. Checked the type of stop its shows ramp. We changed to free wheel stop. Checked the switching frequency it show 2.5Hz its okay. checked the DC adaptation it shows yes it also okay condition. So finally we checked all the parameter and run the drive. We monitor the drive around 2 hrs. no error is displayed. VFD ATV630 75KW was working good no error found. so we recommended to customer to changed the parameter in remaining VFD to reduce the error. So we closed this complaint. Schneider Recommendation: For 75KW, 90KW , 110KW ACC , DCC should be 2.5HZ , type of stop should be free wheel stop . DCC adaptation should be yes. This are parameter to change in the remaining drive all AHU VFD units. | Repair |  | 9- Service Validated | 2023-09-15 10:58 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 180 | INR | 180 | Industrial Automation Ops
WO-11230263 | 103892516 | 2023-09-09 12:22 | 2023-09-08 |  | 2023-09-08 18:17 | E8331FR350_GH_G8 | E8331FR350_GH_G8 | E8331FR350_GH_G8 |  | Complaint Name of Customer KALAVATI WINES Site Address MOTI DAMAN SHOP NO DM C/7 DAMAN 396210 plalu18@yahoo.in Name of contact person at site Mr.Satish Contact Phone / Mob. No: 9664935943 Defective product details E8331FR350_GH_G8 ,E8315_16_WG Nature of Defect NOT WORKING Shutdown availability if applicable No Warranty status yes Commissioned / Installed date Serial No: or DOM of the product Prakash Corp--22 Oct 2022 | 2023-09-08 | 2023-09-09 13:28 | No | Warranty | KALAVATI WINES | SHOP NO DM C/7, MOTI DAMAN null | Daman | 396210 | Dadra and Nagar Haveli | India FS ED&I CSP West Team SHIV SAI ELECTRICALS Vapi | SHIVAM LAD SHIV SAI ELECTRICALS VAPI | shivsai electricals | AS PER SITE VISIT WE CHECK THE PRODUCT AND FOUND OK ON VISUAL INSPECTION.AFTER THAT CHECK THE FAN REGULATOR AND FOUND THE FAN REGULATOR IS STUCK.BOTH PRODUCT IS STUCK.WHEN WE CHECK THE PRODUC WARRNTY STATUS AND FOUND THE PRODUCT IS UNDER WARRNTY NEEDS TO BE REPLACED. | Repair |  | 9- Service Validated | 2023-09-12 13:30 | =S= Consig Fill up 226042692 |  | 18 | INR | 18 | ENM HOME DISTRIBUTION
WO-11229981 |  | 2023-09-11 14:09 | 2023-09-11 |  | 2023-09-08 16:36 | LEO MAXCWTDCV4300AEC FAN2WAY PIBCVW/O H AND H WITH DAMPER DUAL SPLY ATS DUAL SEN | TDCV4300AN002 | TDCV4300AN002 | JK2136000698 | PM | 2023-09-08 | 2023-09-27 18:43 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-27 18:45 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11230275 | 103890836 | 2023-09-11 16:33 | 2023-09-08 |  | 2023-09-08 18:22 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Fwd: Installation Smart Door Bell [ thread::4Q0_b70remiBbIaa_dv0ID4:: ] Pls arrange technician to install SDB wiser. 3*3 box & Wi-Fi is available Deepline Entp--2/9/2023 Jhanduke Bartan Store Main bazaar, Buchho Mandi, 151101 Bathinda Punjab 9988508885 | 2023-09-08 | 2023-09-11 16:35 | No | Commercial Action - Sales | Jhanduke Bartan Store | Main bazaar, Buchho Mandi null | Bathinda | 151101 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Installation done. email : id not provided by the customer. | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-11 16:56 |  |  | 150 | INR | 150 | ENM HOME DISTRIBUTION
WO-11229982 |  | 2023-09-11 14:06 | 2023-09-11 |  | 2023-09-08 16:37 | LEO MAXCWTDCV4300AEC FAN2WAY PIBCVW/O H AND H WITH DAMPER DUAL SPLY ATS DUAL SEN | Uniflair Chilled Water-Cooling Solutions - Room Air Conditioners |  | JK2136000701 | PM | 2023-09-08 | 2023-09-27 18:33 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-27 18:37 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11253063 | 103993889 | 2023-09-13 12:42 | 2023-09-13 | Selector Switch not operating | 2023-09-13 12:13 | 9001KA3 | 9001KA3 | 9001KA3 | A034L728 | FW: Please find attached complaint from Cummins PHP Plant against Schneider Selector switch 9001KS53FB + 9001KA3 + 9001KA2 (Cummins part No. A034L728) ? 02 Qty. P:Total 23 Qty supplied but Cummins found 2 Qty faulty in operations 9001KS53FB + 9001KA3 + 9001KA2 (Cummins part No. A034L728) Cummins India Ltd ? PHP SEZ, Plot No. B-3, SEZ Industrial Area, Village Nandal and Survadi, Tal. Phaltan, Dist: Satara, 410501 Sunil Tambe & 9527174964 9001KS53FB + 9001KA3 + 9001KA2 (Cummins part No. A034L728) Jul-23 | 2023-09-13 | 2023-09-14 10:58 | No | Warranty | Cummins India | Cummins India Limited Power Generation Business Unit plot no.:B2,SEZ Industrial area,Village Nandal & Surwadi Taluka - Phaltan, Dist- Satara -415523 | Pune | 415523 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Swamesh S_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the Selector Switch not operating. checked operation of selector switch at 3 position. all operation found ok. there is no problem observed in product as per function design product operation found ok. | Repair |  | 9- Service Validated | 2023-09-14 11:04 | VIP FSR= No 3. FSR Request: Unavailability of the preferred FSR, need to depute Non VIP FSR(kiran borse). |  | 120 | INR | 120 | Industrial Automation Ops
WO-11234266 | 103909385 | 2023-09-12 11:48 | 2023-09-09 |  | 2023-09-09 12:05 | IN8401(BZ)-A | IN8401(BZ)-A | IN8401(BZ)-A |  | IN8401(BZ) 12no. not working IN8401(BZ) 12no. not working DOM : 21442L SHAKTI KEDIA Kedia House no. 57, Near doon Public School, Sarbahal, Jharsuguda 768201, Odisha 9861555557 | 2023-09-09 | 2023-09-13 13:27 | No | Warranty | SHAKTI KEDIA | Kedia House no. 57, Near doon Public School, Sarbahal | Jharsuguda | 768201 | Odisha | India FS ED&I CSP East Team UNIVERSAL ELECTRIC POWER SOLUTION BHUBANESWAR | RAMESH PRABHAT_UNIVERSAL ELECTRIC POWER SOLUTION BHUBANESWAR | Universal Electric Power Solution(500012032) | material to be booked | Repair |  | 9- Service Validated | 2023-09-16 13:29 |  |  | 364 | INR | 364 | ENM HOME DISTRIBUTION
WO-11229986 |  | 2023-09-11 14:07 | 2023-09-18 |  | 2023-09-08 16:38 | LEO MAXCWTDCV4300AEC FAN2WAY PIBCVW/O H AND H WITH DAMPER DUAL SPLY ATS DUAL SEN | TDCV4300AN002 | TDCV4300AN002 | JK2137000791 | PM | 2023-09-08 | 2023-09-27 18:40 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-27 18:42 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11234323 | 103909709 | 2023-09-09 13:53 | 2023-09-09 | FRee replcement of MCB | 2023-09-09 13:34 | A9N3P63C | A9N3P63C | A9N3P63C |  | #COMPLAIN LETTER COMPANY NAME - Ahmedabad Electric Corporation ADDRESS- 1492 MAHADEV NO KHANCHO, MAMUNAYAK, POLE,GANDHI ROAD,AHMEDABAD Gujarat - 380001, India CON NUM- +91 98248 65283 23 April 2023--MCB center CATALOG NUM SERIAL NUM PROBLEM A9N3P63C 9631355 POLE PROBLEM | 2023-09-09 | 2023-09-11 11:20 | No | Warranty | MCB CENTRE | 1492/2, MAHADEV'S KHANCHO, MAMUNAYAK'S POLE, Nr. MUNICIPAL HOSPITAL, GANDHI ROAD, AHMEDABAD | AHMEDABAD | 380001 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Nijesh Patel_Anik Engineering Ahmedabad | Anik Engineering (554) | visited site and checked the mcb, observed dolly free | Repair |  | 9- Service Validated | 2023-09-11 11:24 | =S= Consig Fill up 226043461 |  | 10 | INR | 10 | ENM HOME DISTRIBUTION
WO-11229989 |  | 2023-09-11 14:01 | 2023-09-11 |  | 2023-09-08 16:40 | LEO MAXCWTDCV4300AEC FAN2WAY PIBCVW/O H AND H WITH DAMPER DUAL SPLY ATS DUAL SEN | Uniflair Chilled Water-Cooling Solutions - Room Air Conditioners |  | JK2136001154 | PM | 2023-09-08 | 2023-09-27 18:06 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-27 18:08 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11230017 |  | 2023-09-11 14:00 | 2023-09-11 |  | 2023-09-08 16:44 | LEO MAXCWTDCV4300AEC FAN2WAY PIBCVW/O H AND H WITH DAMPER DUAL SPLY ATS DUAL SEN | TDCV4300AN002 | TDCV4300AN002 | JK2135005070 | PM | 2023-09-08 | 2023-09-27 18:03 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-27 18:05 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11239964 | 103911932 | 2023-09-11 15:50 | 2023-09-11 |  | 2023-09-11 09:37 | X1001WH_N | X1001WH_N | X1001WH_N |  | Please depute engineer at the site client is facing problam OPALA RANG X1001WH - 45NOS Durga's Switchgear--22 June 2022 GANSHYAM JI SHARAMA NANDPURI JAIPUR MOB 8077446628 | 2023-09-11 | 2023-09-11 17:03 | No | Warranty | GANSHYAM SHARAMA | NANDPURI | JAIPUR | 302001 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Sunny Sharma Sharma Electric Jaipur | Sharma Electric Works | Checked the switch found not working , Hence faulty replaced. X1001WH - 45 nos Email : id not provided by customer | Repair |  | 9- Service Validated | 2023-09-11 17:06 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11230018 |  | 2023-09-11 13:39 | 2023-09-11 |  | 2023-09-08 16:45 | LEO MAXCWTDCV4300AEC FAN2WAY PIBCVW/O H AND H WITH DAMPER DUAL SPLY ATS DUAL SEN | TDCV4300AN002 | TDCV4300AN002 | JK2135005069 | PM | 2023-09-08 | 2023-09-27 17:47 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-27 17:49 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11239982 | 103917709 | 2023-09-11 10:48 | 2023-09-11 | Switches not working | 2023-09-11 09:53 | IN8401_N | IN8401_N | IN8401_N |  | Model: Zencelo 3 nos Invoice : 1 year back Hings Breakage Model: Zencelo 3 nos Invoice : 1 year back Hings Breakage Site : A-404, Isha Sangam , Inside Isha Emral Society, Dibvewadi, Kondhwa road, Market Yard, Pune 411037 Ramakanth Jalan : 9371458887 | 2023-09-11 | 2023-09-12 17:16 | No | Warranty | Ramakanth Jalan | A-404, Isha Sangam , Inside Isha Emral Society, Dibvewadi, Kondhwa road, Market Yard Damodar Society Dibwewadi | Pune | 411037 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Kunal jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the switch found that the Switch is not working it's found broken from inside the board . so this problem is not repairable.So switch Needs to be replaced, Required Material : X1001WH - 02 nos. we arranged the material from our stock and replaced it. on goodwill basis we given the replacement to customer. | Repair |  | 9- Service Validated | 2023-09-12 17:58 | =S= Consig Fill up 226046449 |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11230021 |  | 2023-09-11 14:04 | 2023-09-11 |  | 2023-09-08 16:46 | LEO MAXCWTDCV4300AEC FAN2WAY PIBCVW/O H AND H WITH DAMPER DUAL SPLY ATS DUAL SEN | Uniflair Chilled Water-Cooling Solutions - Room Air Conditioners |  | JK2136001408 | PM | 2023-09-08 | 2023-09-27 18:13 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-27 18:33 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11239995 | 103910839 | 2023-09-11 11:04 | 2023-09-11 | Validated By Prashant | 2023-09-11 10:00 | X1181WH_N | X1181WH_N | X1181WH_N |  | Issue in Opale Switch Operation Nylon Eletric--1 April 2023 Kindly arrange for an engineer on urgent basis at below address for faulty Opale ? X1181WH & X3200WH Address: Mr Parth 201, 2nd Floor, Brij Bhoomi, Above Canara Bank, Vile Parle East. Mumbai Mobile : 9920717107 Purchase : Nylon Electric Corp | 2023-09-11 | 2023-09-11 16:51 | No | Warranty | Mr Parth | 201, 2nd Floor, Brij Bhoomi, Above Canara Bank, Vile Parle East. | Mumbai | 400029 | Maharashtra | India FS ED&I CSP West Team S K SERVICES Mumbai | Ganesh Tati_S K SERVICES Mumbai | S.K. Services (10237) | We Visited Site 32A DP Switches Not Operating So On/Off Operating Side Lock Broken We Replace The Product Closed the Complaint. | Repair |  | 9- Service Validated | 2023-09-11 16:52 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11230026 |  | 2023-09-11 13:58 | 2023-09-11 |  | 2023-09-08 16:47 | LEO MAXCWTDCV4300AEC FAN2WAY PIBCVW/O H AND H WITH DAMPER DUAL SPLY ATS DUAL SEN | TDCV4300AN002 | TDCV4300AN002 | JK2136001410 | PM | 2023-09-08 | 2023-09-27 17:58 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-27 18:01 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11240007 | 103911931 | 2023-09-11 16:00 | 2023-09-11 |  | 2023-09-11 10:03 | P6005_N | P6005_N | P6005_N |  | Please depute engineer at the site client is facing problam livia raNG P6005 KEY CARD =2NOS Durga's Switchgear--7 Nov 2022 ANKUR CHAUHARY SULTAN NAGAR JAIPUR 302020 9419833195 | 2023-09-11 | 2023-09-11 17:08 | No | Warranty | Ankur Chadhary | sultan nagar | Jaipur | 302020 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Sunny Sharma Sharma Electric Jaipur | Sharma Electric Works | Checked the switch found not working. Hence faulty replaced. P6005 - 2 nos Email : id not provided by customer. | Repair |  | 9- Service Validated | 2023-09-11 17:10 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11230027 |  | 2023-09-11 13:36 | 2023-09-11 |  | 2023-09-08 16:49 | LEO MAXCWTDCV4300AEC FAN2WAY PIBCVW/O H AND H WITH DAMPER DUAL SPLY ATS DUAL SEN | TDCV4300AN002 | TDCV4300AN002 | JK2136002698 | PM | 2023-09-08 | 2023-09-27 17:42 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-27 17:44 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11241299 | 103919649 | 2023-09-11 12:45 | 2023-09-11 |  | 2023-09-11 11:50 | A9N3P32C | A9N3P32C | A9N3P32C |  | PROVIDE COMPLAIN NUMBER @ GALLANTT ISPAT LIMITED CUSTOMER NAME : GALLANTT ISPAT LIMITED ADRESS : SURVEY NO 175/1, VILLAGE : SAMAKHIYALI TALUKA : BHACHAU, KUTCH, SAMAKHIYALI - 370150. CONTACT PERSON : AJAY RATHOD : 75748 45713 EMAIL : stores@gallant.com PRODUCT : A9N3P32C SR NO : D2307 QTY : 01 FAULT : DOLLY FREE. | 2023-09-11 | 2023-09-11 17:03 | No | Warranty | Gallon Metal Ltd | 175/1 Near Toll gate Samakhyali District | Kutch | 370150 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Mistri Anik Engineering Ahmedabad | Anik Engineering (554) | Checked the product found physially observed ok. mcb dolly free. so free replacement. for customer satisfaction. | Repair |  | 9- Service Validated | 2023-09-11 17:04 | =S= Consig Fill up 226038188 |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11230029 |  | 2023-09-11 13:37 | 2023-09-11 |  | 2023-09-08 16:50 | LEO MAXCWTDCV4300AEC FAN2WAY PIBCVW/O H AND H WITH DAMPER DUAL SPLY ATS DUAL SEN | TDCV4300AN002 | TDCV4300AN002 | JK2137000790 | PM | 2023-09-08 | 2023-09-27 17:45 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-27 17:47 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11241546 | 103921002 | 2023-09-11 19:57 | 2023-09-11 | Validated By Prashant | 2023-09-11 13:31 | IN8401_N | IN8401_N | IN8401_N |  | COMPLAINT FOR KRISHNA ELE Adress - KRISHNA ELECTRIC STORE 6, Rambhia niwas main Carter road , borivali (East) Mumbai - 66 CONTACT - 9833471616 VIBS Corp--29 March 2023 FACULTY - IN8401 - 7 - IN8SFR | 2023-09-11 | 2023-09-15 19:30 | No | Warranty | Krishna Electric Stores | Rambhia Niwas, Main Kasturba Road, | Mumbai | 400066 | Maharashtra | India FS ED&I CSP West Team S K SERVICES Mumbai | Ganesh Tati_S K SERVICES Mumbai | S.K. Services (10237) | We Visited the site Opel and Zencelo switches is not operating We will replace the switches book ZVO. We Replace The Product Closed The Complaint | Repair |  | 9- Service Validated | 2023-09-15 21:34 | =S= Consig Fill up 226048081 |  | 20 | INR | 20 | ENM HOME DISTRIBUTION
WO-11230031 |  | 2023-09-11 13:56 | 2023-09-11 |  | 2023-09-08 16:51 | LEO MAXCWTDCV4300AEC FAN2WAY PIBCVW/O H AND H WITH DAMPER DUAL SPLY ATS DUAL SEN | TDCV4300AN002 | TDCV4300AN002 | JK2136001409 | PM | 2023-09-08 | 2023-09-27 17:53 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-27 17:54 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11241604 | 103923955 | 2023-09-11 17:43 | 2023-09-11 |  | 2023-09-11 13:55 | IH14000100 | IH14000100 | IH14000100 |  | Wiser Installation For RS Illumination Wiser Relay issue Mobile Moovers inc--7/8/2023 Name of Customer Rajesh Site Address no.753, Hal Subbanna complex, d/847/1442/9, BB Rd, Yelahanka, Bengaluru, Karnataka 560064 Name of Contact Person at the Site Rajesh Customer Mail ID Contact Number 9845296518 | 2023-09-11 | 2023-09-12 16:00 | No | Warranty | Rajesh Rajesh | no.753, Hal Subbanna complex, d/847/1442/9, BB Rd, Yelahanka | Bangalore | 560064 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | C Gunasekaran_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported wiser 4 channel relay, the problem found was relay R1 continuous ON. We disconnected and added again and checked found working ok. The same shown to the customer. -We re-wired the 4ch relays as per the customer's requirement and checked found working ok. | Repair |  | 9- Service Validated | 2023-09-12 23:04 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11230034 |  | 2023-09-11 13:57 | 2023-09-11 |  | 2023-09-08 16:52 | LEO MAXCWTDCV4300AEC FAN2WAY PIBCVW/O H AND H WITH DAMPER DUAL SPLY ATS DUAL SEN | TDCV4300AN002 | TDCV4300AN002 | JK2136002699 | PM | 2023-09-08 | 2023-09-27 17:55 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-27 17:57 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11230035 |  | 2023-09-11 13:33 | 2023-09-11 |  | 2023-09-08 16:53 | LEO MAXCWTDCV4300AEC FAN2WAY PIBCVW/O H AND H WITH DAMPER DUAL SPLY ATS DUAL SEN | TDCV4300AN002 | TDCV4300AN002 | JK2128003024 | PM | 2023-09-08 | 2023-09-27 17:37 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-27 17:39 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11241939 | 103924487 | 2023-09-12 18:40 | 2023-09-11 |  | 2023-09-11 16:14 | A9KF71150 | A9KF71150 | A9KF71150 |  | MATERIAL PROBLEM SSPM Our Custoemr is facing problem as per below. Customer name - SSPM SYSTEM PVT LTD Site - SHED NO 175, PHASE-2, GIDC ESTATE, VATWA,AHMEDABAD Contact Person name - MR JAGDISH - 9054200455 Issue - NOT GETTING ON Reference - A9KF71150BQ QTY - 1NO OUR INVOICE NO - 1513 DATED - 28/8/2023 | 2023-09-11 | 2023-09-12 18:48 | No | Warranty | SSPM Systems & Engineers | Plot No. 175-178, G.I.D.C Phase II, Vatva Industrial Area, Vatva | Ahmedabad | 382445 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | Parthiv Patel JKS Ahmedabad | JKS Engineering Co. | We visit at side check mcb on/off found ok check mcb body and terminal side not any problem check mcb pole open 1nos replacement. | Repair |  | 9- Service Validated | 2023-09-13 10:10 | =S= Consig Fill up 226052340 |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11230037 |  | 2023-09-11 13:21 | 2023-09-11 |  | 2023-09-08 16:56 | LEO MAXCWTDCV4300AEC FAN2WAY PIBCVW/O H AND H WITH DAMPER DUAL SPLY ATS DUAL SEN | TDCV4300AN002 | TDCV4300AN002 | JK2136001411 | PM | 2023-09-08 | 2023-09-27 17:34 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-27 17:36 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11230041 |  | 2023-09-11 13:35 | 2023-09-11 |  | 2023-09-08 16:57 | LEO MAXCWTDCV4300AEC FAN2WAY PIBCVW/O H AND H WITH DAMPER DUAL SPLY ATS DUAL SEN | TDCV4300AN002 | TDCV4300AN002 | JK2137000789 | PM | 2023-09-08 | 2023-09-27 17:39 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-27 17:41 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11245337 | 103932311 | 2023-09-12 10:48 | 2023-09-12 |  | 2023-09-12 09:56 | EZ9R35240 | EZ9R35240 | EZ9R35240 |  | Complaint registration Name of Customer Fasil Site Address Ck house Edakkara Malappuram dt.pin: 679331 Kerala. Name of contact person at site Fasil Contact Phone / Mob. No: 9446159141 Defective product details Easy9 RCCB ( EZ9R35240) Nature of Defect Rccb complaint Shutdown availability if applicable yes Warranty status Under Warranty Commissioned / Installed date 1 months Serial No: or DOM of the product Ceekay Lights--17/8/2023 | 2023-09-12 | 2023-09-14 15:32 | No | Warranty | C K Lights Electrical And Lighting | Main Road, Edakkara, | Malapuram | 679331 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found 2pole rccb dolly free issue EZ9R35240 replaced 1nos problem solved | Repair |  | 9- Service Validated | 2023-09-14 15:37 |  |  | 75 | INR | 75 | ENM HOME DISTRIBUTION
WO-11230044 |  | 2023-09-11 13:14 | 2023-09-11 |  | 2023-09-08 16:58 | LEO MAXCWTDCV4300AEC FAN2WAY PIBCVW/O H AND H WITH DAMPER DUAL SPLY ATS DUAL SEN | TDCV4300AN002 | TDCV4300AN002 | JK2136002702 | PM | 2023-09-08 | 2023-09-27 17:20 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-27 17:22 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11295661 | 104195071 | 2023-09-23 10:30 | 2023-09-22 |  | 2023-09-22 14:30 | BMXP342020 | BMXP342020 | BMXP342020 | 21224380784 | Complaint for BMXP342020 serial number 21224380784 | 2023-09-22 | 2023-09-28 17:32 | No | Warranty | Stark Solutions | First Floor 6/10A, Kh No. 225/2 Katori Mill Mohan Nagar null | GHAZIABAD | 201007 | Uttar Pradesh | India FS ED&I CSP North Team Saffron Automation Delhi | Deepak Pal_Saffron Automation Delhi | Saffron Automation(18001) | Check the Modbus and found physical condition is ok. and is available at dealer site end. We collect the CPU card for testing purpose. CPU card port not communicate. We replace the faulty CPU card with new. Mail Id. accounts@starksolutions.in | Repair |  | 8- Service Completed | 2023-09-29 14:16 |  |  | 46 | INR | 46 | Industrial Automation Ops
WO-11245681 | 103930750 | 2023-09-12 11:17 | 2023-09-12 |  | 2023-09-12 10:41 | EZ9R35463 | EZ9R35463 | EZ9R35463 |  | Tripping Issue in RCCB - Mr. Indravadan Dave Kindly generate the case No. for following site and please resolve the issue as early as possible. 1.Name of customer : Indravadan Dave 2.Site Address: 35, Harikrupa Society, Opp ? Iskon Hights, Nr GEB Training Center, Gotri Road,Vadodara ? 3900 3.Name of Contact Person: Mr. Indravadan Dave 4.Contact No. : 9426979138 5.Defective Products : Easy9 RCCB ? Ref : EZ9R35463 (Tripping Issue) 6.Warranty: Yes RD ? Bharat Electricals ?Bharat Electricals--11 Sep 2023 | 2023-09-12 | 2023-09-12 16:50 | No | Warranty | Indravadan Dave | 35, Harikrupa Society, Opp ? Iskon Hights, Nr GEB Training Center, Gotri Road | Vadodara | 390001 | Gujarat | India FS ED&I CSP West Team Jay Services Vadodara | Ghanshyam Kachiya_Jay Services Vadodara | Jay Services | We visited at site & checked that RCCB physically ok. Checked incoming outgoing connections found ok. RCCB test by trip test button found working satisfactory. RCCB not trip during short circuit because it project against residual current only. We suggest to bemount MCB for over load & short circuit protection. we measure voltage between N & earth found site voltage so pleased checked earthing. | Repair |  | 9- Service Validated | 2023-09-12 16:51 |  |  | 8 | INR | 8 | ENM HOME DISTRIBUTION
WO-11230055 |  | 2023-09-11 13:18 | 2023-09-11 |  | 2023-09-08 16:59 | LEO MAXCWTDCV4300AEC FAN2WAY PIBCVW/O H AND H WITH DAMPER DUAL SPLY ATS DUAL SEN | TDCV4300AN002 | TDCV4300AN002 | JK2136002701 | PM | 2023-09-08 | 2023-09-27 17:28 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-27 17:30 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11296066 | 104216793 | 2023-09-23 07:24 | 2023-09-23 | We have inspected the VFD. VFD Display is not coming. 3-Ph input supply is present. During the inspection, we observed that the Ground cable was undersized. and looped the VFD Ground connections. | 2023-09-22 17:05 | ATV310H075N4E | ATV310H075N4E | ATV310H075N4E | 8B2238627235 | ATV310H075N4E 8B2238627235 Qty:1 P: Blast not working Nuziveedu Seeds Pvt Ltd, Kothur village, After Bandla Mylaram village,, Medchal to vantimamidi road, Mulugu (mandal), Medak district, Kothur, Telangana 509338 Contact Person is : Pandu, Mobile No.+91 9490561622 | 2023-09-22 | 2023-09-27 12:58 | No | Warranty | Nuziveedu Seeds Pvt Ltd | Kothur village, After Bandla Mylaram village,, Medchal to vantimamidi road, Mulugu (mandal), Medak district, Kothur, null | Mahabubnagar | 509338 | Telangana | India FS ED&I CSP South Team ENERPRO ENGINEERING SOLUTIONS Vijayawada | Makineni Jayashankar ENERPRO ENGINEERING SOLUTIONS VIJAYAWADA | Enerpro Engineering Solutions - 500012682 | VFD not working | Repair |  | 8- Service Completed | 2023-09-27 13:02 |  |  | 213 | INR | 213 | Industrial Automation Ops
WO-11246118 | 103951467 | 2023-09-12 12:57 | 2023-09-12 | Relay not working properly | 2023-09-12 10:50 | IH14000100 | IH14000100 | IH14000100 |  | Wiser Relay Not Working at Mr. Amol Hadkar Name: Mr. Amol Hadkar Contact: 9987398857 Address: A-702, Konark Vista Amanora Park Town Main Rd, off karadi magarpata bypass, Amanora Park Town, Hadapsar, Pune, Maharashtra 411028. Products to be serviced: 4 Channel Automation Relay (IH14000100) ? Quantity =1. Standard Sales Corp--24/7/2023 Wiser Relay Not Working | 2023-09-12 | 2023-09-13 11:16 | No | Warranty | Amol Hadkar | A-702, Konark Vista Amanora Park Town Main Rd, off karadi magarpata bypass, Amanora Park Town, Hadapsar | Pune | 411028 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Samadhan S_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the Relay not working properly. terminal no 1 & 3 not working.the light is which is connected in relay is not getting off. we observed this relay is stucked. last 3 days problem is occurred. So this Material is not repairable. So Relay Needs to be replaced. Required material : IH14000100- 01 nos | Repair |  | 9- Service Validated | 2023-09-13 13:06 |  |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-11230067 |  | 2023-09-11 13:15 | 2023-09-11 |  | 2023-09-08 17:02 | LEO MAXCWTDCV4300AEC FAN2WAY PIBCVW/O H AND H WITH DAMPER DUAL SPLY ATS DUAL SEN | TDCV4300AN002 | TDCV4300AN002 | JK2136000699 | PM | 2023-09-08 | 2023-09-27 17:23 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-27 17:24 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11246857 | 103954266 | 2023-09-19 09:34 | 2023-09-19 |  | 2023-09-12 11:36 | A9R12491 | A9R12491 | A9R12491 |  | A9n 100 amp 4p --1 no Not getting on Sr no : DD-2023-W04-5-0 A9n 100 amp 4p --1 no Not getting on Sr no : DD-2023-W04-5-0 Site : Inovic CRM Engineering Vatva,Ground Floor, FP No-1717, GIDC , Phase-3, Gujarat | 2023-09-12 | 2023-09-19 09:39 | No | Warranty | Inovic CRM Engineering | Ground Floor, FP No-1717, GIDC , Phase-3, Vatva null | Ahmedabad | 382440 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | Parthiv Patel JKS Ahmedabad | JKS Engineering Co. | We visit at site check rccb on/off working ok.check rccb tripping found.check rccb body and terminal side not any damage.suggested to customer check the earthing and wiring. | Repair |  | 9- Service Validated | 2023-09-19 09:44 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11230070 |  | 2023-09-11 13:13 | 2023-09-11 |  | 2023-09-08 17:04 | LEO MAXCWTDCV4300AEC FAN2WAY PIBCVW/O H AND H WITH DAMPER DUAL SPLY ATS DUAL SEN | TDCV4300AN002 | TDCV4300AN002 | JK2137000788 | PM | 2023-09-08 | 2023-09-27 17:17 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-27 17:19 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11230073 |  | 2023-09-11 13:16 | 2023-09-11 |  | 2023-09-08 17:05 | LEO MAXCWTDCV4300AEC FAN2WAY PIBCVW/O H AND H WITH DAMPER DUAL SPLY ATS DUAL SEN | TDCV4300AN002 | TDCV4300AN002 | JK2135005071 | PM | 2023-09-08 | 2023-09-27 17:25 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-27 17:27 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11301239 | 104230199 | 2023-09-23 15:57 | 2023-09-23 |  | 2023-09-23 15:45 | TM171ODM14R | TM171ODM14R | TM171ODM14R | RN-2021-W49-00060 | Fault in TM171 controller¦ Milliamps Automation | 2023-09-23 | 2023-09-29 13:21 | No | Warranty | Nutra like Formulation | A/23, swagat-3 Industrial Park, Nr. Kothiya bus stopIndore Highway null | Ahmedabad | 380001 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Mistri Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physically observed ok. TM171ODM14R SR NO : RN 2021 W49 0060 TM171ODM14R SR NO : RN 2021 W49 0031 in serial no 2021 W49 0060 a15 not working open for primary analysis. no any flashing observed. connect in system A15 use with PT1000 value not display other controller workin ok of same location. free replacement recommended. IN serial no RN 2021 W49 0031 when connect dt1 in controller it is restarted automatically . open the controller for primary analysis. no flashing obsreved check in system working satisfactory. problem may be due to internal loose connection. put in operation | Repair |  | 8- Service Completed | 2023-09-29 13:22 | =S= Consig Fill up 226083051 |  | 15 | INR | 15 | Industrial Automation Ops
WO-11230074 |  | 2023-09-11 13:12 | 2023-09-11 |  | 2023-09-08 17:06 | PRODUCT UNIFLAIR LEONARDO CHW LEO EV CW TDCV4300 R3G630 FAN 2WAY PIBCV VALVE WIT | TDCVQ | TDCVQ | C21936000275 | PM | 2023-09-08 | 2023-09-27 17:14 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-27 17:17 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11304296 | 104234158 | 2023-09-27 10:31 | 2023-09-25 |  | 2023-09-25 10:40 | ATV320D11N4C | ATV320D11N4C | ATV320D11N4C | HL2322120007 | Complaint 09-25 (Amtech Projects and Products) ATV320D11N4C Serial No. HL2322120007 | 2023-09-25 | 2023-09-30 15:06 | No | Warranty | Amtech Projects & Products Pvt. Ltd | Gaddo Lakhowal Road, | Ludhiana | 141002 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | checked the vfd found not power up. hence faulty, replaced. ATV320D11N4C - 1 nos. Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-30 15:09 |  |  | 25 | INR | 25 | Industrial Automation Ops
WO-11247104 | 103954279 | 2023-09-12 16:39 | 2023-09-12 | Validated By Prashant | 2023-09-12 13:35 | E84_26_SZ | E84_26_SZ | E84_26_SZ |  | Avatar Int. Socket Faulty Kindly arrange for an engineer at below site on urgent basis for Faulty E8426TSI_WE & E8426TSI_DG. Invoice copy attached for reference. Nylon Electric Corp--11 March 2023 Mr Awadesh Oberoi Esquire A 1606, Gokuldham, Behind Oberoi Mall, Goregaon East. Mumbai. M: 8299038510 | 2023-09-12 | 2023-09-13 13:31 | No | Warranty | Mr Awadesh | Oberoi Esquire A 1606, Gokuldham, Behind Oberoi Mall, Goregaon East | Mumbai | 400029 | Maharashtra | India FS ED&I CSP West Team S K SERVICES Mumbai | Ganesh Tati_S K SERVICES Mumbai | S.K. Services (10237) | We visited the site Product Ref No:-E8426TSI_WE :- 25Nos, E8426TSI_DG:-5Nos We check the material Avatar on international socket 2pin plug not going inside. | Repair |  | 9- Service Validated | 2023-09-13 13:37 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11230077 |  | 2023-09-11 11:39 | 2023-09-11 |  | 2023-09-08 17:07 | LEO MAXCWTDCV4300AEC FAN2WAY PIBCVW/O H AND H WITH DAMPER DUAL SPLY ATS DUAL SEN | TDCV4300AN002 | TDCV4300AN002 | JK2136000700 | PM | 2023-09-08 | 2023-09-27 17:09 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-27 17:11 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11304353 | 104231645 | 2023-09-26 10:44 | 2023-09-25 |  | 2023-09-25 11:06 | ATV310HU40N4E | ATV310HU40N4E | ATV310HU40N4E | 8B2226445122 | Dear schnieder electric , I have schnieder make vfd with serial no 8B2226445122 and model no atv310hu40n4e. Is not showing display while power. On I have check supply at terminal r , s and t. Is ok. Please an engineer to check vfd for replacement At Abu Electro electrical Sc-38 Ambaji industrial area Abu road ,pincode-307026 Rajasthan Contact person - ajay gupta Number -7728861062 | 2023-09-25 | 2023-09-29 14:52 | No | Warranty | Abu electro electricals | SC-38, AMBAJI INDUSTRIAL AREA AMBAJI INDUSTRIAL AREA | ABU ROAD | 307026 |  | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | Checked the vfd found not working due to internally short , Hence faulty replaced . ATV310HU40N4E - 1 nos Email : | Repair |  | 8- Service Completed | 2023-09-29 14:54 |  |  | 485 | INR | 485 | Industrial Automation Ops
WO-11247837 | 103963889 | 2023-09-12 16:42 | 2023-09-12 | Validated By Prashant | 2023-09-12 15:44 | E8334L1_DG_G5 | E8334L1_DG_G5 | E8334L1_DG_G5 |  | Avatar regulator--10 nos Not operating Avatar regulator--10 nos Customer will show the invoice during visit and if in case product found out of warranty they will pay the charges Not operating Site : Narindra Mehta Madhuban House, Plot NO-13 North South Road No08, GVPD Scheme, Ville Parle West Mumbai 9869121273 : Sunil Tejpal | 2023-09-12 | 2023-09-13 17:39 | No | Warranty | Sunil Tejpal | Narindra Mehta Madhuban House, Plot NO-13 North South Road No08, GVPD Scheme, Ville Parle West | Mumbai | 400029 | Maharashtra | India FS ED&I CSP West Team S K SERVICES Mumbai | Ganesh Tati_S K SERVICES Mumbai | S.K. Services (10237) | We Visited the site Product :-E8334L1_DG_G5 -2Nos. We check the material Fan Regulator is properly not operating. We not replace the product because of product is out of warranty. | Repair |  | 9- Service Validated | 2023-09-13 17:40 |  |  | 20 | INR | 20 | ENM HOME DISTRIBUTION
WO-11230080 |  | 2023-09-11 11:38 | 2023-09-11 |  | 2023-09-08 17:08 | LEO MAXCWTDCV4300AEC FAN2WAY PIBCVW/O H AND H WITH DAMPER DUAL SPLY ATS DUAL SEN | Uniflair Chilled Water-Cooling Solutions - Room Air Conditioners |  | JK2136000697 | PM | 2023-09-08 | 2023-09-27 16:54 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-27 17:08 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11304405 | 104230476 | 2023-09-25 15:37 | 2023-09-25 |  | 2023-09-25 11:29 | ATV310HU15N4E | ATV310HU15N4E | ATV310HU15N4E |  | ATV310HU15N4E Qty:1 P: Display not getting on. Balaji Enterprises (Contactecknics) Itrashi Kheda - 461111 (MP) Mr. Neeraj Agarwal Mob No. : 7000609077 | 2023-09-25 | 2023-09-26 12:08 | No | Warranty | Balaji Enterprises | Itrashi Kheda null | Hoshangabad | 461111 | Madhya Pradesh | India FS ED&I CSP West Team ABR Technical Service Indore | Mayank Patidar_ABR Technical Services Indore | ABR Technical Services (9574) | Reached at site as per customer VFD not getting ON. checked system voltage RY-413V, YB-237V, BR-410V, RE-237V, YE-237V, BE-235V, Neutral not available in panel. checked i/p & o/p by static test PA+ L1-.541/OL, L2-.543/OL, L3-.543/OL, PC- L1-.494/OL, L2-.496/OL, L3-.496/OL and o/p side OL/OL in both direction. internal circuit of VFD got damaged burnt. last fault F030 under voltage. for protection of VFD A9kf71306 3P 6A MCB used. checked wiring and found o/p side wrong wiring. motor T1 terminal connected on PB break resistor terminal and T3 terminal open no wiring. as per my primary observation VFD internal ckt and components got burnt due to wrong wiring and we can not consider it in warranty. its not a product issue so we are going to close this case. | Repair |  | 9- Service Validated | 2023-09-27 12:09 |  |  | 320 | INR | 320 | Industrial Automation Ops
WO-11247849 | 103963472 | 2023-09-13 11:12 | 2023-09-12 | NA | 2023-09-12 15:50 | E8334L1_DG_G5 | E8334L1_DG_G5 | E8334L1_DG_G5 |  | Problem with Avatar-on Please arrange to send the service personnel at the following site : Problem with Avatar-on ?Toshniwal Electricals--29 Aug 2023 Lekha Mittal 6 Dover Road Near st Lawrence school Kolkata-700019 M-9831188477 | 2023-09-12 | 2023-09-16 16:15 | No | Warranty | Lekha Mittal | 6 Dover Road Near st Lawrence school | Kolkata | 700019 | West Bengal | India FS ED&I CSP East Team B.D Electroservices Kolkata | KOUSHIK MONDAL_B.D Electroservices Kolkata | B.D Electroservices(500017330) | On received of ZVO material will delivered to customer. | Repair |  | 9- Service Validated | 2023-09-19 16:55 |  |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-11230082 |  | 2023-09-11 13:10 | 2023-09-11 |  | 2023-09-08 17:09 | PRODUCT UNIFLAIR LEONARDO CHW LEO EV CW TDCV4300 R3G630 FAN 2WAY PIBCV WITHOUT H | TDCVQ | TDCVQ | C21939001020 | PM | 2023-09-08 | 2023-09-27 17:11 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-27 17:13 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11304459 | 104236631 | 2023-09-25 14:22 | 2023-09-25 |  | 2023-09-25 11:36 | ABL2REM24045KAE | ABL2REM24045KAE | ABL2REM24045KAE | 8A2022W07 | ABL2REM24045KAA 8A2022W07 PANCHRATNA FASTRNERS 7.4KM STONE JINDH ROAD TITOLI ROHTAK 124001 HARYANA 9896999077 SUNIL SHARMA s.sunil@prfindia.com | 2023-09-25 | 2023-09-28 12:43 | No | Warranty | PANCHRATNA FASTRNERS | 7.4KM STONE JINDH ROAD TITOLI | ROHTAK | 124001 | Haryana | India FS ED&I CSP North Team Saffron Automation Delhi | Yavnish Tyagi Saffron Automation Delhi | Saffron Automation(18001) | Check the power supply and found power supply have output issue. We replace the faulty SMPS. Mail Id. mparora@prfindia.com | Repair |  | 8- Service Completed | 2023-09-29 12:39 |  |  | 128 | INR | 128 | Industrial Automation Ops
WO-11251200 | 103968395 | 2023-09-13 09:58 | 2023-09-13 |  | 2023-09-13 09:25 | IN8401_N | IN8401_N | IN8401_N |  | COMPLAIN ? IN8401 - QTY - 10, IN8402 - QTY - 10, IN8401 / 16 - QTY - 02 (SUPER ELECTRICALS (ADAJAN).) Name of Customer M/S SUPER ELECTRICALS (ADAJAN) 2 Site Address 1ST FLR, SHOP-1,2 CRYSTAL SHOPPING CENTER,MAHADEV ROAD, BEHIND MAHALAXMI TEMPLE GANGESHWAR, SURAT-395009 Contact Phone / Mob. No: 9737656392 3 Name of contact person at site MR.Nikunj Parmar Super Electrical 5 Defective product details IN8401 - QTY - 10 , IN8402 - QTY - 10 , IN8401 / 16 - QTY - 02 6 Product Make SCHNEIDER-SWITCH 7 Nature of Defect NOT WORKING 8 Shutdown availability if applicable 9 Warranty status UNDER WARRANTY 10 Commissioned / Installed date 11 Serial No: or DOM of the product BILL NO - : 7804/22-23 DATE - 30-11-2022 | 2023-09-13 | 2023-09-14 16:33 | No | Warranty | Super Electricals | Gangeshwar Mahdev Road | Surat | 395009 | Gujarat | India FS ED&I CSP West Team SHIV SAI ELECTRICALS Vapi | SHIVAM LAD SHIV SAI ELECTRICALS VAPI | shivsai electricals | AS PER SITE VSIT WE CHECK THE PROUCT AND FOND THE PRODUCT IS OK ON VISUAL INSPECTION.AFTER THAT CHECK THE SWITCH AND FOUND THE TOP PLATE IS BROKEN.BOTH SWITCH IS DOLLY FREE.WHEN WE CHECK THE PRODUCT WARRRNTY STATUS AND FOUND THE PRODUCT IS UNDER WARRNTY NEEDS TO BE REPLACED. | Repair |  | 9- Service Validated | 2023-09-15 16:37 | =S= Consig Fill up 226041546 |  | 136 | INR | 136 | ENM HOME DISTRIBUTION
WO-11230084 |  | 2023-09-11 13:20 | 2023-09-11 |  | 2023-09-08 17:10 | PRODUCT UNIFLAIR LEONARDO CHW LEO EV CW TDCV4300 R3G630 FAN 2WAY PIBCV WITHOUT H | TDCVQ | TDCVQ | C21939001021 | PM | 2023-09-08 | 2023-09-27 17:31 | No | Contract | NTT Global Data Centers & Cloud Inftrastructure India Pvt Ltd | Kajisonnenahalli Village, Bidarahal Survey No -146, Survey No -146, WHITEFEILD HOSKOTE ROAD | Bangalore | 560067 | Karnataka | India FS South4 Cooling CSP UCS project & Service Bangalore | Koushik S_UCS Projects and services Bangalore | UCS Projects & Services | PM DONE SUCCESSFULLY | Preventive Maintenance | Regular Preventive Maintenance | 8- Service Completed | 2023-09-27 17:33 |  |  | 50 | INR | 50 | ENM SECURE POWER
WO-11304798 | 104236525 | 2023-09-25 15:56 | 2023-09-25 |  | 2023-09-25 13:39 | ATV310HU15N4E | ATV310HU15N4E | ATV310HU15N4E | 8B2250407055 | Complaint for ATV310HU15N4E 8B2250407055 | 2023-09-25 | 2023-09-26 16:26 | No | Warranty | RP Crane | G-27, Site-B, Surajpur Indl Area | Greater Noida | 201306 | Uttar Pradesh | India FS ED&I CSP North Team Saffron Automation Delhi | Yavnish Tyagi Saffron Automation Delhi | Saffron Automation(18001) | Check the drive and found drive static test is ok. After providing the input supply drive is power up. Give the run command drive not run reverse only run forward. Drive have programming issue. We reset the drive and re-programming the drive. Now drive is working ok. | Repair |  | 8- Service Completed | 2023-09-26 17:30 |  |  | 38 | INR | 38 | Industrial Automation Ops
WO-11252183 | 103991740 | 2023-09-13 13:51 | 2023-09-13 | Validated By Prashant | 2023-09-13 10:52 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Wiser door bell--1 no Not ringing Invoice : Amazon--12 Sep 2023 Wiser door bell--1 no Not ringing Invoice : Amazon--12 Sep 2023 Site : C wing, 1312 Meriadian Aparmtents, Nerul West , Sec-6, Navi Mumbai 400706 Miss Pooja Gupta : 8407977554 | 2023-09-13 | 2023-09-14 17:03 | No | Warranty | Pooja Gupta | C wing, 1312 Meriadian Aparmtents,Sec-6, Nerul West | Navi Mumbai | 400706 | Maharashtra | India FS ED&I CSP West Team S K SERVICES Mumbai | Ganesh Tati_S K SERVICES Mumbai | S.K. Services (10237) | We visited the site IH100WFVDP:-1Nos We given supply & Neutral app setup configuration installation done. | Repair |  | 9- Service Validated | 2023-09-14 17:04 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11253037 | 103991885 | 2023-09-13 12:44 | 2023-09-13 |  | 2023-09-13 12:03 | A9N16259 | A9N16259 | A9N16259 |  | OM SAI ELECTROMECH A9N16259 COMPLAINT Name of Customer OM SAI ELECTROMECH Site Address VEER ENTERPRISE 42,VEDBHOOMI INDUSTRIAL ESTATE, NR. MIZAN BRIDGE,BAKROL - GATRAD ROAD,BAKROL BUJRANG,BAKROL-c Name of contact person at site BHARAT PANCHAL Contact Phone / Mob. No: 9909231169 Defective product details A9N16259 Nature of Defect DOLLY FREE Shutdown availability if applicable NA Warranty status Commissioned / Installed date INVOICE DATE : 07/09/2022 , INVOICE NO - 9606 | 2023-09-13 | 2023-09-13 17:50 | No | Warranty | VEER ENTERPRISE | 42,VEDBHOOMI INDUSTRIAL ESTATE, NR. MIZAN BRIDGE,BAKROL - GATRAD ROAD,BAKROL null | AHMEDABAD | 382430 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | Parthiv Patel JKS Ahmedabad | JKS Engineering Co. | We visit at site check rccb on/off not working check rccb body and terminal side not any damage.check rccb dolly free 1nos replacement. | Repair |  | 9- Service Validated | 2023-09-14 12:37 | =S= Consig Fill up 226031805 |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11253105 | 103995075 | 2023-09-13 17:16 | 2023-09-13 |  | 2023-09-13 12:37 | UNSMTSTART2M_WE | UNSMTSTART2M_WE | UNSMTSTART2M_WE |  | Model : Unica pure switches--2 nos Invoice : 4/10/2022--CS Electrical Not operating Model : Unica pure switches--2 nos Invoice : 4/10/2022--CS Electrical Not operating Site : 1118, Dr Mukherjee nagar, 3rd Floor, Nr Shiv Temple, Delhi 110009 Mona Sharma : 9212225437 | 2023-09-13 | 2023-09-15 18:23 | No | Warranty | Mona Sharma | 1118, Dr Mukherjee nagar, 3rd Floor, Nr Shiv Temple | Delhi | 110009 | Delhi | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the switches and found switches have breaking issue. We replace the faulty switches with new. | Repair |  | 9- Service Validated | 2023-09-15 18:25 |  |  | 28 | INR | 28 | ENM HOME DISTRIBUTION
WO-11253414 | 103992692 | 2023-09-13 16:48 | 2023-09-13 | Switches Not operating | 2023-09-13 14:29 | IN8401_N | IN8401_N | IN8401_N |  | Switches Issue at Comfort Gold Pune-Aishwaryam Developers We have supplied material to Pune based builder Aishwaryam Developers. Customer is facing some issues with our Zencelo Range. I have attached invoice for your reference. Please arrange further action for customer. Radhika Cables---22 Nov 2022 Customer Name- Ms Pooja E Wing Comfort Gold Akurdi Pune (Aishwaryam Developers) Contact Number- 7719049947 | 2023-09-13 | 2023-09-14 15:03 | No | Warranty | Miss Pooja | E Wing Comfort Gold Akurdi | Pune | 411002 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Kunal jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the Switches Not operating. this switch is not getting on/off. this switches are stucked not changing contact and we removed the switch and taken operation but it's stuck So Switches needs to be replaced. Required material : IN8401- 03 nos | Repair |  | 9- Service Validated | 2023-09-14 17:38 | =S= Consig Fill up 226049959 |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11253473 | 104000403 | 2023-09-13 15:38 | 2023-09-13 | RCCB Not working | 2023-09-13 14:48 | A9N16201 | A9N16201 | A9N16201 |  | A9N16201 Shivam Engineers---June 2023 Not operating A9N16201 Shivam Engineers---June 2023 Not operating Site : Legacy Avenue, Mani Vasti Mumbai Pune Highway Nr BU Bhandari Auto, Wakad, Pune 411057 Mr.Maruti Jadav : 9881915662 7020192509 | 2023-09-13 | 2023-09-14 12:23 | No | Warranty | Maruti Jadav | Legacy Avenue, Mani Vasti Mumbai Pune Highway Nr BU Bhandari Auto, Wakad | Pune | 411057 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Samadhan S_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked . RCCB Not working. as per discussed with customer neutral pole open. then we tight the hardware and checked continuity pole found open., then fitted RCCB in system and taken operation it's working found ok. | Repair |  | 9- Service Validated | 2023-09-14 12:34 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11256802 | 104022983 | 2023-09-14 10:30 | 2023-09-14 |  | 2023-09-14 09:16 | UNS6BPL2M_WE | UNS6BPL2M_WE | UNS6BPL2M_WE |  | complaint: davis_maria goretti Please register complaint at below site: DAVIS C O CHITTUPARAMBAN HOUSE PARAPPURAM P O PIN-683575 MOB:9895728012 Item: UNS6BPL2M_WE -1 nos Invoice : 12 April 2023 | 2023-09-14 | 2023-09-15 16:31 | No | Warranty | DAVIS DAVIS | CHITTUPARAMBAN HOUSE PARAPPURAM P O | ERNAKULAM | 683575 | Kerala | India FS ED&I CSP South Team Geartech Electric Cochin | Vineesh M_Geartech Electric Cochin | Geartech Electric ASC for Schneider Electric | Inspected the switch and found the problem with struck, then replaced the defectives and rectified the problem. Replacement material was arranged from the dealer side. | Repair |  | 9- Service Validated | 2023-09-15 19:32 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11256804 | 104023021 | 2023-09-14 10:42 | 2023-09-15 |  | 2023-09-14 09:19 | UNS6BPL2M_GY | UNS6BPL2M_GY | UNS6BPL2M_GY |  | complaint_santhosh family Please solve complaint at Santhosh kaduthuruthty Ettumanoor Kottayam 9447775712 Pin: 686604 Item: UNS6BPL2M_GY -1 nos Family Electricals--20/1/2023 | 2023-09-14 | 2023-09-30 14:34 | No | Warranty | Santhosh Santhosh | kaduthuruthty Ettumanoor junction, Ettumanoor | Kottayam | 686631 | Kerala | India FS ED&I CSP South Team Geartech Electric Cochin | Vineesh M_Geartech Electric Cochin | Geartech Electric ASC for Schneider Electric | Inspected the switch and found the problem with struck, Replaced the defective switch and rectified the problem - (we have arranged the material from the dealer as a loan ) | Repair |  | 8- Service Completed | 2023-09-30 15:10 |  |  | 55 | INR | 55 | ENM HOME DISTRIBUTION
WO-11256817 | 104017280 | 2023-09-14 11:22 | 2023-09-15 | Validated By Prashant | 2023-09-14 09:31 | E8315USB_WG_G8 | E8315USB_WG_G8 | E8315USB_WG_G8 |  | Fault Issue in Schneider AvatarOn Mr Sahil K 2147, The Atla, Sab TV lane, Nr Laxmi Industrial Estate, Link Road, Andheri West. Mumbai. M: 9920717107 Ref found faulty : E8315USB_WG_G8 purchase from nylon electric corporation Dated 10th August 2022. | 2023-09-14 | 2023-09-15 14:30 | No | Warranty | Sahil K | 2147, The Atla, Sab TV lane, Nr Laxmi Industrial Estate, Link Road, Andheri West | Mumbai | 400001 | Maharashtra | India FS ED&I CSP West Team S K SERVICES Mumbai | Ganesh Tati_S K SERVICES Mumbai | S.K. Services (10237) | We Visited Site Avatar On USB Charger is Not Operating We Check With Data Cable To Phone Not Showing Charging We Open The Socket Neutral Wire Terminal Loose Contact We Tighted Neutral Wire Now Conecting Showing Charging We Solved & Closed The Complaint | Repair |  | 9- Service Validated | 2023-09-15 21:31 |  |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-11256873 | 104014829 | 2023-09-14 11:30 | 2023-09-19 |  | 2023-09-14 10:25 | IH101ZWIFI | IH101ZWIFI | IH101ZWIFI |  | Re: Glitches and snags in the operation of schneider for lights -adjustment of timer functioning etc etc [ thread::5GWvegR0c-2m92WX2lMutz4:: ] Wiser automation Not operating as per customer's invoice the product got out of warranty now , kindly validate the warranty at site as per the serial number and if in case product is still out of warranty then customer is ready to pay charges for support Flat no -6903, Vasavi Sri Nilayam, L.B.Nagar Hyderabad 500074 Telangana 9701000217 | 2023-09-14 | 2023-09-19 15:09 | No | Warranty | Challa Hanumanth Rao | Flat no -6903, Vasavi Sri Nilayam, L.B.Nagar | Hyderabad | 500074 | Telangana | India FS ED&I CSP South Team Master Electrical Solutions Hyderabad | DEBANGSHU BOSE Master Electrical Solutions SECUNDERABAD | Master Electrical Solutions | we have visited the site carried out the following the job we observed that customer is using multiple devices on one router due to some of the applications getting disconnect there is no problem with the product customer insisted on waiting till they get clarification with other devices errors. we have discussed with customer today and took clarification to close the complaint. | Repair |  | 9- Service Validated | 2023-09-19 15:24 |  |  | 29 | INR | 29 | ENM HOME DISTRIBUTION
WO-11258664 | 104025648 | 2023-09-14 13:39 | 2023-09-14 |  | 2023-09-14 11:57 | 13181 | 13181 | 13181 |  | Not Workable Product / Defective Products Kindly generate the case No. for following site and please resolve the issue as early as possible. 1.Name of customer : ELEREN 2.Site Address: SF/A 202,Vrundalay Avenue-1 Nr Laxmipura Police station, Gotri ,Vadodara ? 390023 3.Name of Contact Person: Mr. Bhavin Prajapato 4.Contact No. : 9429935237 5.Defective Products : Kedra Enclosure ? Ref : 13181 (Not Workable) ?Shreeji Entp--13 Sep 2023 6.Warranty: Yes KRO ? Shreeji Enterprise | 2023-09-14 | 2023-09-15 10:15 | No | Warranty | Bhavin Prajapato | SF/A 202,Vrundalay Avenue-1 Nr Laxmipura Police station, Gotri | Vadodara | 390023 | Gujarat | India FS ED&I CSP West Team Jay Services Vadodara | Ghanshyam Kachiya_Jay Services Vadodara | Jay Services | We visited at site & checked that. Box Not Proper packing Extra mount- tap & fited box as per photo graphs. We open & obsered that top cover fitment one leg breakage in moulding. Bottom Box Ok. Above material purchase from Shreeji Enterprise. Again inv no. 0586 date - 13-sep-2023. We Attached all photographs for Reference. Further Action Taken By CCC. We suggest to be Attached - shreeji invoice/Schneider invoice. | Repair |  | 8- Service Completed | 2023-09-15 10:16 |  |  | 6 | INR | 6 | ENM HOME DISTRIBUTION
WO-11258659 | 104026665 | 2023-09-14 16:03 | 2023-09-14 |  | 2023-09-14 11:56 | IN8401_N | IN8401_N | IN8401_N |  | Model : Zencelo switches--2 nos Issue : Not operating Invoice : 21 June 2023--Shubham electrical Model : Zencelo switches--2 nos Issue : Not operating Invoice : 21 June 2023--Shubham electrical Site : Flat No 901, Tower D, Pieneer Araya , Sec-62, Gurugram Haryana 122102 Mr.Yuvaraj Mittal :9873793114 +918287907800 : Mr.Manish | 2023-09-14 | 2023-09-15 17:48 | No | Warranty | Yuvaraj Mittal | Flat No 901, Tower D, Pieneer Araya , Sec-62, | Gurugram | 122102 | Haryana | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the switch and found switch have stuck issue. We replace the faulty switch with new. | Repair |  | 8- Service Completed | 2023-09-16 17:48 | 226057297 zfre booked. |  | 54 | INR | 54 | ENM HOME DISTRIBUTION
WO-11262606 | 104046605 | 2023-09-15 10:50 | 2023-09-15 |  | 2023-09-15 09:40 | P1101_N | P1101_N | P1101_N |  | Complaint Register- Asset Alpine Oaks Name of Customer Asha balakrishnan Site Address Asset Alpine Oaks with pincode NGO Quarters Kakkanad,Near Nava Nirman Education & Welfare Society Kochi, Kerala-682021 Name of contact person at site Asha Balakrishnan Contact Phone / Mob. No: 9745000831 Defective product details P1101_N-3 Nos, P1085_N-2 nos, P1001_N- 4 nos, P2005NS_N- 1 nos, A9N26643 -1, A9N4P40C -1 Nature of Defect Complaint Shutdown availability if applicable Distributor Name,Invoice # & Date 9008507859, 9008506822, 9008507493, 9008572019, | 2023-09-15 | 2023-09-27 10:14 | No | Warranty | Asha balakrishnan | Asset Alpine Oaks NGO Quarters Kakkanad,Near Nava Nirman Education & Welfare Society | Kochi | 682021 | Kerala | India FS South2 ED&I CSP PrinterPeople Cochin | Vysakht PrinterPeople Cochin | PRINTER PEOPLE-COCHIN | A9DC3740- not replaced P1005- not replaced p1001,p1181,p1005,p7002 replacement given | Repair |  | 8- Service Completed | 2023-09-27 10:16 | material booked zfre : 226064075 |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11262618 | 104039600 | 2023-09-15 12:00 | 2023-09-15 |  | 2023-09-15 09:56 | EZ9EPVD06N | EZ9EPVD06N | EZ9EPVD06N |  | Complaint registration Name of Customer Gafoor Site Address Paruthikunnan house Adershery post , kuttippala , kottakkal Malappuram dt , pin : 676106 Kerala. Name of contact person at site Gafoor Contact Phone / Mob. No: 9946325050 Defective product details Easy9 6way phase selector db ( EZ9EPVD06N) Nature of Defect Door lock complaint Shutdown availability if applicable yes Warranty status Under Warranty Commissioned / Installed date 7 months Serial No: or DOM of the product Badhariyya Hardware--1/2/2023 | 2023-09-15 | 2023-09-16 15:09 | No | Warranty | Gafoor Gafoor | Paruthikunnan house Adershery post , kuttippala , kottakkal | Malappuram | 676106 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | VISITED THIS SITE FOUND Vertical phase selector DB, Easy9, metal double door lock issue, lock replaced working fine | Repair |  | 9- Service Validated | 2023-09-16 15:17 | Hi Team, Material booked zfre Zvo : 226058984 |  | 55 | INR | 55 | ENM HOME DISTRIBUTION
WO-11264270 | 104055536 | 2023-09-15 15:41 | 2023-09-15 |  | 2023-09-15 11:05 | P1001_N | P1001_N | P1001_N |  | livia door bell--1 no Invoice : Kumar Electrical--7 days back Not operating livia door bell--1 no Invoice : Kumar Electrical--7 days back Not operating Site : WZ-11, C/3B, New Sahibpura, Bank Wali Gali, Nr CRPF Camp, New Delhi 110018 Mr.Sharanjeet Singh : 9953507639 | 2023-09-15 | 2023-09-20 14:04 | No | Warranty | Sharanjeet Singh | WZ-11, C/3B, New Sahibpura, Bank Wali Gali, Nr CRPF Camp | New Delhi | 110018 | Delhi | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the bell switch and found bell switch have dolly free issue. We replace the faulty bell switch with new. | Repair |  | 8- Service Completed | 2023-09-20 14:39 |  |  | 34 | INR | 34 | ENM HOME DISTRIBUTION
WO-11264295 | 104055930 | 2023-09-16 14:11 | 2023-09-15 |  | 2023-09-15 11:27 | IN8401_N | IN8401_N | IN8401_N |  | Zencelo switch 6amp --3 nos Invoice : RS Entp, Madaan electrical--March 2023,3/5/2022 Not operating Zencelo switch 6amp --3 nos Invoice : RS Entp, Madaan electrical--March 2023,3/5/2022 Not operating pmehra2713@gmail.com | 2023-09-15 | 2023-09-20 14:25 | No | Warranty | Payal Mehra | 1b/32, 3rd floor NEA, Opp Baba Phoola Singh Gurudwara Old Rajender Nagar, Carol Bagh, | Delhi | 110005 | Delhi | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the switches and found switches have stuck issue, As per serial number switches not cover under warranty. Customer provided the invoice. We replace the only this time faulty switches with new. Mail Id. pmehra2713@gmail.com | Repair |  | 8- Service Completed | 2023-09-20 14:36 |  |  | 38 | INR | 38 | ENM HOME DISTRIBUTION
WO-11264771 | 104057691 | 2023-09-16 10:30 | 2023-09-15 | MCb Not working | 2023-09-15 14:15 | E8315_6_WE | E8315_6_WE | E8315_6_WE |  | Compliant for Avatar On switch R&A Tech--26/8/2023 Check-list for Complaint Registration 1 Name of Customer:- Ar. Gautam Jangir 2 Office No 4..2nd Floor, Shanti Sadan Society, Behind Kalyan Jewellers,Near Kalmadi House, Erandwane,Karve Road,Pune: 411004 3 Name of contact person at site:- Somnath Jadhav 4 Contact Phone / Mob. No 9209392010 5 Defective product details:- E8315_6_WE- 1 nos 6 Nature of Defect:- Not Operating proper | 2023-09-15 | 2023-09-16 11:01 | No | Warranty | Gautam Jangir | Office No 4..2nd Floor, Shanti Sadan Society, Behind Kalyan Jewellers | Pune | 411004 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Sachin Jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the MCb Not working. we taken continuity and pole found ok. then we observed MCb Dolly free. so we removed removed side sticker and try to repairer it. but it's not repair it. So Problem observed in MCb . MCB needs to be replaced. Required material : EZ9F21225- 01 nos | Repair |  | 9- Service Validated | 2023-09-18 10:49 | =S= Consig Fill up 226053975 |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11264802 | 104055767 | 2023-09-16 15:53 | 2023-09-15 |  | 2023-09-15 14:32 | IN8401_N | IN8401_N | IN8401_N |  | Complaint @ Hash _ Q Developers _ ZENcelo Name of Customer Hash Construction Site Address Q developers Villa No.20 , SIGNATURE VILLAS Opp. Sadbhavana Worl School, Palazhi, Calicut - 673008 Name of contact person at site Midhun Contact Phone / Mob. No: 93882 82872 Defective product details IN8401 , IN8481/16, IN8426U , IN8426/16, IN84SFR, E8331DN32_WE_G8 Nature of Defect not Working Shutdown availability if applicable Warranty status Inv no. 222302963 dt 06-02-2023 | 2023-09-15 | 2023-09-18 15:16 | No | Warranty | Hash Constructions | Q Developers Opp Sadbavana World School, Palazhi, | Kozhikode | 673008 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Rejilesh APSMarketingCompany Calicut | APS Marketing Company | visited this site found zencelo dp switch in8486/32 struck issue replaced and in8486 1nos & in8402 1nos replaced problem solved | Repair |  | 9- Service Validated | 2023-09-18 15:19 |  |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11264821 | 104059674 | 2023-09-16 12:41 | 2023-09-15 | NA | 2023-09-15 14:39 | E3031FRGS | E3031FRGS | E3031FRGS |  | Re: FAN REGULATOR GIVEN PROBLEM. E3031FRGS C- METRO E3031FRGS SOME OF THE FAN REGULATOR ARE GIVEN PROBLEM, PURCHASED DETAILS:- DESIGNER ELECTRICALS, KOLKATA, INVOICE NO:- DE/GST/1821/2324 DTD:- 27/07/2023. PLEASE ARRANGE TO SEND YOUR PERSON TO DO THE NEEDFUL, CLIENT NAME:- MR. S R GOENKA, GOENKA HOUSE, 6, ALIPORE PARK ROAD, KOLKATA - 700027. WEST BENGAL, INDIA. CONTACT PERSON MR. SANDIP JHA CARE-TAKER (M) 9958092143, | 2023-09-15 | 2023-09-21 14:00 | No | Warranty | Sandeep Jha | No-6, Alipore park raod | Kolkata | 700027 | West Bengal | India FS ED&I CSP East Team B.D Electroservices Kolkata | KOUSHIK MONDAL_B.D Electroservices Kolkata | B.D Electroservices(500017330) | On received of ZVO material will delivered to customer. | Repair |  | 9- Service Validated | 2023-09-21 11:08 | =S= Consig Fill up 226060588 |  | 10 | INR | 10 | ENM HOME DISTRIBUTION
WO-11265127 | 104061369 | 2023-09-16 11:51 | 2023-09-15 |  | 2023-09-15 16:42 | MTN6725-0003 | MTN6725-0003 | MTN6725-0003 |  | MTN6725-0003- 1 Nos Defective Company Name & Complete Address with pin code - Where product is installed INCYGYS AUTOMATION PVT LTD. ADDRESS: 4th Floor, No:404 Fortune Monarch Signature, Road No: 36, Jubilee Hills, Hyderabad- 500033. Contact Person at Site : Name & Mobile No. NARENDER Alternate Mobile No : 8919694426 Contact Person at Site - Email Address** narender@incygys.in Defective Product Model/Part No (Pls refer FAQ sheet ) KNX DALI-Gateway Basic REG-K/1/16/64 / MTN6725-0003 Nature of Defect* - Defects Video and Photographs Shutdown availability if applicable 23.08.2023 POP - SE Authorised Partner Invoice soft copy PURCHASE INVOICE FROM REXEL IS ATTACHED IN ATTACHMENTS--26.08.2023 Schneider Invoice Number :- Invoice Date Invoice Number 26-08-2023 AA2730125467 | 2023-09-15 | 2023-09-16 12:00 | No | Warranty | INCYGYS AUTOMATION PVT LTD | 4th Floor, No:404 Fortune Monarch Signature, Road No: 36, Jubilee Hills null | Hyderabad | 500033 | Telangana | India FS ED&I CSP South Team Sumanth Electrical Services Hyderabad | Basanth Reddy_SUMANTH ELECTRICAL SERVICES HYDERABAD | Sumanth Electrical Services | Visited the Site and Inspected the Schneider Electric- KNX DALI gateway basic REG-K/1/16/64 product Reference MTN6725-0003 - 01 No's. Here in our observation the material was at the distributor place. As per Customer the device was not powering ON even after giving operational supply . We have found that the PCB got burnt at the supply terminal area. Suspecting that voltage fluctuation have caused the damage. We cannot provide any free replacement in this case or failure due to external causes.Complaint is closed. | Repair |  | 9- Service Validated | 2023-09-16 17:39 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11265157 | 104055345 | 2023-09-15 19:07 | 2023-09-15 |  | 2023-09-15 16:48 | A9N4P40C | A9N4P40C | A9N4P40C |  | MEGA SWITCHGEAR - BARODA Mega Switchgears 54/3B, G.I.D.C. Ind. Estate, Makarpura, Vadodara - 390 010 Kavita - M :- 9624767567 Bhavin Shroff -Cell No. : +91 63522 21342 Contact Person at Site - Email Address**. Defective Product Model/Part No (Pls refer FAQ sheet ) A9N4P40C = 01 no. inv. : AS2324-107474?dt.12/8/23 Defective Product Model/Part No (Pls refer FAQ sheet ) A9S4P040 = 1 no. INV. : AS2324-108354 dt.31/8/2023 TRIPPING PROBLEM | 2023-09-15 | 2023-09-18 11:46 | No | Warranty | Mega Switchgears | 54/3B, GIDC, Makarpura, | Vadodara | 390010 | Gujarat | India FS ED&I CSP West Team Jay Services Vadodara | Ghanshyam Kachiya_Jay Services Vadodara | Jay Services | We visited at site and observed that mcb. And Isolator both are dolly free. It is not repairable Now we replaced from our distributor stock . | Repair |  | 9- Service Validated | 2023-09-18 11:47 | =S= Consig Fill up 226061092 |  | 8 | INR | 8 | ENM HOME DISTRIBUTION
WO-11265175 | 104061301 | 2023-09-15 20:13 | 2023-09-15 |  | 2023-09-15 16:54 | A9KF71210 | A9KF71210 | A9KF71210 |  | Complaint - ASD Controls Site Name & Complete Address ASD CONTROL SYSTEMS No.6 and 7, 4th Main, 16th Cross Byraveshwara Industrial Estate, Peenya 2nd Stage, Bangalore -560091 Site Contact Name & Mob# Mr. Subramanya Mob No. : 9945355456 Site Contact Email Address** Defective Product Model/Part No A9KF71210BQ Nature of Defect* Knob cut Shutdown availability if applicable Yes Distributor Name,Invoice # & Date Nil Serial No: or DOM of the product Invoice No. 232402956 Date : 05-06-2023 | 2023-09-15 | 2023-09-22 14:17 | No | Warranty | ASD Control Systems | NO 6,7, 4th Main Road, 16th Cross, Vishwaneedam, Andrahalli Main Road, Bhairaveshwara Insdustrial Estate, | Bangalore | 560091 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | MANOJ GANESAN SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported mcb, the problem found was mcb on/off knob not available and received in knob broken condition. On goodwill basis we had arranged for the replacement and new materials handed over to the customer. | Repair |  | 9- Service Validated | 2023-09-22 14:27 |  |  | 32 | INR | 32 | ENM HOME DISTRIBUTION
WO-11275067 | 104082844 | 2023-09-18 11:54 | 2023-09-18 |  | 2023-09-18 09:33 | P1001 | P1001 | P1001 |  | Livia switches--3 nos , 1 socket Not operating Livia switches--3 nos , 1 socket Not operating Warranty Certificate --5 years warranty from 2021 9909923962 Customer will show warranty certificate during time of visit | 2023-09-18 | 2023-09-19 11:16 | No | Warranty | Pranav Shah | Q 604 , shyamal park lane , 30 mtrs sunpharma bielee road . vadodra null | vadodra | 390012 | Gujarat | India FS ED&I CSP West Team Jay Services Vadodara | Ghanshyam Kachiya_Jay Services Vadodara | Jay Services | we visited at site and checked that livia 10 A 1 way 03 Nos switch top cover out of space now we replaced all from our stock and tested ok , we also checked that socket not working it is loose termination now rectify and tested ok . | Repair |  | 9- Service Validated | 2023-09-19 11:16 | =S= Consig Fill up 226061085 |  | 11 | INR | 11 | ENM HOME DISTRIBUTION
WO-11275071 | 104079351 | 2023-09-18 11:04 | 2023-09-18 | Relay Not working | 2023-09-18 09:40 | IH14000100 | IH14000100 | IH14000100 |  | Issue with one relays of home automation IH14000100 Qty:1 P: Not Working Abhijit Bhosale 9822373375 Flat 404, Seya Apartment, Opp. Union Bank, Near Navashya Maruti Mandir, Sinhgad Road, Pune ? 411030. I have purchased the home automation from livspace in Dec 2022. Last week we found one of the relays was not switching off the power to socket even after switching it off from app or physical switch. It was fixed as complaint 103929768 on 12 Sep 2023. Today we are seeing same issue with same relay but not it is for a led profile light. Can someone address this on priority? The light is not getting switched off. Thanks, Abhiiit Bhosale 9822373375 | 2023-09-18 | 2023-09-18 11:25 | No | Warranty | Abhijit Abhijit |  | Pune | 411030 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Kunal jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the Relay not working properly. terminal no 1 & 3 not working.the light is which is connected in relay is not getting off. we observed this relay is stucked. So this Material is not repairable. So Relay Needs to be replaced. Required material : IH14000100- 01 nos | Repair |  | 9- Service Validated | 2023-09-18 15:48 | =S= Consig Fill up 226063693 |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11275085 | 104078865 | 2023-09-19 09:38 | 2023-09-18 |  | 2023-09-18 09:53 | IN8401(BZ)-A | IN8401(BZ)-A | IN8401(BZ)-A |  | Zencelo complient (H Mart) We have supplied Zencelo material on 23-06-23 in that below mentioned items are not working. Kindly send our service person to solve this issue immediately. Items: IN8401(BZ)-9Nos, IN8426UNS(BZ)?7NOS Date-23-06-23---Aditya Agencies Address : Hmart India LLP NearSbi zonal office Balaji nagar, Siripuram Visakhapatnam-530003 Ph no: 9848497739 | 2023-09-18 | 2023-09-20 09:56 | No | Warranty | Hmart Hmart | NearSbi zonal office Balaji nagar, Siripuram | Visakhapatnam | 530003 | Andhra Pradesh | India FS ED&I CSP South Team Voltamp Electrical Works Visakhapatnam | Vydha Venkatesh_VOLT AMP ELECTRICAL WORKS Visakhapatnam | Voltamp Electrical Works | visited the site and found above the zencello switches is not working so today we have observed the problem of on/off mechanism issue so Schneider stock replaced so issue | Repair |  | 9- Service Validated | 2023-09-20 09:56 |  |  | 10 | INR | 10 | ENM HOME DISTRIBUTION
WO-11276970 | 104088301 | 2023-09-18 14:24 | 2023-09-18 |  | 2023-09-18 13:36 | A9N3P32C | A9N3P32C | A9N3P32C |  | A9N3P32C MCB Sr No. DD2023-W14-5-1 Operating Knob Free A9N3P32C MCB Sr No. DD2023-W14-5-1 Operating Knob Free Unable to switch ON Kadol lighting industry 3e Chhoti, 275, SSB Rd,Ramlal Colony, Ashok Nagar B Sri ganganagar 335001 Mr. Mahesh Sharma 9024827313 | 2023-09-18 | 2023-09-18 14:44 | No | Warranty | Kadol lighting industry | 3e Chhoti, 275, SSB Rd, Ramlal Colony, Ashok Nagar B | Sri ganganagar | 335001 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | Checked the mcb found dolly free after repairing now mcb working ok . Checked the capacitor found leakage issue and vfd found not power up, Hence faulty replaced. MEHVCSDY250A44 - 1 nos ATV310H075N4E - 1 nos Email : id not provided by customer. | Repair |  | 8- Service Completed | 2023-09-18 15:33 |  |  | 470 | INR | 470 | ENM HOME DISTRIBUTION
WO-11276998 | 104088681 | 2023-09-19 13:56 | 2023-09-18 |  | 2023-09-18 13:47 | UNS6BP2M_GY | UNS6BP2M_GY | UNS6BP2M_GY |  | Model : Unica Pure UNS6BP2MGY Door Bell--1 no , 6 amp switches--4 nos, 1 regulaor 1/7/2022 : Kumra Electric Works Not operating Model : Unica Pure UNS6BP2MGY Door Bell--1 no , 6 amp switches--4 nos, 1 regulaor 1/7/2022 : Kumra Electric Works Not operating Site : Rajan Moonga , HN-40,Bank Enclave, Extn-2, Nr Kuki taab Chonwk, Jalandhar 144003 9653424545 +919876913148 | 2023-09-18 | 2023-09-19 13:58 | No | Warranty | Rajan Moonga | HN-40,Bank Enclave, Extn-2, Nr Kuki taab Chonwk | Jalandhar | 144003 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | checked the switch and fan regulator found not giving output. Hence faulty, replaced. UNS61SW1M_GY - 1 Nos. UNS21USB1P1M_GY - 1 Nos. UNS5STFAN2M_GY - 1 Nos. Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-19 16:07 |  |  | 65 | INR | 65 | ENM HOME DISTRIBUTION
WO-11277198 | 104091529 | 2023-09-18 16:41 | 2023-09-18 |  | 2023-09-18 15:10 | IN8401_N | IN8401_N | IN8401_N |  | Zencelo switches---10 nos Invoice : Sai Trading--2 month back Not operating Zencelo switches---10 nos Invoice : Sai Trading--2 month back Not operating Site : Mr Kundan E-22, 1st floor, Vasant Vihar Coorgi Marg, Nr E Block Market, Delhi 110057 9873724977 | 2023-09-18 | 2023-09-22 17:21 | No | Warranty | Mr Kundan | E-22, 1st floor, Vasant Vihar Coorgi Marg, Nr E Block Market | Delhi | 110057 | Delhi | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the switches and found switches have stuck issue, We replace the faulty switches with new. | Repair |  | 8- Service Completed | 2023-09-22 17:25 |  |  | 32 | INR | 32 | ENM HOME DISTRIBUTION
WO-11277204 | 104088389 | 2023-09-18 16:52 | 2023-09-18 |  | 2023-09-18 15:16 | A9C30811 | A9C30811 | A9C30811 |  | COMPLAINT ABDUL MUNEER MK 1 Name of Customer ABDUL MUNEER MK 2 Site Address MANATHALA KARANATH VAVOOR CHEEKODE PO MALAPPURAM - 673640 3 Name of Contact Person at Site ABDUL MUNEER MK 4 Contact Phone / Mob. No: 9645220143 5 Defective Product Details A9C30811 - 1 PCS 6 Nature of Defect Not working 7 Shutdown availability if applicable Yes 8 Warranty Status Under Warranty 9 Commissioned / Installed date Before Three Months 10 Serial No: or DOM of the Product Bismi Electricals--9 Aug 2022 | 2023-09-18 | 2023-09-19 13:08 | No | Warranty | ABDUL MUNEER MK | MANATHALA KARANATH VAVOOR CHEEKODE PO | MALAPPURAM | 673640 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Rejilesh APSMarketingCompany Calicut | APS Marketing Company | visited this site found Acti9 iTL is a modular impulse relay not working A9C30811 replaced relay working fine | Repair |  | 9- Service Validated | 2023-09-19 13:13 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11277229 | 104092029 | 2023-09-20 15:32 | 2023-09-18 |  | 2023-09-18 15:24 | P1001_N | P1001_N | P1001_N |  | Livia switches--12 nos Invoice : Power Controls--9/9/2022 Not operating Livia switches--12 nos Invoice : Power Controls--9/9/2022 Not operating Site : House No-D-184, shrinathpuram, Kota Raj 324010 Puran Malnagar: 9829843881 | 2023-09-18 | 2023-09-20 15:34 | No | Warranty | Puran Malnagar | House No-D-184, shrinathpuram | Kota | 324010 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | Checked the fan regulator found working ok. Email : id not provided by customer . | Repair |  | 8- Service Completed | 2023-09-20 15:38 |  |  | 250 | INR | 250 | ENM HOME DISTRIBUTION
WO-11277387 | 104093326 | 2023-09-18 17:13 | 2023-09-18 |  | 2023-09-18 17:03 | A9N4P25C | A9N4P25C | A9N4P25C |  | Mcb Complaint Name of Customer THE MARSDEN BAKUBHAI & SONS PVT LTD. Site Address ?Darshan? Near Parimal Railway Underpass, Paldi, Ahmedabad 380 007 Name of contact person at site Ashwin Solanki Contact Phone / Mob. No: 99789 90416 Defective product details A9N4P25C Nature of Defect dolly free Shutdown availability if applicable YES Warranty status YES Commissioned / Installed date Serial No: or DOM of the product Name & phone No: of person registering the complaint Vishal Patni - 8141494244 INVOICE NO WITH DATE AA2730106574 - 17.07.2023 | 2023-09-18 | 2023-09-20 15:01 | No | Warranty | The Marsden Bakubhai &Sons Pvt. Ltd | 'Darshan', Near Parimal Railway Underpass,Paldi, Ahmedabad | AHMEDABAD | 380 007 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | Parthiv Patel JKS Ahmedabad | JKS Engineering Co. | We visit at side check mcb on/off not working.check mcb terminal and body side not any damge.check mcb dolly free.so now customer satisfaction 1time 1nos mcb replacement. | Repair |  | 9- Service Validated | 2023-09-20 15:59 | =S= Consig Fill up 226068268 |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11279283 | 104112672 | 2023-09-19 12:20 | 2023-09-19 |  | 2023-09-19 09:32 | X1001WH_N | X1001WH_N | X1001WH_N |  | Model : Opale 20A Invoice copy : 24/10/2022 Name : manoj kumar Add : FMD office sobha city dwarka expressway gurugram haryana 122017 M.No : 9810210704 Mail Id : fm.scg@sobha.com Model : Opale 20A Invoice copy : 24/10/2022 Contact Person : Manoj Kumar Quantity of faulty product : 5 | 2023-09-19 | 2023-09-20 14:25 | No | Warranty | Manoj Kumar | FMD OFFICE SOBHA CITY DWARKA EXPRESSWAY GURUGRAM | Gurgaon | 122017 | Haryana | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the switches and found switches have stuck issue and burnt issue, We replace the faulty switches with new. Mail Id. fm.scg@sobha.com | Repair |  | 8- Service Completed | 2023-09-20 14:33 |  |  | 54 | INR | 54 | ENM HOME DISTRIBUTION
WO-11280325 | 104116694 | 2023-09-19 17:29 | 2023-09-19 |  | 2023-09-19 12:41 | A9N3P63C | A9N3P63C | A9N3P63C |  | Model : A9n3p63c Sr : D2146 Not operating Model : A9n3p63c Sr : D2146 Not operating | 2023-09-19 | 2023-09-20 15:15 | No | Warranty | Deni Zone | Kh No 24/21 Nangli Sakravati Near Hond Service center Najafgarh | Delhi | 110043 | Delhi | India FS ED&I CSP North Team Sharma Electric Works Delhi | Pradeep Sharma_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mcb found phase missing, Hence faulty replaced. A9N3P63C - 1 nos Email : id not provided by customer. | Repair |  | 8- Service Completed | 2023-09-20 15:18 |  |  | 20 | INR | 20 | ENM HOME DISTRIBUTION
WO-11280806 | 104120097 | 2023-09-20 09:48 | 2023-09-19 | Hence this os needed to be replaced - X1001WH_N -01Nos | 2023-09-19 15:20 | X1001WH_N | X1001WH_N | X1001WH_N |  | Re: Low quality switches [ thread::nTeSI-lAcLumEo5Qm7bfUT4:: ] I purchased today and installer two numbers of Following switches for home. Customer purchased in Sep 2023 Opale 6AX. Both are of low quality and are of very low quality. Feels like it will break at any moment. Photos attached. Kindly help. Nilesh Wankhede B-204, Woodsville Phase 2, Borhadewadi, Moshi, Pune -412105. Contact number - 9422160001 | 2023-09-19 | 2023-09-21 15:50 | No | Warranty | Nilesh Wankhede | B-204, Woodsville Phase 2, Borhadewadi, Moshi | Pune | 412105 | Maharashtra | India FS ED&I CSP West Team Alliance Controls Pvt Ltd Pune | Shmabhu Bone_Alliance Controls Pvt. Ltd | Alliance Controls Pvt. Ltd. (7966) | 1)Visited on site & checked X1001WH - 01Nos , found that switches having an operating issue. Hence this os needed to be replaced - X1001WH_N -01Nos | Repair |  | 8- Service Completed | 2023-09-21 15:52 |  |  | 3 | INR | 3 | ENM HOME DISTRIBUTION
WO-11280929 | 104123933 | 2023-09-19 16:56 | 2023-09-19 |  | 2023-09-19 16:20 | UNSMTSTART2M_WE | UNSMTSTART2M_WE | UNSMTSTART2M_WE |  | switches exceeded the warranty , kindly Replace the 5 nos switches as a one time support to customer and mention the same on SIR copy Unica pure switches issue Model : Unica pure 6amp Grey color--5 nos Not operating | 2023-09-19 | 2023-09-23 15:27 | No | Warranty | Ram Ram | A 127 Yojana Vihar Near Sabita Vihar Market | Delhi | 110092 | Delhi | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the switches and found switches have stuck issue and output issue. We replace the faulty switches with new. Mail Id. rlwadhwa@hotmail.com | Repair |  | 8- Service Completed | 2023-09-23 17:33 |  |  | 18 | INR | 18 | ENM HOME DISTRIBUTION
WO-11280976 | 104123925 | 2023-09-20 10:07 | 2023-09-19 | need to be Replaced X1001WH_N-01Nos. | 2023-09-19 16:44 | X1001WH_N | X1001WH_N | X1001WH_N |  | Complaint for replacement of electric switch under warranty Society under 10 years warranty for switchs Dear Sir , I am resident of J102 , Greens , Opp. PUDUMJEE PAPER MILL, THERGAON ,PUNE . Few ELECTRIC SWITCH are not working in my flat and are coverd under warranty , request for Service engineer visit ,on priority . Pls acknowledge and share complaint no . Regards Saurabh Markhedkar 9575311326 | 2023-09-19 | 2023-09-20 14:00 | No | Warranty | Saurabh Markhedkar | J102 , Greens , Opp. PUDUMJEE PAPER MILL, THERGAON | PUNE | 410506 | Maharashtra | India FS ED&I CSP West Team Alliance Controls Pvt Ltd Pune | Shmabhu Bone_Alliance Controls Pvt. Ltd | Alliance Controls Pvt. Ltd. (7966) | 1) Visited at site & discuss with customer & check the switch board .(2) After proper shutdown , we found ( 01 Nos ) switch broken (boulby part (3) Then we need to be replaced , this switch is under warranty period & having 10 year of warranty .(4) Hence this switch need to be Replaced X1001WH_N-01Nos. | Repair |  | 8- Service Completed | 2023-09-20 14:00 |  |  | 11 | INR | 11 | ENM HOME DISTRIBUTION
WO-11283847 | 104144261 | 2023-09-20 11:06 | 2023-09-20 |  | 2023-09-20 10:43 | A9N4P32C | A9N4P32C | A9N4P32C |  | Product : A9N4P32C - Qty:1 Srn : D2215 Warranty Yes April 2022 Problem : Not getting ON M/s. SANT ELECTRICAL & MILL STORE SAIPUR ROAD,SAINI COLONY, OPP FOCAL POINT, JALANDHAR. 144005 Mr. Jaswant Singh 9417198561 jaswant_gsb@yahoo.com Product : A9N4P32C - Qty:1 Srn : D2215 Warranty Yes April 2022 Problem : Not getting ON | 2023-09-20 | 2023-09-20 11:15 | No | Warranty | SANT ELECTRICAL & MILL STORE | SAIPUR ROAD , SAINI COLONY OPP FOCAL POINT JALANDHAR | JALANDHAR | 144001 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the MCB found Not getting ON due to phase missing and meter found not power up and auxiliary contact block-(timer on delay found no changeover in contact. Hence faulty replaced. A9N4P32C - 1 Nos. METSEEM6438HCL10RS - 1 Nos. LADT2 - 1 Nos. email : jaswant_gsb@yahoo.com | Repair |  | 8- Service Completed | 2023-09-20 15:41 |  |  | 65 | INR | 65 | ENM HOME DISTRIBUTION
WO-11285020 | 104145806 | 2023-09-20 14:29 | 2023-09-20 |  | 2023-09-20 11:55 | A9N3P32C | A9N3P32C | A9N3P32C |  | Model : A9N3P32C Sr: D2244 1 Phase missing | 2023-09-20 | 2023-09-23 14:49 | No | Warranty | Ritesh Ritesh | Sua Road, Jaspal Bangar, Nr Satsang Ghar null | Ludhiana | 141122 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | checked the mcb found phase missing. hence faulty,replaced. A9N3P32C - 1 Nos. Email: id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-23 14:51 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11285549 | 104147439 | 2023-09-21 11:09 | 2023-09-20 | Smart Doorbell Installation | 2023-09-20 14:36 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Regarding Wiser Smart Doorbell Installation Project Shanti Samarth, Mr. Naren Varpe Product to be Installed: Wiser Smart Doorbell ( IH100WFVDP ) ?> Quantity = 1. New India Cables--21 April 2023 Installation at Following Flat No: Mr. Naren Varpe ? 9763262425 -> Flat No: 202. Address: Mate Nagar, Vadgaon Sheri, Opp Jodhpur Sweets, Kharadi, Pune 411014. | 2023-09-20 | 2023-09-21 11:14 | No | Commercial Action - Sales | Naren Varpe | Flat No: 202,Mate Nagar, Vadgaon Sheri, Opp Jodhpur Sweets, Kharadi | Pune | 411014 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Kunal jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the smart doorbell. so we given supply to VDP and set up. then we taken customer mobile and installed wiser for india App and add the smart doorbell. and then taken operation it's found ok. VDP working ok. | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-21 11:26 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11285859 | 104154028 | 2023-09-20 17:55 | 2023-09-20 | NA | 2023-09-20 15:57 | IN84SFR_N | IN84SFR_N | IN84SFR_N |  | Zencelo IN84SFR--1 no Himmat electricals--5 month back Not operating Zencelo IN84SFR--1 no Himmat electricals--5 month back Not operating Site : 40, Ezra Street, 4th floor, Kolkata 700001 Mr.Vicky Singh : 9875557895 | 2023-09-20 | 2023-09-26 13:00 | No | Warranty | Vicky Singh | 40, Ezra Street, 4th floor | Kolkata | 700001 | West Bengal | India FS ED&I CSP East Team B.D Electroservices Kolkata | KOUSHIK MONDAL_B.D Electroservices Kolkata | B.D Electroservices(500017330) | On received of ZVO material will delivered to customer. | Repair |  | 8- Service Completed | 2023-09-26 11:18 |  |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-10745817 | 101003516 | 2023-05-29 18:28 | 2023-05-26 |  | 2023-05-26 13:20 | E3033H2_EBGS | E3033H2_EBGS | E3033H2_EBGS |  | Re: 100706994 Sreerosh Properties NEED suggestion | 2023-05-26 | 2023-09-19 14:55 | No | Warranty | Sreerosh Properties Pvt Ltd | 2nd Floor Sreerosh Centre Old No. 41 New No. 97 New Avadi Road Kilpauk null | Chennai | 600010 | Tamil Nadu | India FS South2 ED&I CSP UpservePowerSystems Chennai | HARI PRASATH UpservePowerSystems Chennai | Upserve Power Systems | Replacement is given. | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-19 17:32 |  |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-11286146 | 104154516 | 2023-09-20 17:34 | 2023-09-20 |  | 2023-09-20 17:20 | A9KF71332 | A9KF71332 | A9KF71332 |  | PROVIDE COMPLAIN NUMBER @ UMIYA ELECTRICALS CUSTOMER NAME : UMIYA ELECTRICALS ADRESS : SHOP NO 3, SUKHIL SANSAR APARTMENT, OPP. GANDHI PARK SOCIETY, VIRATNAGAR, ODHAV AHMEDABAD - 382415. CONTACT PERSON : KAUSHIK BHAI : 99243 21721 EMAIL : kaushikpatel338@gmail.com PRODUCT : A9KF71332 SR NO : D2221 QTY : 01 FAULT : DOLLY FREE | 2023-09-20 | 2023-09-21 10:33 | No | Warranty | UMIYA ELECTRICAL | SHOP NO 3,OPERA INDUSTRIAL ESTATE,OPP.TORRENT POWER VINZOL,RAMOL VATVA ROAD,PHASE IV,VATVA | AHMEDABAD | 380001 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Nijesh Patel_Anik Engineering Ahmedabad | Anik Engineering (554) | Checked the product A9KF71332 SR NO : D2221 ok but dolly free so free replacemnet for customer satisfaction. | Repair |  | 9- Service Validated | 2023-09-21 10:33 | =S= Consig Fill up 226070535 |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11289151 | 104162775 | 2023-09-21 12:12 | 2023-09-21 |  | 2023-09-21 09:14 | EZ9ESND08 | EZ9ESND08 | EZ9ESND08 |  | Re: EAZY9 DB LOCK COMPLAINT PREMIER ELECTRICALS BALUSSERY [ thread::aGQV6I0beISP1SdcjM9-Tz4:: ] Name of Customer JAMSHID S/O HAMSA Site Address VELUTHEDATH KATTIPARA KOZHIKODE Name of contact person at site JAMSHID Contact Phone / Mob. No: 9447071608 Defective product details EAZY9 DB Nature of Defect DB LOCK COMPLAIINT Shutdown availability if applicable yes Distributor Name,Invoice # & Date Premier electricals, Balussery Serial No: or DOM of the product Premier Electricals--11/1/2023 | 2023-09-21 | 2023-09-22 21:15 | No | Warranty | JAMSHID JAMSHID | VELUTHEDATH KATTIPARA | Kozhikode | 673002 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Rejilesh APSMarketingCompany Calicut | APS Marketing Company | visited this site found Easy9 - TPN DB - double door clip missing, door clip replaced working fine | Repair |  | 9- Service Validated | 2023-09-22 21:16 |  |  | 40 | INR | 40 | ENM HOME DISTRIBUTION
WO-11289160 | 104158592 | 2023-09-21 12:08 | 2023-09-21 |  | 2023-09-21 09:22 | A9C30811 | A9C30811 | A9C30811 |  | COMPLAINT MUNEER MK VAVOOR 1 Name of Customer ABDUL MUNEER 2 Site Address MANANTHALA KARANATH VAVOOR CHEEKODE (PO) MALAPPURAM - 673645 3 Name of Contact Person at Site ABDUL MUNEER 4 Contact Phone / Mob. No: 9645220143 5 Defective Product Details A9C30811 : 1 PCS 6 Nature of Defect Not working 7 Shutdown availability if applicable Yes 8 Warranty Status Under Warranty 9 Commissioned / Installed date Before Three Months 10 Serial No: or DOM of the Product Bismi Electricals--9 Aug 2022 | 2023-09-21 | 2023-09-22 15:00 | No | Warranty | ABDUL MUNEER MK | MANATHALA KARANATH VAVOOR CHEEKODE PO | MALAPPURAM | 673640 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found A9C30811 impulse relay not working checked the relay, its working fine, no abnormality found | Repair |  | 9- Service Validated | 2023-09-22 15:05 |  |  | 40 | INR | 40 | ENM HOME DISTRIBUTION
WO-11289975 | 104175104 | 2023-09-21 16:05 | 2023-09-21 |  | 2023-09-21 11:17 | A9N16252 | A9N16252 | A9N16252 |  | E9N16252 Dom : 10/2021 Not tripping A9N16252 Dom : 10/2021 Not tripping Site : 70,D-3F, Rama Road Industrial area Nxt to Goel Properties, Nr Kiti Nagar Station, New Delhi 110015 Mr Bahl : 9050178371 | 2023-09-21 | 2023-09-21 16:11 | No | Warranty | Mr Bahl | 70,D-3F, Rama Road Industrial area Nxt to Goel Properties, Nr Kiti Nagar Station | New Delhi | 110015 | Delhi | India FS ED&I CSP North Team Sharma Electric Works Delhi | Pradeep Sharma_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the rccb found not tripping due wrong selection but rccb found out of warranty from serial number, Hence no replacement given to customer. Email : id not provided by customer. | Repair |  | 8- Service Completed | 2023-09-21 16:17 |  |  | 20 | INR | 20 | ENM HOME DISTRIBUTION
WO-11290197 | 104177942 | 2023-09-23 11:21 | 2023-09-21 |  | 2023-09-21 12:51 | UNSMTSTART2M_WE | UNSMTSTART2M_WE | UNSMTSTART2M_WE |  | Grey switches--8 nos Invoice : 7 months back not operating Grey switches--8 nos Invoice : 7 months back not operating Site : Pankaj Kumar Aggarwal Plot No-21, Sahib Nagar Bhuvneshwar, 751022 8093113332 | 2023-09-21 | 2023-09-25 12:06 | No | Warranty | Pankaj Kumar Aggarwal | Plot No-21, Sahib Nagar | Bhubaneswar | 751022 | Odisha | India FS ED&I CSP East Team UNIVERSAL ELECTRIC POWER SOLUTION BHUBANESWAR | RAMESH PRABHAT_UNIVERSAL ELECTRIC POWER SOLUTION BHUBANESWAR | Universal Electric Power Solution(500012032) | material to be booked | Repair |  | 8- Service Completed | 2023-09-28 12:09 |  |  | 16 | INR | 16 | ENM HOME DISTRIBUTION
WO-11290273 | 104178767 | 2023-09-21 15:30 | 2023-09-21 |  | 2023-09-21 13:14 | A9N4P63C | A9N4P63C | A9N4P63C |  | A9N4P63C Sr : D2314 1 pole not working A9N4P63C Sr : D2314 1 pole not working Site : Faridabad Electrical, Nr Old PNB, Chawla Colny, Ballabhgardh 121004 Mr.Surinder : 9810329173 lbosswal@gmail.com | 2023-09-21 | 2023-09-25 13:09 | No | Warranty | Faridabad Electricals | Near Old Punjab National Bank Chawla Colony Ballabhgarh Faridabad 121100 | Faridabad | 121100 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mcb found phase missing, Hence faulty replaced A9N4P63C - 1 nos Email : | Repair |  | 8- Service Completed | 2023-09-25 13:12 |  |  | 45 | INR | 45 | ENM HOME DISTRIBUTION
WO-11290480 | 104179281 | 2023-09-21 16:59 | 2023-09-21 | NA | 2023-09-21 14:43 | E8334L1LED_GH_G8 | E8334L1LED_GH_G8 | E8334L1LED_GH_G8 |  | Problem with Avatar-on Please arrange to send the service personnel at the following site : Item Name is - 1. (E8334L1LED_GH_G8) 2. (E8315_6_WG) Toshniwal Electricals--29 aug 2023 Lekha Mittal 6 Dover Road Near st Lawrence school Kolkata-700019 M-98311-88477 | 2023-09-21 | 2023-09-26 16:15 | No | Warranty | Lekha Mittal | 6 Dover Road Near st Lawrence school | Kolkata | 700019 | West Bengal | India FS ED&I CSP East Team B.D Electroservices Kolkata | KOUSHIK MONDAL_B.D Electroservices Kolkata | B.D Electroservices(500017330) | On received of ZVO material will delivered to customer. | Repair |  | 8- Service Completed | 2023-09-26 17:54 |  |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-11290736 | 104185448 | 2023-09-21 17:34 | 2023-09-21 |  | 2023-09-21 16:47 | P1001_N | P1001_N | P1001_N |  | Livia switches--13 nos Invoice : ES Electrical Switchgear---Aug 2023 Not operating Livia switches--13 nos Invoice : ES Electrical Switchgear---Aug 2023 Not operating Site : Oliva Property No-2, Kapil Vihar, Nr Pillar No-347, Pitampura, Delhi Mr.Lalit : 9873409011 | 2023-09-21 | 2023-09-23 17:52 | No | Warranty | Mr Lalit | Oliva Property No-2, Kapil Vihar, Nr Pillar No-347, Pitampura | Delhi | 110034 | Delhi | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the switches and found switches have continuity ok. So switches is ok. We suggest to customer please check the wiring and bell. We close the complaint. Switches is ok | Repair |  | 8- Service Completed | 2023-09-23 18:09 |  |  | 38 | INR | 38 | ENM HOME DISTRIBUTION
WO-11295334 | 104207956 | 2023-09-22 15:22 | 2023-09-22 | As per sr no product in warranty raise ZVO for replacement | 2023-09-22 12:26 | IN8401_N | IN8401_N | IN8401_N |  | COMPLAIN ? IN8401 - QTY - 07 (SUPER ELECTRICALS (ADAJAN).) Name of Customer M/S SUPER ELECTRICALS (ADAJAN) 2 Site Address 1ST FLR, SHOP-1,2 CRYSTAL SHOPPING CENTER,MAHADEV ROAD, BEHIND MAHALAXMI TEMPLE GANGESHWAR,SURAT-395009 Contact Phone / Mob. No: 7698897074 3 Name of contact person at site MR.Bhavesh Bhai 5 Defective product details IN8401 - QTY - 07 6 Product Make SCHNEIDER- BUTTON SWITCH 7 Nature of Defect NOT WORKING PROPERLY 8 Shutdown availability if applicable 9 Warranty status UNDER WARRANTY 10 Commissioned / Installed date 11 Serial No: or DOM of the product BILL NO - : 6491/22-23 DATE - 18-10-2022 | 2023-09-22 | 2023-09-23 10:34 | No | Warranty | Super Electricals | Gangeshwar Mahdev Road | Surat | 395009 | Gujarat | India FS ED&I CSP West Team VARDHAMAN ELECTROSOFT Vadodara | MAHENDRA SINGH VARDHAMAN ELECTROSOFT Vadodara | VARDHAMAN ELECTROSOFT | we visited the site and check the switch is physically ok. we check and found that switch ON/OFF pole is open and stuck issue. | Repair |  | 9- Service Validated | 2023-09-25 10:35 | 226075568 |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11234337 | 103909491 | 2023-09-13 11:05 | 2023-09-09 |  | 2023-09-09 13:58 | METSEPM2230D | METSEPM2230D | METSEPM2230D |  | Dear Team, Please find the picture of meter as required. Kindly resolve the case, it is still open. Name of Customer APL Apollo Building Products Private Limited Site Address Village Rigini Keseda, Tehsil Simga, Baloda Bazar, Raipur Name of contact person at site Mr Shyamendra Singh 92058 83472 Email id:customercare@tricolite.com Product detail 1 no Meter : METSEPM2230D Nature of Defect Not Working Commissioned in M/o March 2023 Serial No: or DOM of the product : 540250249914 Name & phone No: of person registering the complaint Seema Sharma- 9958998882 With Regards Seema Sharma Service Coordinator Tricolite Electrical Industries Ltd 9958998882 customercare@tricolite.com Unit 1-Plot No 18/1A, Site 4, Sahibabad Ghaziabad UP 201010Unit 2-Plot No 5, Sector 6, IMT Manesar Gurgaon HR-122052Unit 3-Plot No 11, Sector 6, IMT Manesar Gurgaon HR-122052 Unit 4-Plot No 32, Sector 6, IMT Manesar Gurgaon HR-122052 www.tricolite.com From: Customer Care Sent: Thursday, August 10, 2023 3:51 PM To: Schneider Electric <customercare.in@schneider-electric.com> Subject: RE: Regarding 1 no Meter display problem at Apollo Raipur Site, Case: 103196111, Image attached With Regards Seema Sharma Service Coordinator Tricolite Electrical Industries Ltd 9958998882 customercare@tricolite.com Unit 1-Plot No 18/1A, Site 4, Sahibabad Ghaziabad UP 201010Unit 2-Plot No 5, Sector 6, IMT Manesar Gurgaon HR-122052Unit 3-Plot No 11, Sector 6, IMT Manesar Gurgaon HR-122052 Unit 4-Plot No 32, Sector 6, IMT Manesar Gurgaon HR-122052 www.tricolite.com From: Schneider Electric <customercare.in@schneider-electric.com> Sent: 10 August 2023 15:50 To: Customer Care <customercare@tricolite.com> Subject: Regarding 1 no Meter display problem at Apollo Raipur Site, Case: 103196111, Dear Customer, Thank you for contacting Schneider Electric. Your request has been received and you should expect a response from us within the next business day. You can also try alternative channels as given below. Please do connect with us on Chat for faster response. Your case reference #: 103196111 For Service and technical request. Please make sure mandatory information is shared as per the check list if not please share to avoid the delay. Service Check list you could download from the below link: - https://www.se.com/in/en/faqs/FAQ000219086/ For Latest Product Selection and Document Request Tool please refer the link given below: - https://www.se.com/in/en/faqs/FAQ000220894/ It is an automated email, and if you have already shared the information with us, please ignore this email, we will prioritize your request and acknowledge it with the complaint number. Best Regards ------------------------------------------------------------------------------------------------- Customer Care Centre ¦ Schneider Electric ¦ India ¦ Site: www.schneider-electric.com ¦Toll Free: 18001030011 / 18004254272 ¦ Email: customercare.in@se.com | 2023-09-09 | 2023-09-19 12:00 | No | Warranty | APL Apollo Building Products Pvt Ltd | Village Rigini Keseda Tehsil Simga Baloda Bazar Raipur Unit 1 | Raipur | 493113 | chhattisgarh | India FS ED&I CSP East Team SOMDEV & COMPANY RAIPUR | SOUMYA BEHERA_SOMDEV & COMPANY RAIPUR | Somdev & Company | the meter is not working properly so we replace the same. | Repair |  | 9- Service Validated | 2023-09-19 17:46 |  |  | 45 | INR | 45 | ENM POWER PRODUCTS
WO-11295615 | 104210880 | 2023-09-22 15:25 | 2023-09-22 | Switch not working | 2023-09-22 14:14 | IN8401_N | IN8401_N | IN8401_N |  | Switch not working Pl issue complaint no. 1. Name of Customer: Swapnil patil 2. Site Address: - flat no- 1105 Aishwaryam Comfort, Chinchwad - Akurdi Link Rd, opposite Yuvraj Motors, Maharashtra 411035 3. Name of contact person at site :- Swapnil patil 4. Contact Phone / Mob. No: - 7799606567 5. Defective product details:-IN8401 6. Product Make:- Zencelo 7. Nature of Defect: Switch not working 8. Shutdown availability if applicable :nil 9. Serial No: or DOM of -21514L 10. Dealer Name /OA no. /Invoice Details: - In warranty 11. Commissioned / Installed date:- NIL 12. Name & phone No: of person registering the complaint: Mr.Swapnil patil -7799606567 | 2023-09-22 | 2023-09-22 16:19 | No | Warranty | Swapnil Patil | flat no- 1105 Aishwaryam Comfort, Chinchwad - Akurdi Link Rd, opposite Yuvraj Motors, | Pune | 411035 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Kunal jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the Switches not working. it;s found stuck not changing contact. switches stuck again & again. this problem is not repairable. So Switches needs to be replaced. Required Material : IN8401- 03 nos | Repair |  | 9- Service Validated | 2023-09-23 11:21 | =S= Consig Fill up 226075025 |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11295857 | 104213999 | 2023-09-23 12:02 | 2023-09-22 | Socket Operating Issue | 2023-09-22 15:32 | P2005NS_N | P2005NS_N | P2005NS_N |  | COMPLAINT. Company Name & Complete Address with pin code - Where product is installed Saniket Buildcon The Rising kiwale site Mob- 7028667950 2 Contact Person at Site : Name & Mobile No. Mob- 7028667950 Alternate Mobile No : 3 Contact Person at Site - Email Address** sonali@srentp.com 4 Defective Product Model/Part No (Pls refer FAQ sheet ) P2005NS_N - 6A SOCKET LIVIA 5 Nature of Defect* - Defects Video and Photographs Livia Switch board & Socket not properly working. 6 Shutdown availability if applicable 7 POP - SE Authorised Partner Invoice soft copy Invoice # 9008518717 | 2023-09-22 | 2023-09-26 15:33 | No | Warranty | Saniket Saniket | MP6H+FF7, Kiwale, Ravet, Dehu Road | Pimpri-Chinchwad | 412101 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Kunal jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the Socket Operating Issue. socket internal shutter not holding pins. we insert the socket at that time immediately thrown the pin outside. inside shutter the not holding pins. so problem observed in socket. it's needs to be replaced. Required Material : P2005NS- 03 nos | Repair |  | 9- Service Validated | 2023-09-27 11:08 | =S= Consig Fill up 226086330 |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11299969 | 104229075 | 2023-09-23 15:21 | 2023-09-23 |  | 2023-09-23 09:49 | IN8401_N | IN8401_N | IN8401_N |  | Complaint Register- Sudheer Zencelo Name of Customer Sudheer Chembath Site Address Chembath House with pincode Kokkoor Post, Malapuram Dist Kerala-679591 Name of contact person at site sudheer Contact Phone / Mob. No: 9746998888 Defective product details IN8401- 1, IN8426UNS- 2, IN8481/16- 2 Nature of Defect Complaint Shutdown availability if applicable Distributor Name,Invoice # & Date 9008316501 | 2023-09-23 | 2023-09-26 15:47 | No | Warranty | Sudheer Chembath | Chembath House,Changaramkulam, alamkode panchayath road Kokkoor Post, Malapuram Dist-679591 | Malapuram | 679591 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Rejilesh APSMarketingCompany Calicut | APS Marketing Company | visited this site found zencelo switchs dolly crack and not working IN8401 8NOS IN8402 3NOS replaced problem solved | Repair |  | 8- Service Completed | 2023-09-26 15:50 |  |  | 85 | INR | 85 | ENM HOME DISTRIBUTION
WO-11301088 | 104229435 | 2023-09-23 13:12 | 2023-09-23 |  | 2023-09-23 11:14 | A9KF71463 | A9KF71463 | A9KF71463 |  | Product : A9KF71463 MCB Sr No. D2212 Problem : Knob Free Product : A9KF71463 MCB Sr No. D2212 Problem : Knob Free Not getting Power ON Chinar Electricals Industries Rangreth Sidco complex Srinagar,190001 Jammu and Kashmir PIN 190001 Mr. Pardeep 9888415588 | 2023-09-23 | 2023-09-23 13:16 | No | Warranty | Chinar Electricals Industries | Rangreth Sidco complex kashmir srinagar | Srinagar | 190007 | Jammu and Kashmir | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Ram Ashish Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the mcb found dolly free and capacitor found derated problem, Hence faulty replaced. EZ9F71463 - 1 nos MEHVCHDY250A44 - 1 nos Email : iqbalvalley@yahoo.com | Repair |  | 8- Service Completed | 2023-09-23 17:19 |  |  | 650 | INR | 650 | ENM HOME DISTRIBUTION
WO-11301218 | 104229774 | 2023-09-23 15:35 | 2023-09-23 |  | 2023-09-23 15:01 | A9R41463 | A9R41463 | A9R41463 |  | PLEASE REPLACE RCCB PLEASE CHANGE RCCB OF 63AMP 4POL RCCB 2NOS THESE RCCB IS UNDER WARENTY , Qty : 2 nos DOM : 2022, 2023 | 2023-09-23 | 2023-09-25 14:15 | No | Warranty | Laxmi Trading Co | Shop. No. 1 & 2 , Maruti Complex Near IOCL Petrol Pummp Chowkdi | Dahej | 392130 | Gujarat | India FS ED&I CSP West Team Jay Services Vadodara | Ghanshyam Kachiya_Jay Services Vadodara | Jay Services | We visited at site & checked Both RCCBs physically ok. Both are incomming & Outgoing terminals are ok. We observed both are dolly free. It is not repairable . Now we replace both from our distributor stock. | Repair |  | 9- Service Validated | 2023-09-25 14:16 | =S= Consig Fill up 226082540 |  | 123 | INR | 123 | ENM HOME DISTRIBUTION
WO-11305455 | 104246274 | 2023-09-25 16:59 | 2023-09-25 |  | 2023-09-25 16:15 | E8315C_6_WE | E8315C_6_WE | E8315C_6_WE |  | AvatarOn switches--2 nos , 3 socket Subhadra Trading--6 months back Not operating AvatarOn switches--2 nos , 3 socket Subhadra Trading--6 months back Not operating Site : 20, Centosa Neemland, Opp Balaji Kutir Bangalow, Chandkheda Kalol Highway Nr Narmada Canal, Adalaj, Gujarat 382421 Mr. JM Shah : 9825777724 | 2023-09-25 | 2023-09-29 12:52 | No | Warranty | Jindutt Jindutt | 20-Sentossa Neemland,Opp.Balaji Kutir Banglow, Sabarmati Kalol Highway, Nr.Narmada Canal Adalaj | Gandhinagar | 382421 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Mistri Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physically observed ok. E8315_6_WE SR NO : 05 2022 W06 observed switching on off mechsnism problem. 7 Nos. E8315_6_WE SR NO : 05 2022 W08 observed switching problem 06 Nos. E833L2 _WE _G8 SR NO : 2022 W06 observesd switching on off mechanism problem. ( 1 nOS ) so free replacement. E8334LR _WE _08 SR NO : 2022 W03 observed switching on off problem. so free replacemnet. ( 1 Nos ) . | Repair |  | 8- Service Completed | 2023-09-29 12:52 | =S= Consig Fill up 226086068 |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11305611 | 104249245 | 2023-09-26 09:06 | 2023-09-25 | NA | 2023-09-25 18:01 | A9N4P63C | A9N4P63C | A9N4P63C |  | Acti9 4p 63amp--1 no Invoice : Ashok Electrical--6 Dec 2022 Contact burn Acti9 4p 63amp--1 no Invoice : Ashok Electrical--6 Dec 2022 Contact burn Site : at Sec City Hall, Annexe, Kamla mill compound Gate No-4,Nr Passport office, 1st floor, Nxt to RR Cable , Worli, Maha 7303916786 / 9324902975 : Vaseem | 2023-09-25 | 2023-09-27 13:19 | No | Warranty | Vaseem Vaseem | at Sec City Hall, Annexe, Kamla mill compound Gate No-4,Nr Passport office, 1st floor, Nxt to RR Cable , Worli | Mumbai | 400018 | Maharashtra | India FS ED&I CSP West Team East India Power Engineers Mumbai | Akshya Vidhate_East India Power engineers Mumbai | East India Power Engineers (5043) | Visited the site & Checked the MCB found intarnal side 'Y' pole is heated & burnt. It's cause due to loose & poor fittment & not use proper lug for termination. This case not convered in under warranty replacement. | Repair |  | 8- Service Completed | 2023-09-27 13:32 |  |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11310513 | 104267871 | 2023-09-26 15:29 | 2023-09-26 | Validated By Prashant | 2023-09-26 12:57 | IN8401_N | IN8401_N | IN8401_N |  | Complain for sovergine tower Add- Sovergine tower, 1901 , Sovereign CHS Behind Galleria Mall, Central Ave, Hiranandani Gardens, Powai, Mumbai, Maharashtra 400076 Contact person - 8850561713 Faulty item - 6A Switch zencelo - 7pcs Arham Electricals--7 Feb 2023 | 2023-09-26 | 2023-09-28 12:44 | No | Warranty | Mr Pinkumar | Sovergine tower, 1901,Behind Galleria Mall, Central Ave, Hiranandani Gardens, Powai | Mumbai | 400076 | Maharashtra | India FS ED&I CSP West Team S K SERVICES Mumbai | Ganesh Tati_S K SERVICES Mumbai | S.K. Services (10237) | We Visited the site Product Ref No:-IN8401-5Nos Serial No:-23186,23210,23203-3Nos We check the material 6A 1Way switch properly not operating. We replace the product raised the ZVO | Repair |  | 9- Service Validated | 2023-09-28 12:45 | =S= Consig Fill up 226082438 |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-11314543 | 104280429 | 2023-09-27 14:38 | 2023-09-27 |  | 2023-09-27 09:52 | A9N2P32C | A9N2P32C | A9N2P32C |  | MCB TP not working Hi, i purchased a 32 Amp MCB TP on 1st September 2023 and i am facing issue as the mcb is not working. Kindly solve my problem as soon as possible. I am attaching the bill with this email for your reference. GS CHHABRA KNITWEAR Address- 722, B-12, Brown road, Adjoining red cross Ludhiana, Punjab, India Mobile number- +91 9417530860 Invoice : Brij Electricals--1/9/2023 32 Amp MCB | 2023-09-27 | 2023-09-29 11:07 | No | Warranty | G.S. CHHABRA KNITWEARS | B-12-722/ Brown Road, Addjoining Red Cross null | Ludhiana | 141003 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the mcb found not getting output. Hence faulty replaced. A9N2P32C - 1 nos. A9N3P32C - 1 nos. email : shubham.gumber2@gmail.com | Repair |  | 8- Service Completed | 2023-09-29 11:13 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11316551 | 104304138 | 2023-09-27 19:15 | 2023-09-27 |  | 2023-09-27 13:19 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Smart Door Installation For Rohini Kamath Name of Customer Rohini Kamath Site Address Villa 74, Secret Soil by living walls, Off hennur main road, sonam layout, bamgalore-560077 Name of Contact Person at the Site Rohini Kamath Customer Mail ID Contact Number 9880416310 Smart Doorbell--1 no Saga infotech--22 May 2023 Not operating | 2023-09-27 | 2023-09-28 11:24 | No | Warranty | Rohini Kamath | Villa 74, Secret Soil by living walls, Off hennur main road, sonam layout, | Bangalore | 560077 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Mohammad Riyaz_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | we had visited the site and checked the customer reported VDP found notification not triger due to VDP logged out in mobile .we login and checked working ok . | Repair |  | 8- Service Completed | 2023-09-28 17:46 |  |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-11316621 | 104305486 | 2023-09-27 16:07 | 2023-09-27 |  | 2023-09-27 13:50 | A9KF71216 | A9KF71216 | A9KF71216 |  | Model : A9KF71216--1 no Sr : D2139 1 pole not working Model : A9KF71216--1 no Sr : D2139 1 pole not working Site : Devraj Negi Stone Crusher VPO Gojjar,Nr Gurudwara, Dist Sirmaur Paota Sahib 173025 Mr.Saurab negi : 7018171800 saurabhmyfriend@gmail.com | 2023-09-27 | 2023-09-28 12:08 | No | Warranty | Devraj Negi Stone Crusher | VPO Gojjar,Nr Gurudwara, Paonta Sahib null | Sirmaur | 173025 | Himachal Pradesh | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the mcb found phase missing. Hence faulty replaced. A9N2P16C - 1 Nos. email : saurabhmyfriend@gmail.com | Repair |  | 8- Service Completed | 2023-09-28 15:03 |  |  | 125 | INR | 125 | ENM HOME DISTRIBUTION
WO-11316653 | 104301572 | 2023-09-27 14:34 | 2023-09-27 | This is not product issue . | 2023-09-27 14:02 | E8315_6_WG | E8315_6_WG | E8315_6_WG |  | COMPLAIN ? E8315_6_WG - QTY - 01 (Meena Creations Private Limited.) Name of Customer M/S Meena Creations Private Limited 2 Site Address S-1,902, happy excelencia, Vesu, Surat - 395007, SURAT Contact Phone / Mob. No: 9825422251 3 Name of contact person at site Meena Madam 5 Defective product details E8315_6_WG - QTY - 01 6 Product Make SCHNEIDER-6A 2/3 PIN SW SKT. WG 7 Nature of Defect NOT WORKING PROPERLY 8 Shutdown availability if applicable 9 Warranty status UNDER WARRANTY 10 Commissioned / Installed date 11 Serial No: or DOM of the product BILL NO - : 9516/22-23 DATE - 27-01-2023 | 2023-09-27 | 2023-09-27 16:48 | No | Warranty | Meena Creations Private Limited | S-1,902, happy excelencia,Vesu null | Surat | 395007 | Gujarat | India FS ED&I CSP West Team VARDHAMAN ELECTROSOFT Vadodara | MAHENDRA SINGH VARDHAMAN ELECTROSOFT Vadodara | VARDHAMAN ELECTROSOFT | we visited the site we checked switch and it is physically ok .when we open the switch its base plate is not insulated properly when the switch is placed on its alignment gets spoiled. so this is not a product issue | Repair |  | 8- Service Completed | 2023-09-27 16:55 |  |  | 26 | INR | 26 | ENM HOME DISTRIBUTION
WO-11316692 | 104306499 | 2023-09-28 12:48 | 2023-09-27 |  | 2023-09-27 14:17 | EZ9F71463 | EZ9F71463 | EZ9F71463 |  | Model : EZ9F71463 Ajex Electricals---3/4/2023 Issue : Dolly free Model : EZ9F71463 Ajex Electricals---3/4/2023 Issue : Dolly free Site : Jaswant Cold Storage C-5,Laurance Road Industrial Area, Keshavpuram , delhi 110035 Mr.Pramod Singh : 8826228369 siddhicoldchain@gamil.com | 2023-09-27 | 2023-09-28 12:50 | No | Warranty | Jaswant Cold Storage | C-5,Laurance Road Industrial Area, Keshavpuram null | Delhi | 110035 | Delhi | India FS ED&I CSP North Team Sharma Electric Works Delhi | Pradeep Sharma_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mcb found working ok. Email : id not provided by customer . | Repair |  | 8- Service Completed | 2023-09-28 13:02 |  |  | 20 | INR | 20 | ENM HOME DISTRIBUTION
WO-11317091 | 104310317 | 2023-09-27 16:38 | 2023-09-27 | NA | 2023-09-27 16:23 | A9N4P63C | A9N4P63C | A9N4P63C |  | A9N4P63C--1 nos Phase missing D2243 A9N4P63C--1 nos Phase missing D2243 Site : C-wing, 104, Matra Chayaa Housing society, Pooja Nagar, Mira Road East Thane 401107 9324902975 : Vaseem | 2023-09-27 | 2023-09-28 15:13 | No | Warranty | Mr Vaseem | C-wing, 104, Matra Chayaa Housing society, Pooja Nagar, Mira Road East | Thane | 401107 | Maharashtra | India FS ED&I CSP West Team East India Power Engineers Mumbai | Ratnesh Shigvan East India Power engineers Mumbai | East India Power Engineers (5043) | Visited the site & checked the MCB and found the input side terminal heated & burnt. This burnt condition occurs due to poor tightness & it will be not covered in under warrnaty. | Repair |  | 8- Service Completed | 2023-09-28 15:23 |  |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-11321848 | 104330035 | 2023-09-28 11:50 | 2023-09-28 |  | 2023-09-28 11:15 | A9N3P63C | A9N3P63C | A9N3P63C |  | MCB Complaint | 2023-09-28 | 2023-09-28 11:52 | No | Warranty | Sunny KUMAR | H no. D-156, Sunshine Society GH 21 | Sirohi | 307001 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Sunny Sharma Sharma Electric Jaipur | Sharma Electric Works | Checked the mcb found not giving output due to dolly free and phase missing, Hence faulty replaced. A9N3P63C - 1 nos A9N4P16C - 1 nos A9N4P32C - 1 nos A9N2P63C - 1 nos Email : | Repair |  | 8- Service Completed | 2023-09-28 16:02 |  |  | 415 | INR | 415 | ENM HOME DISTRIBUTION
WO-11321974 | 104330232 | 2023-09-28 15:02 | 2023-09-28 |  | 2023-09-28 12:20 | A9N3P16C | A9N3P16C | A9N3P16C |  | #COMPLAIN LETTER COMPANY NAME - SHIVAM TECHNOMECH ADDRESS- 136, ABHISHREE INDUSTRIAL ESTATE B/H , GVMM ODHAV G.I.D.C , AHMEDABAD 382415 CON NUM- 9909941905 , 9638891603 CATALOG NUM SERIAL NUM PROBLEM A9N3P16C 9631355 POLE PROBLEM Ahmedabad Electric--27 Sep 2023 | 2023-09-28 | 2023-09-29 15:31 | No | Warranty | SHIVAM TECHNOMECH | 136, ABHISHREE INDUSTRIAL ESTATE B/H , GVMM ODHAV G.I.D.C null | AHMEDABAD | 382415 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Mistri Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physically observed ok. but mcb dolly free so free replacment for customer satisfaction. | Repair |  | 8- Service Completed | 2023-09-29 15:31 | =S= Consig Fill up 226093939 |  | 10 | INR | 10 | ENM HOME DISTRIBUTION
WO-11322157 | 104330938 | 2023-09-28 15:07 | 2023-09-28 |  | 2023-09-28 13:38 | A9KF71425 | A9KF71425 | A9KF71425 |  | 25A FP MCB (A9KF71425) POLE MALFUNCTION A9KF71425 DD-2023-W01-4-5 I/we had purchased 25A FP MCB (A9KF71425) from ?MAHAVIR SALES CORPORATION? Ankleshwar, Gujarat on 02/08/2023 [Invoice Attached herewith]. Now, on 25/09/2023 while the MCB was ON, the Machine/Motor with which it was connected to, suddenly stopped working. Upon checking the electrical connection by electrician it was found that out of the four poles in the MCB one had stopped working, and as result the MCB was giving output of only 2 phase out of 3 phase required. Please note that there were no fluctuations in current or malfunctions in motor as other machines were also running simultaneously without any fault at the same time. | 2023-09-28 | 2023-09-30 10:31 | No | Warranty | P. J. TECHNOCRAT PRIVATE LIMITED | D-2/E/292, Opposite Swastik Packaging,Dahej-II GIDC Industrial Estate, Village: Galenda null | Bharuch | 392130 | Gujarat | India FS ED&I CSP West Team Jay Services Vadodara | Ghanshyam Kachiya_Jay Services Vadodara | Jay Services | We checked above MCB found ON-OFF Operation found ok. Checked MCB I/C & O/g all pole terminals found ok. We observed that MCB Y phase pole continuity open. It is not repairable. Now we replaced MCB from our distributor stock. | Repair |  | 8- Service Completed | 2023-09-30 10:34 | =S= Consig Fill up 226090677 |  | 107 | INR | 107 | ENM HOME DISTRIBUTION
WO-11327338 | 104363281 | 2023-09-29 14:40 | 2023-09-29 | This is not product issue . Resolve the issue | 2023-09-29 13:49 | UNSMTSTART2M_WE | UNSMTSTART2M_WE | UNSMTSTART2M_WE |  | Model : Unica switches grey--15 nos Invoice : Modular concept--9 months back Not operating Model : Unica switches grey--15 nos Invoice : Modular concept--9 months back Not operating Site : 84, Motiphalli, Nr Roopmata Temple, Palgam,Surat Ankit : 9662030137 | 2023-09-29 | 2023-09-30 21:30 | No | Warranty | Mr Ankit | 84, Motiphalli, Nr Roopmata Temple, Palgam | Surat | 394510 | Gujarat | India FS ED&I CSP West Team VARDHAMAN ELECTROSOFT Vadodara | MAHENDRA SINGH VARDHAMAN ELECTROSOFT Vadodara | VARDHAMAN ELECTROSOFT | we visited the site and find that switch is physically ok . when i check i found that switch has loose connection . after that we tight the connection and found ok. | Repair |  | 8- Service Completed | 2023-09-30 13:46 |  |  | 10 | INR | 10 | ENM HOME DISTRIBUTION
WO-11305256 | 104235974 | 2023-09-25 16:35 | 2023-09-25 | As per sr no product is out of warranty | 2023-09-25 15:24 | ATV610D18N4 | ATV610D18N4 | ATV610D18N4 | 4000900JM220700843 | Customer Complain ATV-610 4000900JM220700843 ATV610D18N4E | 2023-09-25 | 2023-09-26 16:04 | No | Warranty | Insecticides (India) Ltd | Plot no. CH/21, GIDC Industrial Estate, Dahej, Tal Vagra | Bharuch | 392130 | Gujarat | India FS ED&I CSP West Team VARDHAMAN ELECTROSOFT Vadodara | MAHENDRA SINGH VARDHAMAN ELECTROSOFT Vadodara | VARDHAMAN ELECTROSOFT | we visited the site and observed that trip on "SCF 3" fault without load .during site report we found that ATV320 rectifier section found ok in drive power ON time "4" and run time "0" in case accelerate to team adn will update further update as soon as possibel. | Repair |  | 9- Service Validated | 2023-09-27 16:10 |  |  | 270 | INR | 270 | Industrial Automation Ops
WO-11305349 | 104239513 | 2023-09-25 16:10 | 2023-09-25 | Part Order request Validated by Pradip kumar Vagela Sir | 2023-09-25 15:40 | ATV320U07N4C | ATV320U07N4C | ATV320U07N4C | HL224191304 | complaint for VFD Altivar 320 ATV320U07N4C HL2241913043 | 2023-09-25 | 2023-09-26 16:43 | No | Warranty | SM Food Engineering Pvt Ltd | Patwari Halka No. 36, Survey No. 381, Village Limbodagari, | Indore | 453111 | Madhya Pradesh | India FS ED&I CSP West Team ABR Technical Service Indore | Lalu Sen_ABR Tecneical Services Indore | ABR Technical Services (9574) | Reached at site at panel builder office and checked after giving 3 phase supply and found its showing SCF3 .Fault Then we checked Rectifier /IGBT section found OK .Then we checked internally and found No any burning mark. We are unable to take any Technical details. because VFD at panel builder office. then collected SoMove file and found all fault ground short circuit (SCF3) Power on time -42 H Run time -18 h (SoMove file alt) as per customer VFD used conveyor belt ,so as per observation VFD PCB components malfunctioning .thats why VFD showing SCF3 so we recommended to replace 1 No. VFD | Repair |  | 9- Service Validated | 2023-09-27 16:44 | =S= Consig Fill up 226089223 |  | 30 | INR | 30 | Industrial Automation Ops
WO-11305479 | 104236872 | 2023-09-25 17:23 | 2023-09-25 |  | 2023-09-25 16:30 | VW3A1111APZ | VW3A1111APZ | VW3A1111APZ |  | VW3A111 Qty:1 P: Display issue Kindly check invoice at site VA Tech Wabag Limited 150MLD STP BWSSB K&C Valley, B.nagasandra, via challagatta, yemmalur post, Near Old HAL AIRPORT ROAD bangalore-560037 Mr Venkatesan (8249692589) / Mr Sathishkumar (9980369467) | 2023-09-25 | 2023-09-26 10:17 | No | Warranty | VA Tech Wabag Limited | 150MLD STP BWSSB K&C Valley, B.nagasandra, via challagatta, yemmalur post, Near Old HAL AIRPORT ROAD | Bangalore | 560037 | Karnataka | India FS ED&I CSP South Team Vamtech Energy Solutions Private Limited Bengaluru | Yuvraj Naik.R Vamtech Energy Solutions Private Limited Bengaluru | VAMTECH Energy Solutions (P) Limited | Being Plain text display terminal not working contact card not working control card to be changed. Email id: v_venkatesan@wabag.in | Repair |  | 8- Service Completed | 2023-09-27 10:20 |  |  | 28 | INR | 28 | Industrial Automation Ops
WO-11305520 | 104235802 | 2023-09-25 21:53 | 2023-09-25 |  | 2023-09-25 16:54 | ATV310HD22N4E | ATV310HD22N4E | ATV310HD22N4E | 88220456606 | ATV 310 VFD : Freq Vs Output issue : NGL Finechem : Sonepar ATV310HD22N4E Serial No : 882204566061 | 2023-09-25 | 2023-09-28 15:03 | No | Warranty | Vetfar Pharmaceutical | Plot k37, Bachu Bhai Dube Industrial Estate | Palghar | 401506 | Maharashtra | India FS ED&I CSP West Team R P Electrical Mumbai | Digambar Vishe R P Electrical Mumbai | R P Electrical | Checked ATV310HD22N4E for not getting output i.e. output voltage low. Took thyristor test found ok. Factory reset the drive then measured voltage across. Motor terminal found Ok. So again customer set parameter to check again output was still low. Then connected motor to check motor was not rotating frequency was fluctuating. The factory reset the drive and then run motor, motor running Ok. | Repair |  | 8- Service Completed | 2023-09-29 15:07 |  |  | 93 | INR | 93 | Industrial Automation Ops
WO-11309019 | 104239852 | 2023-09-27 15:57 | 2023-09-26 |  | 2023-09-26 10:39 | ATV12H018M2 | ATV12H018M2 | ATV12H018M2 | 8B2305912079 | IMA PG COMPLAINT ATV12H018M2, ATV12H018M2 Dt.17.09.2023 | 2023-09-26 | 2023-09-28 12:17 | No | Warranty | Dr. Reddy,s laboratory Ltd | FTO-06 Khol Nalagarh Road Mauja Thana | Baddi | 173205 | Himachal Pradesh | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Vinod Kumar_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked two nos drives installed in panel with DG found working ok on same to another drives on other panel showing OSF fault with DG. Advise customer to checked there wiring & machine. our product is heathy. email : id not provided by the customer. | Repair |  | 8- Service Completed | 2023-09-28 12:34 |  |  | 55 | INR | 55 | Industrial Automation Ops
WO-11309926 | 104240127 | 2023-09-26 17:56 | 2023-09-26 |  | 2023-09-26 10:54 | ATV310HU55N4E | ATV310HU55N4E | ATV310HU55N4E | 8B2242523007 | Log the complaint of drive ATV310HU55N4E serial no. - 8B2242523007 | 2023-09-26 | 2023-09-27 11:36 | No | Warranty | Agarwal and sons beverages private limited. | Plot no. UPSIDC 234/56 | VARANASI | 221008 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Abhishek Patel Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found VFD is ok, its having MCB faulty. | Repair |  | 8- Service Completed | 2023-09-27 11:43 |  |  | 330 | INR | 330 | Industrial Automation Ops
WO-11310130 | 104268006 | 2023-09-26 12:46 | 2023-09-26 |  | 2023-09-26 10:57 | ABL2REM24065K | ABL2REM24065K | ABL2REM24065K | 8A-2022-w20 6161B007 | Product : :ABL2REM24065K Sr No. 8A-2022-w20 6161B007 DOM May 2022 Fault:- Not powering ON K-SPARK AUTOMATIONS Shed No. 4, Step GNDEC Backside GNE College, Gill Garden Road, Ludhiana,Punjab. Pin 143526 Mr.Bhupinder / Nirmal Singh 9815974402 | 2023-09-26 | 2023-09-26 13:42 | No | Warranty | K-SPARK AUTOMATIONS | SHOP NO. 3 , KNOWLEDGE PARK , GNA COLLEGE | LUDHIANA | 141006 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the PLC found not power up and mcb found dolly free, Hence faulty replaced. ABL2REM24065K -1 Nos. EZ9F71432 - 3 Nos. EZ9F71440 - 2 Nos. Email : patialelectrical@gmail.com | Repair |  | 8- Service Completed | 2023-09-27 06:23 |  |  | 25 | INR | 25 | Industrial Automation Ops
WO-11310299 | 104247619 | 2023-09-26 13:34 | 2023-09-26 |  | 2023-09-26 12:03 | ATS22C32Q | ATS22C32Q | ATS22C32Q | 8B2327226003 | soft starter sscr fault ATS22C32Q problem - SSCR FAULT ( 1 PHASE PASS THE CONTINUITY ) serial no - 8B2327226003 | 2023-09-26 | 2023-09-27 11:46 | No | Warranty | water treatment plant (WTP) | ram bagh chauraha agra main highway null | Agra | 282003 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Aman Khare_Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found soft starter having one phase bypass contactor stuck so we open and remove the bypass contactor , now soft starter working fine. | Repair |  | 8- Service Completed | 2023-09-27 11:51 |  |  | 350 | INR | 350 | Industrial Automation Ops
WO-11310385 | 104246689 | 2023-09-26 14:48 | 2023-09-26 |  | 2023-09-26 12:33 | ATV310HU55N4E | ATV310HU55N4E | ATV310HU55N4E | 8B2323006280 | Complaint for 5.5 KW VFD ATV310HU55N4E 8B2323006280 8B2323006325 | 2023-09-26 | 2023-09-30 13:14 | No | Warranty | GS enterprises- II | 6-A SHIVAJI PARK MOTI NAGAR KARAMPURA INDUSTRIAL AREA | Delhi | 110015 | Delhi | India FS ED&I CSP North Team Saffron Automation Delhi | Yavnish Tyagi Saffron Automation Delhi | Saffron Automation(18001) | Check the drive and found drive static test is ok. After providing the input supply drive is power up and show ready. Run the drive and found drive trip on BLU fault. Reset the drive and re-program the drive and check the drive and found drive run successfully but after some time drive F011 fault. We replace the faulty drive with new. | Repair |  | 8- Service Completed | 2023-09-30 15:15 |  |  | 32 | INR | 32 | Industrial Automation Ops
WO-11310567 | 104270696 | 2023-09-26 13:47 | 2023-09-26 |  | 2023-09-26 13:17 | RXM4LB2P7 | RXM4LB2P7 | RXM4LB2P7 | 8A-2020-W43-3A-X | FW: HYD111ROMP01 - MEDS-0.1B - MSDB-0.1B3 "Limit Switch Fail alarm on S1 breaker" Warranty Part code : RXM4LB2P7 Serial no : 8A-2020-W43-3A-X Issue:RXM Relay coil is not picking up. No change of conatcts happens. Site Address:Amazon Data Services India Pvt Ltd (HYD-111) Survey No 190, Chandanvelly Village, Hytabad, Shabad Mandal, Rangareddy District, Telangana - 509217" Christo Thomas - 9074737395 8547733458 christo.thomas1@se.com Navaneethan Rajendran - +91-9004609800 | 2023-09-26 | 2023-09-29 12:00 | No | Warranty | Amazon Data Services India Private Limited | Survey Number 190(P) of Chandanvelly Village / 195(P) of Hythabad Village, Shabad Mandal, Ranga Reddy District, | Shabad Mandal | 501503 | Telangana | India FS ED&I CSP South Team Sumanth Electrical Services Hyderabad | Madhu Mantena_SUMANTH ELECTRICAL SERVICES HYDERABAD | Sumanth Electrical Services | Visited the Site and Inspected the Schneider Electric- RXM4LB2P7-01 No's. Here in our observation we found that the Pla Relay is getting limit switch fail alarm or S1. We have replaced with New RXM4LB2P7-01 No's and we have checked the ON/OFF operations which found OK. Complaint is closed. | Repair |  | 8- Service Completed | 2023-09-29 17:35 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 55 | INR | 55 | Industrial Automation Ops
WO-11310875 | 104244218 | 2023-09-29 06:36 | 2023-09-26 | We have inspected the Soft Starter. SOFT STARTER: ATS22C41Q ( Somove file collected) Motor: 160KW, 1490RPM, 258A Delta, Duty: S1 (Nameplate collected). We have inspected the soft stater operation and load measurement. Soft stater giving STF error on the run command. We have changed the ACC & TLs settings. Softstater working ok. | 2023-09-26 15:22 | ATS22C41Q | ATS22C41Q | ATS22C41Q | 882233094005 | ATS22C410 Qty:1 P: Not Working kidnly check invoice at site M/s JURALA ORGANIC FARMS AND AGRO INDUSTRIES LLP CHITANUR VILLAGE,MARIKAL MANDAL, NARAYANPET DISTRICT, Telangana - 509353 Mr.Amit Kumar :- Mobile no. 6393725225 Mr. Venkat Ramana :- Mobile No. 9960400920 Mr. Akshay Kulkarni :- Mobile No. 8660853721 / 7204456230 | 2023-09-26 | 2023-09-28 06:58 | No | Warranty | JURALA ORGANIC FARMS AND AGRO INDUSTRIES LLP | CHITANUR VILLAGE,MARIKAL MANDAL,Narayanpet | Mahabubnagar | 509353 | Telangana | India FS ED&I CSP South Team ENERPRO ENGINEERING SOLUTIONS Vijayawada | ES Chowdary_ENERPRO ENGINEERING SOLUTIONS VIJAYAWADA | Enerpro Engineering Solutions - 500012682 | THE SOFT STARTER NOT WORKING | Repair |  | 8- Service Completed | 2023-09-29 07:02 |  |  | 279 | INR | 279 | Industrial Automation Ops
WO-11317183 | 104311198 | 2023-09-29 10:46 | 2023-09-27 |  | 2023-09-27 17:02 | ATV930C16N4C | ATV930C16N4C | ATV930C16N4C | N22220400285 | Complaint 09-03 104125661 ATV930C16N4C Serial No. N22220400285 | 2023-09-27 | 2023-09-29 17:18 | No | Warranty | Satia Industries Limited | Village Rupana, Muktsar-Malout road, | Muktsar | 152026 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the vfd found working ok. email : id not provided by the customer. | Repair |  | 8- Service Completed | 2023-09-29 17:30 |  |  | 151 | INR | 151 | Industrial Automation Ops
WO-11317219 | 104301339 | 2023-09-29 13:24 | 2023-09-27 |  | 2023-09-27 17:26 | ATV340D55N4E | ATV340D55N4E | ATV340D55N4E | 4.0506e+17 | Complain regarding VFD ATV340D55N4E : 2 Serial No : 405060088223002033 | 2023-09-27 | 2023-09-29 15:08 | No | Warranty | Kveetech enterprises | Building No 191, Gala No 1 and 2, Indian Corporation Compound, Opp.Gajajan Petrol Pump, Dapode | Bhiwandi | 421302 | Maharashtra | India FS ED&I CSP West Team R P Electrical Mumbai | Digambar Vishe R P Electrical Mumbai | R P Electrical | Checked ATV340D55N4E for analog output not generated. When drive is started drive showing SOC state, showing for absence of motor when off set to not triggered. As motor was not connected and for checking it must be on Function Inactive. As parameter changed to function inactive analog output was generated properly. Also showing CIL as motor type was not proper. SET to V/F VC spots then drive was running properly. | Repair |  | 8- Service Completed | 2023-09-29 15:14 |  |  | 36 | INR | 36 | Industrial Automation Ops
WO-11317229 | 104308823 | 2023-09-28 12:19 | 2023-09-27 |  | 2023-09-27 17:31 | ATS22C11Q | ATS22C11Q | ATS22C11Q | 8B2141330024 | Soft starter issue at TATA IGBT 8B2141330024 ATS22C | 2023-09-27 | 2023-09-28 15:16 | No | Warranty | AEON INTEGRATED BUILDING DESIGN CONSULTANTS LLP | Plot No. A122, Sector 136 | Noida | 201304 | Uttar Pradesh | India FS ED&I CSP North Team Saffron Automation Delhi | Yavnish Tyagi Saffron Automation Delhi | Saffron Automation(18001) | As per customer confirm customer schedule we reach the site, but not found the subject complain product not available at site. We suggest to customer please confirm the material at site then login again the complaint. We close the complaint. | Repair |  | 8- Service Completed | 2023-09-28 16:05 |  |  | 25 | INR | 25 | Industrial Automation Ops
WO-11320212 | 104329457 | 2023-09-28 10:45 | 2023-09-28 |  | 2023-09-28 10:24 | ATV340D30N4E | ATV340D30N4E | ATV340D30N4E | 88222936009 | RE: WO for SAIL IISCO Banpur, WB Dear Team, Kindly arrange a WO under Assessment- Inspection category. Site details- Customer Name: STEEL AUTHORITY OF INDIA LIMITED Customer Location: STEEL AUTHORITY OF INDIA LIMITED - SITE Address: Sail Iisco Steel Plant, Burnpur, Asansol West Bengal 713325 Bardhaman India Contact Name: Utpal Das Contact phone number: 9434776586. Main Installed Product: ATV340D30N4E Main IP Serial Number: 88222936009 Work reason Modbus commination and VFD healthiness checked. | 2023-09-28 | 2023-09-30 16:46 | No | Warranty | STEEL AUTHORITY OF INDIA LIMITED | Sail Iisco Steel Plant, Burnpur, Asansol | Bardhaman | 713325 | West Bengal | India FS ED&I CSP East Team SREYAM SERVICES BHATPARA | AMIT BHATTACHARYA_SREYAM SERVICES BHATPARA | Sreyam Services(8513) | AFTER SITE VISIT 1 NOS DC BUS BOARD AND 1 NOS POWER BOARD REPLACE BY NEW ONE AND DEFFECTIVE MATERIAL IS COLLECTED. | Assessment/ Inspection | Data Collection | 8- Service Completed | 2023-09-30 16:51 |  |  | 220 | INR | 220 | Industrial Automation Ops
WO-11320733 | 104314054 | 2023-09-28 13:13 | 2023-09-28 |  | 2023-09-28 10:45 | ATV310HU22N4E | ATV310HU22N4E | ATV310HU22N4E | 8B2139596288 | Attend customer complaint urgently-Waves Aircon Pvt. Ltd. (ATV310HU22N4E- Serial no.- 8B2139596288) | 2023-09-28 | 2023-09-30 14:59 | No | Warranty | Waves Aircon | Wave 1 Mall Sec 18, Opposite Radisson Hotel null | Noida | 201301 | Uttar Pradesh | India FS ED&I CSP North Team Saffron Automation Delhi | Yavnish Tyagi Saffron Automation Delhi | Saffron Automation(18001) | Check the drive and found drive static test is ok with PA+ . Then we giving the 3 phase input supply in drive and found (- - 11 Fault) . So drive is faulty. We replace the faulty drive with new. Mail Id. measales@maxgroup.co.in | Repair |  | 8- Service Completed | 2023-09-30 15:22 |  |  | 22 | INR | 22 | Industrial Automation Ops
WO-11322257 | 104330116 | 2023-09-28 17:14 | 2023-09-28 |  | 2023-09-28 14:25 | ATV610D75N4 | ATV610D75N4 | ATV610D75N4 |  | ATV610D75N4 4001500JM233202635 Qty:1 P: Not powring on Power Control Equipments Unit 2 No. 57, 3rd Road, Ist phase Jigani Indl. Area, AnekalTaluk, Bengaluru - 560105 Mr. Gururaj Mob No. : 7975693778 RAVI@POOJAPOWER.COM | 2023-09-28 | 2023-09-30 15:01 | No | Warranty | Power Control Equipments Unit - 2 | Plot 40-A, 57 Vaddarapalya 1st Phase, 3rd Road, Jigani Industrial Area, | Bangalore | 562106 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | C Gunasekaran_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | We had visited the site and checked the customer reported VFD .found starting capacitor charging sound came.we dismantle and fixed the same and checked sound not came.working properly,there is no issues with our product. | Repair |  | 8- Service Completed | 2023-09-30 15:10 |  |  | 45 | INR | 45 | Industrial Automation Ops
WO-11322575 | 104338537 | 2023-09-29 10:50 | 2023-09-28 |  | 2023-09-28 16:50 | ATS22D17Q | ATS22D17Q | ATS22D17Q | 8B2304 | Display not come ATS22D17Q SERIAL NO. - 8B2304 PROBLEM - display not come | 2023-09-28 | 2023-09-29 12:36 | No | Warranty | IMSE PVT LTD | IND AREA 1/2 PLOT NO 7879,Jalun, | Jalaun | 285001 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Aman Khare_Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found Soft starter is ok, its having site issue. | Repair |  | 8- Service Completed | 2023-09-29 12:37 |  |  | 310 | INR | 310 | Industrial Automation Ops
WO-11324237 | 104334247 | 2023-09-29 16:49 | 2023-09-28 |  | 2023-09-28 21:32 | ATV310HU15N4E | ATV310HU15N4E | ATV310HU15N4E |  | ATV310HU15N4E 8B2319533155 Qty:1 P: Not powring on. Pac Systems and Solutions No-59, 4th Cross, 8th Main, 3rd Phase Peenya Industrial area Bangalore - 560058 Mr. Rajshekar Mob No. : 8970268649 santhosh@poojapower.com | 2023-09-28 | 2023-09-30 18:00 | No | Warranty | Pac Systems and Solutions | No-59, 4th Cross, 8th Main, 3rd Phase Peenya Industrial area null | Bangalore | 560058 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | C Gunasekaran_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported 1.5kw drive taken the cold test values found ok. Checked input and output voltages found ok .internal pcb board found ok. Checked the on, off operations | Repair |  | 8- Service Completed | 2023-09-30 19:37 |  |  | 30 | INR | 30 | Industrial Automation Ops
WO-11325740 | 104344214 | 2023-09-29 11:10 | 2023-09-29 | Only invoice number provided by customer , invoice not provided. | 2023-09-29 10:25 | ZARC01 | ZARC01 | ZARC01 | 2022W45 | Dear Team, Please generate a service complaint and do needful for visit of our service engineer urgently. Product ref. : ZARC01 Ser. No. : 2022W45 Problem : Not changing with ZART8L Customer : Konex Material Handling Systems LLP Plot No. 17, Shreeji Industrial Park, Opp. Swagat Estate, Kujad Bakrol Road, Bakrol, Tal - Daskroi, Dist. Ahmedabad ? 382430, Gujarat, India. Contact person : Nitin Solanki - 9925002119 Thanks & Regards, Nitin Solanki (M) 9925002119 Authorized Channel Partner of Schneider Logo - Super Global Services | 2023-09-29 | 2023-09-29 14:40 | No | Warranty | Konex Material Handling Systems LLP | Plot No. 17, Shreeji Industrial Park, Opp. Swagat Estate, Kujad Bakrol Road, Bakrol, Tal - Daskroi, | Ahmedabad | 382430 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Nijesh Patel_Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physically observed ok. charger connect with remote but battery led not glowing. so change the charged and trial taken working satisfactory. as per serial dom charger out of warranty . customer give invoice no schneider to automation control solution INVOICE AA2720119674 DTD 28/11/2022 .automation and control solution to konex material invoice AA/1223/22-23 dtd 10/12/2022. so problem in ratio remote charger . further action taken by scneider benefit of doubt free replacement. | Repair |  | 8- Service Completed | 2023-09-29 14:41 | =S= Consig Fill up 226096372 |  | 15 | INR | 15 | Industrial Automation Ops
WO-11327064 | 104338988 | 2023-09-29 12:45 | 2023-09-29 |  | 2023-09-29 11:46 | TM200C24T | TM200C24T | TM200C24T | WX10852230621033 | service complaint TM200C24T TM200C24T SL.NO:-WX 10852 23 06 2 1033 24V | 2023-09-29 | 2023-09-30 15:37 | No | Warranty | SRINIVASA ELECTRICALS | 14-1-14, OPP. ANANDA BHARATI GROUNDS, CINEMA ROAD, | KAKINADA | 533001 | Andhra Pradesh | India FS ED&I CSP South Team Voltamp Electrical Works Visakhapatnam | Chinni SaiKumar_VOLT AMP ELECTRICAL WORKS Visakhapatnam | Voltamp Electrical Works | Visited the site and found above the PLC 24V controller is power up issue so today we have given the 24V input voltage that time PLC module is power upend and module indicating load lights is glow so that module is working fine we find problem customer input voltage issue so we are closing the issue | Repair |  | 8- Service Completed | 2023-09-30 15:39 |  |  | 170 | INR | 170 | Industrial Automation Ops
WO-11305617 | 104246067 | 2023-09-26 11:11 | 2023-09-25 |  | 2023-09-25 18:03 | A9KESND12 | A9KESND12 | A9KESND12 |  | Distribution Locking Problem | 2023-09-25 | 2023-09-26 13:42 | No | Warranty | Tirupati Agencies | 13, Press Complex, A.B.Road | Indore | 452010 | Madhya Pradesh | India FS ED&I CSP West Team ABR Technical Service Indore | Chirag Jain_ABR Tecneical Services Indore | ABR Technical Services (9574) | Reached at site and checked distribution board and found its not locking properly. Then we checked lock were ok. Then we checked and found lock not working due to proper gap not available in wall and DB. Also found when we locking wall putty comes between DB base and door. So we cleared gap in-between and also cleaned dust of putty and checked 4-5 times now DB lock working properly. As per our primary observation it's not product issue lock not working due to external reasons so we resolved it and now we are closing this case. | Repair |  | 9- Service Validated | 2023-09-26 13:44 |  |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-11305631 | 104238205 | 2023-09-27 15:59 | 2023-09-25 |  | 2023-09-25 18:14 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Automation and Smart Door Bell not working: Mr. Naveen Sobti, Ambala | 2023-09-25 | 2023-09-27 17:17 | No | Warranty | Sobti Enterprises | Sena Nagar, Ambala City | Ambala | 134007 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Ram Ashish Sharma Electric Chandigarh | Sharma Electric works(1003) | checked the vdp found humming sound issue. hence faulty, replaced. IH100WFVDP - 1 Nos. email :stancab@gmail.com | Repair |  | 8- Service Completed | 2023-09-28 16:42 |  |  | 52 | INR | 52 | ENM HOME DISTRIBUTION
WO-11305646 | 104240327 | 2023-09-26 11:20 | 2023-09-25 |  | 2023-09-25 18:21 | MTN684064 | MTN684064 | MTN684064 |  | Compalin FOR MR VIVEK NARAYAN | 2023-09-25 | 2023-09-27 14:58 | No | Warranty | PRABHAT SINGH | ARUN CHAMBER P-38 INDIA EXCHANGE PLACE 2ND FLOOR | KOLKATA | 700001 | West Bengal | India FS ED&I CSP East Team SREYAM SERVICES BHATPARA | AMIT BHATTACHARYA_SREYAM SERVICES BHATPARA | Sreyam Services(8513) | AFTER SITE VISIT FOUND KNX POWER SUPPLY CHECK AND COLLECTED NEW MATERIAL DIRECT ORDER BY CUSTOMER SITE. | Repair |  | 8- Service Completed | 2023-09-27 15:03 |  |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-11310142 | 104249525 | 2023-09-26 17:17 | 2023-09-27 |  | 2023-09-26 10:59 | IH101ZWIFI | IH101ZWIFI | IH101ZWIFI |  | FW: Installation | 2023-09-26 | 2023-09-28 05:22 | No | Commercial Action - Sales | Kuber Factory | Bhram Bazaar, Chandausi null | Moradabad | 244412 | Uttar Pradesh | India FS ED&I CSP North Team Seamtek International Pvt. Ltd. GHAZIABAD | Satish Raika Seamtek International Pvt. Ltd. GHAZIABAD | Seamtek International Pvt. Ltd. | Following wiser component has been installed: Gateway : 1 4 channel relay : 1 | Commissioning & Installation | Start-up | 8- Service Completed | 2023-09-28 14:24 |  |  | 185 | INR | 185 | ENM HOME DISTRIBUTION
WO-11079614 | 103027643 | 2023-08-05 15:37 | 2023-08-25 |  | 2023-08-05 09:32 | UC15/6UXGL | UC15/6UXGL | UC15/6UXGL |  | ULTI SWITCHES COMPLAINT?-SITE INSPECTION REQUIRED Electric Point--22/2/2022 This is with reference to the above subject matter we wish to inform you that we have supplied Ulti switches to our customer. We have received a complaint stating that the switches are not functioning properly and also some of the plates got faded. We sincerely request you to depute your Engineer or sales manager to inspect the site along with our Person Mr.Krishna mohan as our end customer is very much annoyed and raising complaints on the product. Looking forward to hear from you and a speedy action is required to satisfy the customer. -- Thanks and Regards For Electric Point Radhakrishna 9849080770 | 2023-08-05 | 2023-09-14 11:53 | No | Warranty | Radhakrishna Radhakrishna | Road No:12 , Banjara hills null | Hyderabad | 500033 | Telangana | India FS ED&I CSP South Team Master Electrical Solutions Hyderabad | DEBANGSHU BOSE Master Electrical Solutions SECUNDERABAD | Master Electrical Solutions | VISITED THE SITE AND CARRIED OUT THE FOLLOWING JOBS .NEW MATERIAL REPLACED AND OLD DEFECTIVE MATERIAL TAKEN BACK FROM THE CUSTOMER . | Assessment/ Inspection | Data Collection | 8- Service Completed | 2023-09-14 11:58 | Hi team, Below reference is not defined in sales ORG IN 01 U201SPM-DP-B00-S ? Not defined in sales ORG IN01 UC21DP/P>XGL-OS ? Temporarily blocked Rest Below booked zfre UC24SW/P>XGL-OS UC22SW/P>XGL-OS UC15/6UXGL UC15/616XGL Zvo : 226040138 |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-11125540 | 103261715 | 2023-08-17 13:05 | 2023-08-16 |  | 2023-08-16 11:21 | 5500PACA | 5500PACA | 5500PACA |  | Fwd: Complaint C Bus Controller Krishna Electricals---25 Feb 2022 I have a automation controler which is not working Name prakhar gupta Mobile no 7860922222 Adress Swaroop nagar kanpur 208002 | 2023-08-16 | 2023-09-18 15:24 | No | Warranty | Prakhar Gupta | Swaroop nagar | Kanpur | 208002 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Abhishek Patel Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found Cbus having internal issue so we replaced. | Repair |  | 8- Service Completed | 2023-09-18 15:27 |  |  | 115 | INR | 115 | ENM HOME DISTRIBUTION
WO-11135639 | 103368720 | 2023-08-18 15:10 | 2023-08-18 | Required products- (1) US15/616000- 02Nos, (2) UC15/616XGL- 01Nos. | 2023-08-18 14:36 | US15/616000 | US15/616000 | US15/616000 |  | Switch not working properly We have supplied US15/616000- 3nos to M/S Techspertise Solutions. In said material switch is not working properly. GP Electropneumatics--7 June 2023 We are requesting you to depute your service engineer on following site address. Our sale bill attached herewith for your ready reference. Site address- : Maheshwari House, Plot no. 20, Lane no-1 Koregaon park, Pune-411001. Contact person on site- Mr. Aditya, Phone no-8668502850 | 2023-08-18 | 2023-09-05 12:48 | No | Warranty | Mr. Aditya | Maheshwari House, Plot no. 20, Lane no-1 Koregaon park | Pune | 411001 | Maharashtra | India FS ED&I CSP West Team Alliance Controls Pvt Ltd Pune | Shmabhu Bone_Alliance Controls Pvt. Ltd | Alliance Controls Pvt. Ltd. (7966) | We visited at site and checked as per below following points. (1) We checked US15/616000 250V 1 gang 6/16A switched socket ulti Impress. The ultimate switch in 02nos with S/N- X0916 and U1013. (2) As per serial No. product is out of warranty but as per tax invoice given by customer product is in warranty. (3) We have checked ON/OFF operations and observed in 15 to 20 operations found stuck and also checked without cover plate crystal glass UC15/616XGL but problem remains same. Also observed some fine dust. (4) As per discussion with Mr. Datta sir this above products needed to be replaced. (5) We have replaced 01 nos US15/616000 6/16A switched socket from our stock and checked found stuck in operations. Required products- (1) US15/616000- 02Nos, (2) UC15/616XGL- 01Nos. | Repair |  | 9- Service Validated | 2023-09-05 12:48 | =S= Consig Fill up 225983742 |  | 16 | INR | 16 | ENM HOME DISTRIBUTION
WO-10956414 | 102246570 | 2023-07-05 16:19 | 2023-07-05 |  | 2023-07-05 15:57 | U101DFR400XBL1 | U101DFR400XBL1 | U101DFR400XBL1 |  | Ulti Switches Ian 7022567083 Junk House in Benson Town,No2 Benson Road Bangalore | 2023-07-05 | 2023-09-19 12:28 | No | Warranty | Ian Ian | Junk House in Benson Town,No2 Benson Road | Bnagalore | 560046 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Santhosh DP_P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | Inspected and found 1)Ref: US15/6U000 S/N: 2021-40 = 120 No'S 6A 1Gang 2/3 pin switch socket ON/OFF not operating properly. Switch was strucking issue. Some time operated, some time not operating. Hence as per Schneider FSE confirmation we will give the same new switched socket and with cover plate socket CRYSTAL GLASS (UC15/6UX6L) 120 No'S Warranty replacement ASAP | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-19 12:28 |  |  | 16 | INR | 16 | ENM HOME DISTRIBUTION
WO-11103308 | 103194715 | 2023-08-12 11:39 | 2023-08-11 |  | 2023-08-11 13:14 | ATV610D55N4 | ATV610D55N4 | ATV610D55N4 | 4001400JM223502292 | Dear Sir, Please find the enclosed attachment invoice copy Thanks & Regards SOKINDRA KUMAR PURCHASE H.O.D. Plot no 798 Sector 69, IMT, Faridabad- 121001, Haryana, India Cell : +91-7428316306 Email : purchase@accordtpl.com Our GST No- 06AAICA3221G1Z5 Web : www.accordtpl.com (An ISO 9001: 2008 Certified Company) Solution provider for Electrical & Industrial Automation?. From: SK Tomar [mailto:purchase@accordtpl.com] Sent: 10 August 2023 11:15To: 'Customer Care' <customercare.in@schneider-electric.com>; 'ankit.goel@se.com' <ankit.goel@se.com>Cc: 'raj.singh@accordtpl.com' <raj.singh@accordtpl.com>; 'amrik.singh@accordtpl.com' <amrik.singh@accordtpl.com>; 'durgabhai@gmail.com' <durgabhai@gmail.com>; 'durgabhaiburari2@gmail.com' <durgabhaiburari2@gmail.com>; 'ravi.sengar@accordtpl.com' <ravi.sengar@accordtpl.com>; 'durgabhaiburari2@gmail.com' <durgabhaiburari2@gmail.com>Subject: VFD 75 hp warranty replacement Dear Sir We are facing the problem in 75hp drive so please depute the engineer immediately on side When VFD is connect the supply then incomer 160 amp fuse burn & MCCB trip. Drives details are below mention. VFD model no (ATV610D55N4) Serial no-4001400JM223502292. 75HP drives Address are below mention. KBA Agrotech Private Limited. Jagdishpur,Bhagalpur Bihar. Pin code ? 813105 Contact no - 9051513232 Thanks & Regards SOKINDRA KUMAR PURCHASE H.O.D. Plot no 798 Sector 69, IMT, Faridabad- 121001, Haryana, India Cell : +91-7428316306 Email : purchase@accordtpl.com Our GST No- 06AAICA3221G1Z5 Web : www.accordtpl.com (An ISO 9001: 2008 Certified Company) Solution provider for Electrical & Industrial Automation?. | 2023-08-11 | 2023-09-07 15:57 | No | Warranty | KBA Agro tech Pvt Ltd | Jagdishpur null | Bhagalpur | 813105 | Bihar | India FS ED&I CSP East Team Vidya Enterprises Lucknow | Rana Ranjan_Vidya Enterprises Lucknow | Vidya Enterprises | As per customer customer complaint visited the site and check the drive found not working. Perform coal test after supply result is not satisfactory. Open the drive found diode rectifier module are blast. we discuss with internal team need to book the rectifier module. on 2nd visit we replaced the rectifer module from schneder service stock and power on the drive. we perform the coal test and result is ok. but not power on. as discuss the internal team. need to book power card. during 3 rd visit we replaced the power card found drive is power up and working fine as per customer satisfaction. | Repair |  | 9- Service Validated | 2023-09-07 16:09 |  |  | 270 | INR | 270 | Industrial Automation Ops
WO-11115240 | 103255842 | 2023-08-14 17:36 | 2023-08-14 |  | 2023-08-14 16:36 | ATV630D37N4Z | ATV630D37N4Z | ATV630D37N4Z | 5.1545e+17 | RE: WO-11010076 from Schneider Electric, Case: 103252565, [ thread::gCyY8yA8eNmVgsjEM_4CRD4:: ] Site / Company name: Dear AKSHATHA , Drive start tripping again after running some times and showing NLP. Please generate the new work order as we have to visit again at site. ANAND RAI Manager- Field Service Customer Support Schneider Electric M 9654792372/9069699860 Customer Care 18004254272 E anand.rai@se.com C-56, Mayapuri Phase 2 New Delhi India Delhi Jal board Site complete address with Pin Code I) For Sonia Vihar : Delhi jal board, pusta, sonia vihar, 110094 II) For Burari : Delhi jal board, baba colony, Burari, near shamshaan ghat 110036 Name of contact person: DIVYANSHU SINGH Contact Phone / Mob. No: 8285803112 Product Part reference I) For 50 HP : ATV630D37N4Z II) For 30 HP : ATV630D22N4Z Nature of Problem/ Support required The Said VFD'S show these fault in display.( Connection in Progress, DC Bus Overvoltage,Supply Mains Undervoltage) Serial No. of Product i) 515430088221041036 ii) 515430088221045028 iii) 515430088221039017 iv) 515450088220887018 v) 515450088220885040 Invoice Copy (attach please) i) INVOICE NO- AA3320057133 DATE 4-6-22 ii) INVOICE NO- AA3320045975 DATE 5-5-22 | 2023-08-14 | 2023-09-29 10:49 | No | Warranty | Delhi Jal Board | Sonia Vihar Zero Pusta gate no. 2 | Delhi | 110094 | Delhi | India FS ED&I CSP North Team Saffron Automation Delhi | Deepak Pal_Saffron Automation Delhi | Saffron Automation(18001) | Check the drive and and replace the faulty spare and resole the issue, Now drive is working ok. Mail Id. enquiry.macro@gmail.com | Repair |  | 9- Service Validated | 2023-09-01 18:16 | 225975012 |  | 28 | INR | 28 | Industrial Automation Ops
WO-11200548 | 103728442 | 2023-09-02 14:40 | 2023-09-02 |  | 2023-09-02 12:00 | ATV610D37N4 | ATV610D37N4 | ATV610D37N4 | JM215202249 | Attend Customer Complaint Urgently- M/s Delhi Jal Board (ATV610D37N4 SR. NO.-JM215202249) L1 technical comment: ATV610D37N4 NO DISPLAY Kindly attend the complaint at site address on urgent basis:- CAT NO:- ATV610D37N4 SERIAL NO:- JM215202249 NATURE OF FAULT :- NO DISPLAY CUSTOMER NAME:- M/s. Delhi Jal Board : GOVT. of NCT of Delhi ADDRESS:- Office of the Executive Engineer (SDW)-IV, Gate No. 2, Sludge Management Plant, Kondli, Delhi - 110096. (Near Noida Mod) CONTACT PERSON :- Mr. Rajesh Yadav CONTACT NUMBER :- 9871430918 Thanks & Regards, Jayanti Mob: 9250010588 Max Engineering & Automation (P) Ltd Cottage No. - 13A , West Patel Nagar, New Delhi-110008 Ph : 011-43044545 Email :- measales@maxgroup.co.in I www.maxautomation.co.in Works: Plot No. 191-192, EHTP Sector - 56, Phase ? 5, Kundli, Sonepat, Haryana. Pin Code ? 131028. | 2023-09-02 | 2023-09-08 16:25 | No | Warranty | Delhi Jal Board | , Sewage Treatment Plant, Kondli, Delhi | delhi | 110096 | Delhi | India FS ED&I CSP North Team Saffron Automation Delhi | Deepak Pal_Saffron Automation Delhi | Saffron Automation(18001) | Check the drive and found drive | Repair |  | 9- Service Validated | 2023-09-10 16:41 |  |  | 14 | INR | 14 | Industrial Automation Ops
WO-11211349 | 103764833 | 2023-09-07 11:04 | 2023-09-04 |  | 2023-09-04 15:46 | ATS22C11Q | ATS22C11Q | ATS22C11Q |  | 917014926874 Soft Starter Not working Geeta Industries Village Jugalpura Shrimadhav Pur rupendrarajput12360@gmail.com Sikar 332028 | 2023-09-04 | 2023-09-06 18:09 | No | Warranty | Geeta Industries | Khasra NO: OLd(1085/8) Village Jugalpura Shrimadhav Pur null | Sikar | 332028 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Sunny Sharma Sharma Electric Jaipur | Sharma Electric Works | Checked the soft starter found working ok. Email : id not provided by customer. | Repair |  | 9- Service Validated | 2023-09-07 15:29 |  |  | 125 | INR | 125 | Industrial Automation Ops
WO-11222128 | 103824352 | 2023-09-08 09:43 | 2023-09-06 |  | 2023-09-06 17:58 | ATV930C16N4C | ATV930C16N4C | ATV930C16N4C |  | P margin-top:0;margin-bottom:0; SUBJECT:- BINDLAS DUPLUX LTD ;ATV930C16N4C_4031100N2221700087 (ATV930; 160KW/250HP); PROBLEM ::NO DISPLAY/ NOT POWER UP DEAR TEAM, KINDLY ISSUE A COMPLAINT NO. FOR UNDER WARRANTY PRODUCT AT BINDLAS DUPLUX LTD FOR SCHNEIDER VFD ATV930C16N4C_4031100N2221700087 (ATV930; 160KW/250HP); PROBLEM :NO DISPLAY/ NOT POWER UP . PLEASE FIND THE FOLLOWING DETAILS, AND REQUESTED FOR IMMEDIATE ACTION FOR :- ATV930C16N4C. CUSTOMER FACING THE PROBLEM IN VFD ATV930C16N4C_4031100N2221700087 (ATV930; 160KW/250HP); PROBLEM :NO DISPLAY/ NOT POWER UP. PLANT IS UNDER SHUTDOWN AND NEED IMMEDIATE SUPPORT ON SITE. PROBLEM:- NOT POWER UP/ NO DISPLAY IN VFD. SHUTDOWN AVAILABILITY : YES PRODUCT REFERENCE:- ATV930C16N4C_4031100N2221700087 (ATV930; 160KW/250HP) CUSTOMER ADDRESS & CONTACT DETAILS BINDLAS DUPLUX LTD 10.6 KM. BHOPA ROAD,VILL. JATMUJHERA DISTT. MUZAFFARNAGAR U.P. PIN 251308 A K PANDAY +91 97201 71585 YOUR FAST ACTION WILL BE HIGHLY APPRECIABLE, AWAITING REPLY ASAP Thanks for your patience and kind support as always !!!! ??????? ????? ?????, ???? ????? !!! ????? ?? ?? ?????? ? ?? ?? ????????? ?? ?????? ? ???? | 2023-09-06 | 2023-09-14 18:02 | No | Warranty | A K PANDAY | BINDLAS DUPLUX LTD 10.6 KM. BHOPA ROAD,VILL. JATMUJHERA | MUZAFFARNAGAR | 251308 | Uttar Pradesh | India FS ED&I CSP North Team Saffron Automation Delhi | Deepak Pal_Saffron Automation Delhi | Saffron Automation(18001) | Check the drive and found drive static test is not ok input & output are open with PA+ and PC-. Check the complete hardware and found flash on power board. Power up the control card with external 24 V dc found power up found no fault history. Last warning IGBT thermal. Need to be replace power card, IGBT and Thyristor. We replace the faulty spare with new. Now drive is working ok. | Repair |  | 9- Service Validated | 2023-09-15 18:03 |  |  | 1 | INR | 1 | Industrial Automation Ops
WO-11223737 | 103846934 | 2023-09-07 11:21 | 2023-09-07 |  | 2023-09-07 10:44 | ATV320U75N4B | ATV320U75N4B | ATV320U75N4B | HL2248400600 | Issue : screw is not tightening its freely rotated KK Wind Solution ATV320U75N4B- screw is not tightening its freely rotated. Sl#: HL2248400600-As per Manjunath Narayan CX BP - Secure Power & Industrial Automation Customer Satisfaction &Quality confirmation to create the WO for replacement Case 2: ATV320U75N4B- screw is not tightening its freely rotated. Sl#: HL2248400600- refer to attached video and pics. Replacement of product is suggested. @AKSHATHA RANI Product return to Batam plant for preliminary analysis. @Rajat Kumar Singh @RAJESH PATIL Based on the analysis, if issue is related to supplier- supplier PRB need to be raised immediately. If it turns out to be a misuse from the customer- help India CS&Q to drive improvement actions through mission profile. Thanks Manjunath Narayan DGM- Customer Experience Business Partner Secure Power and Industrial Automation International Operations M +91-9972108464 MS TEAMS Manjunath.Narayan@se.com E Manjunath.Narayan@se.com Customer Care 18001030011/18004194194272 Bearys Global Research Triangle 63/3B Gorvigere Village Bidarahalli Hobli Whitefield Ashram road Bengaluru Karnataka 560067 India Type number: ATV320U75N4B Rejected quantity: 01 no SO : 225334436 Issue : screw is not tightening its freely rotated Refer to above details, Please find here in enclosed images & videos. Please depute your service engineer to below mentioned site address to resolve the issue. Contact : Santhosha G : +91 88848 13746 / Mr Lokesh +91 74067 55535 SITE ADRESS : KK Wind Solutions India Private Limited #44, 3rd Main Rd, 3rd Cross Rd, Industrial Suburb 2nd Stage, Yeshwantpur 560022 Bangalore With Regards, Description: Delton New Logo 3 Kokila S ¦ Deltoncontrol & Switchgears LLP ¦ TeleFax :- 080-29743555,26753597,26756527,26756713, 26757190 ¦ Mobile: +91 9620265717 Email: projects@deltoncontrol.com¦ Address: 43-43A,1st main road, New Timberyard Layout, off Mysore road, Bangalore -560026, Landmark-Near Karnataka Bank | 2023-09-07 | 2023-09-12 16:55 | No | Warranty | KK India Wind Solution | 44, 3 cross, 3rd Main, Industrial Suburb, 2nd Stage, Yeshwanthpur | Bangalore | 560022 | Karnataka | India FS ED&I CSP South Team Vamtech Energy Solutions Private Limited Bengaluru | BalaMurugan Venkadaswamy Vamtech Energy Solutions Private Limited Bengaluru | VAMTECH Energy Solutions (P) Limited | being material Delivered Email Id:'santg@kkwindsolutions.com' | Repair |  | 9- Service Validated | 2023-09-12 17:00 |  |  | 32 | INR | 32 | Industrial Automation Ops
WO-11229698 | 103850169 | 2023-09-09 17:16 | 2023-09-08 |  | 2023-09-08 14:43 | ATV310HU22N4E | ATV310HU22N4E | ATV310HU22N4E | 8B2308876296 | Dear CCC, Again we are facing a problem in AC Drive reference No. ATV310HU22N4E Serial No. 8B2308876296 at our site. Please arrange the expert at site & diagnose the problem. Problem Type : Not getting power up Details as Follows: Customer Address : AFI Agro Industries Gobindgarh, Khanna ? 141401 (Alaur, Gobindgarh,) Contact Person : Mr Harjot Singh Contact Number :+91- 94651-79540 We are requesting you to please solve the problem on URGENT basis. Thanks and Regards, Amtinder Singh Internal Internal | 2023-09-08 | 2023-09-09 17:18 | No | Warranty | AFI Agro Industries | AFI Agro Industries , Gobindgarh, Khanna | Ludhiana | 141401 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | checked the vfd found working ok. Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-09 17:20 |  |  | 65 | INR | 65 | Industrial Automation Ops
WO-11234254 | 103908852 | 2023-09-11 16:14 | 2023-09-09 |  | 2023-09-09 11:58 | ATV610D22N4 | ATV610D22N4 | ATV610D22N4 | JM231304463 | Dear Team, We have supplied following drives to customer as per following details : Type: ATV610D22N4- 2 nos Invoice number : 9008651348.Contact details : Mr. Puran Chand Bala JI . Mobile number is 9417169816 ATV610D22N4 40Mr. Puran Chand Bala JI . Mobile number is 9417169816 JM231304463 M/S-Shree Balaji Rice Mill Sullar Gharat Road, Sullar Punjab 148035 sudhir@hsvtechno.com Drives are not operative. Kindly ask service engineer to check the same. With Best Regards Sudhir Sharma ¦sudhir@hsvtechno.com ¦ www.hsvtechno.com¦ HSV Technologies LLP M.+91 9818992435 O.+918076394736 Office Add : 401 Tower C Ithum Sector 62 Noida . (UP). 201309 | 2023-09-09 | 2023-09-11 16:17 | No | Warranty | M/S-Shree Balaji Rice Mill | Sullar Gharat Road, Sullar null | Sangrur | 148035 | Punjab | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Karnail Singh Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the drive found showing STO error due to ribbon wire cut by mouse and also checked other vfd found showing F013 fault due to motor issue. Advised customer to motor and machine. No replacement given in this case. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-11 17:52 |  |  | 2 | INR | 2 | Industrial Automation Ops
WO-11129701 | 103333928 | 2023-08-17 15:42 | 2023-08-17 |  | 2023-08-17 11:14 | MTN6215-5910 | MTN6215-5910 | MTN6215-5910 |  | RE: Issues in Multitouch Pro [ thread::hNDO9e2zfqmTlwFocOqBOj4:: ] MTN6215-5910 Not working Address ? IIIOT INFOTECH PVT LTD, Unit no-317, 3rd Floor, Vipul Trade Center, Sec-48, Sohna Road, Gurgaon, 122018 Contact Person Name ? Nariender Singh Rana Contact No - +91 7807652063 Contact Person Name ? Harshit Sharma Contact No - +91 8218612352 | 2023-08-17 | 2023-09-25 14:38 | No | Warranty | III OT Infotech Pvt Ltd | 317, Vipul Trade Center Sect-48 Sohna Road Gurugram | Gurugram | 122018 | Haryana | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the KNX multi-touch and found display Blank/white after providing the input supply. Customer provide the invoice date-08-11-2022. Which is under warranty. It need yo be replace. We replace the faulty display with new. Mail Id. nariender.singh@iiiot-infotech.com | Repair |  | 8- Service Completed | 2023-09-25 18:04 |  |  | 56 | INR | 56 | ENM HOME DISTRIBUTION
WO-11234285 | 103883096 | 2023-09-09 15:36 | 2023-09-09 |  | 2023-09-09 12:33 | ATS22C11Q | ATS22C11Q | ATS22C11Q | 8B221326515 | Dear Team, Please reissue the case no. Earlier it was cancelled . AEN PHED SAMUDAY BHAWAN PRATAP NAGAR UDAIPUR MR. ANKIT KUMAR 9509439995 Product : ATS22C11Q Serial Number : 8B221326515 NOT GETTING ON ---------- Forwarded message --------- From: Complaints SEW Date: Tue, Sep 5, 2023 at 5:16?PM Subject: Case : 103793336 dt. 5.9.23 To: Complaints SEW , Sharma Electric Cc: Ramkaran Yadav , Mukesh Kumar , Rajan Singh Dear Sir, AEN PHED SAMUDAY BHAWAN PRATAP NAGAR UDAIPUR MR. ANKIT KUMAR 9509439995 Product : ATS22C11Q Serial Number : 8B221326515 NOT GETTING ON -- *WITH REGARDS-* Sarabjit Singh SHARMA ELECTRIC WORKS I CHANDIGARH I ADMIN. AUTH. SERVICE & SPARES DEALER : CROMPTON GREAVES & SCHNEIDER ELECTRIC INDIA* Tele FAX 0172-4629871 E MAIL : complaints@sharmaelectricworks.com * Address : PLOT NO. 279, GF, INDUSTRIAL AREA,* *PHASE-II, CHANDIGARH-160002 , Website : www.sharmaelectricworks.com* *** Please consider the environment before printing this e-mail -- *WITH REGARDS-* Sarabjit Singh SHARMA ELECTRIC WORKS I CHANDIGARH I ADMIN. AUTH. SERVICE & SPARES DEALER : CROMPTON GREAVES & SCHNEIDER ELECTRIC INDIA* Tele FAX 0172-4629871 E MAIL : complaints@sharmaelectricworks.com * Address : PLOT NO. 279, GF, INDUSTRIAL AREA,* *PHASE-II, CHANDIGARH-160002 , Website : www.sharmaelectricworks.com* *** Please consider the environment before printing this e-mail | 2023-09-09 | 2023-09-20 14:57 | No | Warranty | AEN PHED | Saheli Marg, New Fatehpura, Panchwati | Udaipur | 313001 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | Checked the soft stater found not getting on, Hence faulty replaced. ATS22C11Q - 1 nos Email : | Repair |  | 8- Service Completed | 2023-09-21 15:00 |  |  | 395 | INR | 395 | Industrial Automation Ops
WO-11234318 | 103909342 | 2023-09-10 16:54 | 2023-09-09 |  | 2023-09-09 13:28 | BMXCPS3500 | BMXCPS3500 | BMXCPS3500 | 8B223080668 | Dear Sir/Ma'am, We recently purchased a Power Supply model number BMXCPS3500 serial number 8B223080668 from Rexel India Pvt. Ltd. and provided it to Ojasvi Intellimation. Today a customer complained that this Power Supply is not working. You are requested to look into this matter and arrange to solve this issue ASAP. Checklist for Complaint Registration 1 Name of Customer Ojasvee Intellimation 2 Site Address Plot No. -3, Sector Zeta -1 Behind Assotech Society Greater Noida(201308) 3 Name of contact person at site Piyush Pandey 4 Contact Phone / Mob. No: 9627339523 5 Defective product details Power Supply 6 Nature of Defect 7 Shutdown availability if applicable 8 Warranty status YES 9 Commissioned / Installed date 10 Serial No: or DOM of the product 8B223080668 11 Name & phone No: of person registering the complaint Akshu Goel/8745028920 Thanks & Regards Stark Solutions AK Goyal ¦ +91-8745028920 Email Id : Sales.starksolutions@gmail.com Reg. Office & Factory: Plot No. 521/1, Swarn Park, Mundka Indl. Area, New Delhi -110041 Deals In : AC Drive ¦ PLC ¦ HMI/MMI Display ¦ AC Servo System ¦ Power Supply ¦ Encoder ¦ MCC Panel ¦ VFD Panel ¦ APFC Panel ¦ LT Panel ¦ PLC Panels ¦ Fire Panel ¦ ACDB Panel ¦ DCDB Panel ¦ Energy Meter ¦ Conduit Pipe ¦ Cable Glands ¦ Limit Switch ¦ Sensor ¦ Timer & Counter ¦ PID Controller | 2023-09-09 | 2023-09-15 11:04 | No | Warranty | Ojasvee Intellimation | Plot No. -3, Sector Zeta -1 Behind Assotech Society null | Greater Noida | 201308 | Uttar Pradesh | India FS ED&I CSP North Team Saffron Automation Delhi | Yavnish Tyagi Saffron Automation Delhi | Saffron Automation(18001) | Check the power supply and found power supply available at dealer end. Tested the power supply and found not power up after providing the input supply. We replace the faulty power supply with new. | Repair |  | 9- Service Validated | 2023-09-15 18:29 |  |  | 39 | INR | 39 | Industrial Automation Ops
WO-11162860 | 103548383 | 2023-08-28 11:04 | 2023-08-25 |  | 2023-08-25 13:52 | UNS61SW1M_GY | UNS61SW1M_GY | UNS61SW1M_GY |  | URGENT Complaint Please register Customer complaint. Item - uns61sw1m_gy - 15 pcs Shree Krishna Electricals---3 Jan 2023 Please note the site address. Home Address. Kansal Nivas, Near kaka dev thana, kanpur, Uttar Pradesh, Pincode - 208025 Name - Sandeep Kansal Phone number - 9335644440. | 2023-08-25 | 2023-09-02 12:45 | No | Warranty | Sandeep Sandeep | Kansal Nivas Near kaka dev than | Kanpur | 208025 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Abhishek Patel Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found fan regulator having speed variation issue , cover plate having cracked issue so we replaced. | Repair |  | 9- Service Validated | 2023-09-02 12:49 |  |  | 115 | INR | 115 | ENM HOME DISTRIBUTION
WO-11234341 | 103879396 | 2023-09-10 16:57 | 2023-09-09 |  | 2023-09-09 14:13 | HMIET6400 | HMIET6400 | HMIET6400 | HL2305210100168 | Dear Team, Kindly attend the complaint at site address on urgent basis:- CAT NO:- HMIET6400 SERIAL NO:- HL2305210100168 NATURE OF FAULT :- HMI Screen Glow White Continue. CUSTOMER NAME:- M/s. NOIDA FABCON MACHINE PVT LTD ADDRESS:- PLOT NO- 73, SECTOR- ECOTECH-XII, GREATER NOIDA, PIN-201306 CONTACT PERSON :- MR. NEERAJ DUDY CONTACT NUMBER :-8510010722 Thanks & Regards, Jayanti Mob: 9250010588 Max Engineering & Automation (P) Ltd Cottage No. - 13A , West Patel Nagar, New Delhi-110008 Ph : 011-43044545 Email :- measales@maxgroup.co.in I www.maxautomation.co.in Works: Plot No. 191-192, EHTP Sector - 56, Phase ? 5, Kundli, Sonepat, Haryana. Pin Code ? 131028. ***************************************************************** ***************************************************************** | 2023-09-09 | 2023-09-15 11:14 | No | Warranty | Noida Fabcon Machines Pvt. Limited | Plot No.73, Ecotech XII | Noida | 201306 | Uttar Pradesh | India FS ED&I CSP North Team Saffron Automation Delhi | Yavnish Tyagi Saffron Automation Delhi | Saffron Automation(18001) | Check the HMI and found HMI is power up but display goes blank after providing the input supply 24 V Dc. We replace the faulty HMI with new. | Repair |  | 9- Service Validated | 2023-09-15 18:30 |  |  | 34 | INR | 34 | Industrial Automation Ops
WO-11258891 | 104028254 | 2023-09-14 13:18 | 2023-09-14 |  | 2023-09-14 13:13 | ATV320U15N4C | ATV320U15N4C | ATV320U15N4C | HL2305041167 | Dear Customer care, Please help for visit of our service engineer on below site urgently. Product : ATV320U15N4C Ser. No. : HL2305041167 Problem : No display Customer : Bahuchar Engineers, B/56, Shurbhi shopping center, Opp. Triveni Park, Mahadev nagar ? Vastral road, Vastral, Ahmedabad ? 362418, GUJARAT, INDIA. Contact Person : Mr. Nitin Solanki - 9925002119. Thanks & Regards, Nitin Solanki (M) 9925002119 Authorized Channel Partner of Automation And Control Solution, Shed No.25,Sahjanand Business Park, Nr.Keshvam Estate,Nikol-Odhav Ring Road, Kathwada,Ahmedabad-382415, Gujarat, India. E mail - nitin@acsdrives.in Web. - www.acsdrives.in | 2023-09-14 | 2023-09-15 17:05 | No | Warranty | Bahuchar Engineers | B/56, Shurbhi shopping center, Opp. Triveni Park, Mahadev nagar ? Vastral road, Vastral, null | Ahmedabad | 362418 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Mistri Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked t he product found physically observed ok. check the igbt and rectifier observed ok. check the pa+ and pb , pc observed ok. give a 3 supply but display show "nlp" check the voltage in mounting 250v observed. check the runtime 26min ontime 17h, acc = 1.0sec ,dcc = 1.0sec, take a drive from customer for further action. we have change the control card for checking the same. so it may be problem in power board so unde warrnaty status free replacement. | Repair |  | 9- Service Validated | 2023-09-15 17:06 | =S= Consig Fill up 226056332 |  | 10 | INR | 10 | Industrial Automation Ops
WO-11258989 | 104028906 | 2023-09-14 14:38 | 2023-09-14 |  | 2023-09-14 13:59 | ATV310H075N4E | ATV310H075N4E | ATV310H075N4E | 8B2143451057 | Dear Team,Nirmal Kutiya Trust,Sec-13 Karnal Haryana.Mr Surinder Singh9813089557Product : ATV310H075N4ESrn : 8B2143451057Not power Up.-- *WITH REGARDS-*Sarabjit SinghSHARMA ELECTRIC WORKS I CHANDIGARH I ADMIN. AUTH. SERVICE & SPARESDEALER : CROMPTON GREAVES & SCHNEIDER ELECTRIC INDIA*Tele FAX 0172-4629871E MAIL : complaints@sharmaelectricworks.com *Address : PLOT NO. 279, GF, INDUSTRIAL AREA,**PHASE-II, CHANDIGARH-160002 , Website : www.sharmaelectricworks.com**** Please consider the environment before printing this e-mail | 2023-09-14 | 2023-09-15 11:20 | No | Warranty | Nirmal Kutiya trust | ITI Chowk | Karnal | 132024 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the vfd found showing --11 , no line power state. Hence faulty replaced. ATV310H075N4E- 1 nos. EMAIL :complaints@sharmaelectricworks.com | Repair |  | 8- Service Completed | 2023-09-15 12:51 |  |  | 1 | INR | 1 | Industrial Automation Ops
WO-11269342 | 104065941 | 2023-09-16 12:38 | 2023-09-16 | We have observed the Tower light AMBER indication not working. | 2023-09-16 11:13 | XVGM3S | XVGM3S | XVGM3S |  | Dear Team, Greeting of the day. Please find the attached Tower Lamp Images & below complaint form XVGM3S Issue. As per the customer feedback XVGM3S not working. Please take action and solve As soon as possible. Checklist for Complaint Registration 1 Site Name & Complete Address Automation Solutions, Plot no.42, Vijetha Green Homes, Hydernagar, Nizampet-500090 2 Site Contact Name & Mobile Richa Arya- 8885066293 3 Site Contact Email Address** richa@automationsolutions.co.in 4 Defective Product Model/Part No XVGM3S 5 Nature of Defect* Not working 6 Shutdown availability if applicable 7 Distributor Name, Invoice # & Date M/s. Power Electricals 8 Serial No: or DOM of the product 8B-2021-W30-5 9 Name & phone No: of person registering the complaint Richa Arya- 8885066293 Points 1,2,4,5 & (7or8) are mandatory. Point 7 not applicable for Industry Business. * Kindly share defect symptoms instead of "Not working?. ** End user will receive a survey asking feedback on service Thanks & Regards, Murali Gundeboina Engineer ? Sales Mob : +91 8956581838 Rexel India Pvt. Ltd. B-9/1,Office no.1, Phase ?II, Technocart Estate, Khajaguda, Balanagar, Hyderabad ? 500037 www.rexel.co.in | 2023-09-16 | 2023-09-19 18:38 | No | Warranty | Automation Solutions | Plot no.42, Vijetha Green Homes, Hydernagar null | Hyderabad | 500090 | Telangana | India FS ED&I CSP South Team ENERPRO ENGINEERING SOLUTIONS Vijayawada | Makineni Jayashankar ENERPRO ENGINEERING SOLUTIONS VIJAYAWADA | Enerpro Engineering Solutions - 500012682 | TOWER LIGHT NOT WORKING | Repair |  | 9- Service Validated | 2023-09-19 18:40 |  |  | 245 | INR | 245 | Industrial Automation Ops
WO-11269595 | 104076970 | 2023-09-18 10:25 | 2023-09-16 |  | 2023-09-16 18:23 | ATV930C13N4C | ATV930C13N4C | ATV930C13N4C | 4031000N2214800374 | Dear Sir, Please find the complaint registration form attached. Name of Customer DIYA PACKAGING PVT.LTD. Site Address " PLOT NO- 201, NEAR BHAYLA WATER TANK,BHAYLA-SAKODRA ROAD, VILLA.-BHAYLA,AHMEDABAD -382210 " Name of contact person at site MR. RAKESH SHAH Contact Phone / Mob. No: 9099912869 Defective product details ATV930C13N4C Nature of Defect Not working Display Shutdown availability if applicable Warranty status under warranty Commissioned / Installed date Serial No: or DOM of the product 4031000N2214800374 Name & phone No: of person registering the complaint MINI;9744227600 @ranRani S We purchased a ATV930C13N4C . But the item display is not working so Kindly do the needful immediately for service . Kindly do the needful at the earliest. Regards, Mini shibin ¦ Cadillac Automation & Controls Mobile: 9744227600 Email: projects@cadillacautomation.com Website: www.cadillacautomation.com Address: 37/1062 A,Ground Floor, Metro pillar No:317, Opposite Najath School, South Kalamassery, Ernakulam, Kerala-682033 | 2023-09-16 | 2023-09-21 16:14 | No | Warranty | DIYA PACKAGING PVT. LTD. | Plot No.- 201, Near Bhayla Water Tank | AHMEDABAD | 382210 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Nijesh Patel_Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physically obsrved ok. due to customer repair the drive outside due to misplat shutdown. so no consider in warranty. check the runtime 1656.5 no of state 247 drive damage due to the voltage strike. recommended the customer please install input side the semi conductor fuse for the in future. | Repair |  | 8- Service Completed | 2023-09-21 16:15 |  |  | 60 | INR | 60 | Industrial Automation Ops
WO-11277128 | 104087578 | 2023-09-20 11:21 | 2023-09-18 |  | 2023-09-18 14:43 | ATV610D37N4 | ATV610D37N4 | ATV610D37N4 |  | Hello All,Pls. Refer Below Customer Mail & Resolve On Priority. Regards, Pramod Name of Customer Unique Control Pvt. Ltd. Site Address VRV HOSPITALITY PVT LTD TEHSIL CHAK-ALIA, VILLAGE DINANAGAR, DIST. GURDASPUR, PUNJAB GURDASPUR-143521 PUNJAB. Name of contact person at site Mr. Joji Biju Contact Phone / Mob. No: Cell 9446668993 Defective product details : ATV610D37N4 ATV610, VSD IP20 37kW, 380/415V Product Make Schneider Nature of Defect Display Problem Shutdown availability if applicable Yes Warranty status Yes Commissioned / Installed date No Serial No: or DOM of the product/OA no./Invoice Details S/N 4001200JM223000209 Invoice No. 2204017 dt 24/12/2022 attached invoice Name & phone No: of person registering the complaint Jayram Patil - Mb.9130035982 | 2023-09-18 | 2023-09-21 15:53 | No | Warranty | Unique Control Pvt. Ltd | VRV HOSPITALITY PVT LTD TEHSIL CHAK-ALIA, VILLAGE DINANAGAR null | GURDASPUR | 143521 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the vfd found display issue, keyboard error due to HMI faulty and control block faulty. Hence faulty replaced. VX4B610100 - 1 Nos. VW3A1113 - 1 nos. email : id not provided by the customer. | Repair |  | 8- Service Completed | 2023-09-21 16:23 |  |  | 2 | INR | 2 | Industrial Automation Ops
WO-11280972 | 104124143 | 2023-09-19 18:29 | 2023-09-19 |  | 2023-09-19 16:43 | PFXSP5500WAD | PFXSP5500WAD | PFXSP5500WAD | 132496JA00626 | Dear sir/ madam, Please find the attached HMI complaint registration form. Defective product details PFXSP5500WAD Serial No: or DOM of the product 132496JA00557 Nature of Defect TOUCH NOT WORK Name of Customer Powertronics Control System Pvt Ltd. Site Address D-1, Shayona Estate, Memco Cross Road, Naroda Road, Ahmedabad ? 380025. Gujarat, India. Name of contact person at site DEVESH PATEL Contact Phone / Mob. No: 8511993544 Defective product details PFXSP5500WAD Nature of Defect TOUCH NOT WORK Shutdown availability if applicable Sunday Warranty status Warranty period Commissioned / Installed date 24-Jan-23 Serial No: or DOM of the product 132496JA00557 Name & phone No: of person registering the complaint DEVESH PATEL MO :- 8511993544 service@powertronics.in Thanks & Best Regards, Devesh Patel Service Engineer ? Service Department D-1, Shayona Estate, Memco Cross Road, Naroda Road, Ahmedabad ? 380025, Gujarat, INDIA. O: 079-22200773-74 ¦ M : 085119 93544 Web: www.powertronics.in ¦ E-Mail: service@powertronics.in Branch: Rajkot I Surat I Mumbai I Jaipur I Chandigarh I Pune | 2023-09-19 | 2023-09-22 13:00 | No | Warranty | POWERTRONICS CONTROL SYSTEM P LTD.(500050226) | D1, Shayona Estate Memco char rasta Naroda | Ahmedabad | 380025 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Mistri Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physically obsrved ok power up the hmi and touch working ok. as per customer sometime heat touch not working. so we check the touch calibration and touch panel working ok 4 to 5 times. as per customer product obesrvation under 2 days. | Repair |  | 9- Service Validated | 2023-09-22 13:00 | =S= Consig Fill up 226075024 |  | 10 | INR | 10 | Industrial Automation Ops
WO-11285738 | 104143991 | 2023-09-20 16:38 | 2023-09-20 |  | 2023-09-20 15:43 | TM200CE24T | TM200CE24T | TM200CE24T | WXNHA51441222270063 | Dear Team,Please reissue the case no. Earlier it was cancelled .---------- Forwarded message ---------From: Complaints SEW Date: Fri, Sep 15, 2023 at 12:22?PMSubject: Case : 104056079 dt. 15.9.23To: Complaints SEW , SharmaElectric Cc: Ramkaran Yadav , Mukesh Kumar, Rajan SinghDear Sir,TNG Bharti airtelGround floor,Raj Rajeshwar Colony BanswaraMr. Lekhraj9950540989Product : TM200CE24TSerial Number : WXNHA51441222270063 Not Working--*WITH REGARDS-*Sarabjit SinghSHARMA ELECTRIC WORKS I CHANDIGARH I ADMIN. AUTH. SERVICE & SPARESDEALER : CROMPTON GREAVES & SCHNEIDER ELECTRIC INDIA*Tele FAX 0172-4629871E MAIL : complaints@sharmaelectricworks.com *Address : PLOT NO. 279, GF, INDUSTRIAL AREA,**PHASE-II, CHANDIGARH-160002 , Website : www.sharmaelectricworks.com**** Please consider the environment before printing this e-mail-- *WITH REGARDS-*Sarabjit SinghSHARMA ELECTRIC WORKS I CHANDIGARH I ADMIN. AUTH. SERVICE & SPARESDEALER : CROMPTON GREAVES & SCHNEIDER ELECTRIC INDIA*Tele FAX 0172-4629871E MAIL : complaints@sharmaelectricworks.com *Address : PLOT NO. 279, GF, INDUSTRIAL AREA,**PHASE-II, CHANDIGARH-160002 , Website : www.sharmaelectricworks.com**** Please consider the environment before printing this e-mail | 2023-09-20 | 2023-09-20 16:41 | No | Warranty | TNG Bharti airtel | Grnd floor,Raj Rajeshwar Colony | Banswara | 327001 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | Checked the HMI found working ok. Email : id not provided by customer . | Repair |  | 8- Service Completed | 2023-09-20 16:44 |  |  | 510 | INR | 510 | Industrial Automation Ops
WO-11290811 | 104178343 | 2023-09-21 17:51 | 2023-09-21 | LIMIT SWITCH NOT OPERATING | 2023-09-21 17:29 | ZCKJ404 | ZCKJ404 | ZCKJ404 |  | Dear CCC, Pl issue complaint no. 1. Name of Customer: GHATGE PATIL INDUSTRIES LTD KAGAL ? UNIT --II 2. Site Address: - Brisk electronics pvt Ltd KOLHAPUR-416012 3. Name of contact person at site :- Maruti Desai. 4. Contact Phone / Mob. No: - 7888043203 5. Defective product details: ZCK-J404- LIMIT SWITCH 6. Product Make:-Schneider Electric 7. Nature of Defect?OPEN LIMIT SWITCH WITHOUT SPARES 8. Shutdown availability if applicable nil 9. Serial No: or DOM : nil 10. Dealer Name /OA no. /Invoice Details: -78 ? DATED 13-4-23 11. Commissioned / Installed date:- NIL 12. Name & phone No: of person registering the complaint: MARUTI DESAI 788043203 | 2023-09-21 | 2023-09-25 17:23 | No | Warranty | Brisk Electronics Pvt Ltd | D-23,KOLHAPUR UDYAM CO-OP SOCIETY LTD. , 1328/34, Y.P.POWARNAGR. | KOLHAPUR | 416008 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Samadhan S_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the Limit Switch found that the it's not operating properly. changeover of NO - NC Contact & in normal condition NO-NC Contact working found ok. no problem observed in Limit Switch. It's working found ok. | Repair |  | 9- Service Validated | 2023-09-25 17:35 |  |  | 280 | INR | 280 | Industrial Automation Ops
WO-11140664 | 103390995 | 2023-08-21 13:48 | 2023-08-19 |  | 2023-08-19 17:06 | MTN6710-0102 | MTN6710-0102 | MTN6710-0102 |  | Complaint for KNX DIMMER AND EXT. (DR.TANVIR KAUR SIDHU) Name :- DR.TANVIR KAUR SIDHU Address :- H.NO 19809, STREET NO 20, AJIT ROAD, BATHINDA-151001 Contact number :- 8146962367 (Customer) Contact number :- 85688 02030 ( Engineer) Complaint :- 1 ) MTN6710-0102 Qty 1 pcs 2) MTN6810-0102 Qty 2 pcs Problem :- This item is not working properly. Kindly attend the complaint on priority basis. Attached Pur and Sale invoice | 2023-08-19 | 2023-09-30 15:10 | No | Warranty | TANVIR KAUR SIDHU | H.NO 19809, STREET NO 20, AJIT ROAD, | Bhatinda | 151001 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the MTN found module malfunctioning issue and not working properly. Hence faulty replaced. Material replaced by dealer. MTN6710-0102 - 1 Nos. MTN6810-0102 - 2 Nos. email : id not provided by the customer. | Repair |  | 8- Service Completed | 2023-09-30 15:29 |  |  | 150 | INR | 150 | ENM HOME DISTRIBUTION
WO-11171812 | 103571638 | 2023-08-29 16:25 | 2023-08-28 |  | 2023-08-28 10:29 | UNSMTSTART2M_WE | UNSMTSTART2M_WE | UNSMTSTART2M_WE |  | In 16oct 2022 i have buy USB unica white Schneider. when we charge a device it f USB socket unica white--1 no Invoice : Bansal Electronics--16 oct 2022 Not operating properly Site : VPO Amlela Khas, Tehsil Jawali, Nagrota Surian, Dis Kangra 176027 Mr.Rakshit Kumar : 9805550706 rakshitkumar612@gmail.com | 2023-08-28 | 2023-09-02 12:53 | No | Warranty | Rakshit Kumar | VPO Amlela Khas, Tehsil Jawali, Nagrota Surian | Kangra | 176027 | Himachal Pradesh | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Rakesh Kumar Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the starter switch and fan regulator found not giving output. Hence faulty replaced. UNSMTSTART2M_WE- 1 nos. UNS4STFAN1M_WE- 1 nos. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-02 12:59 |  |  | 225 | INR | 225 | ENM HOME DISTRIBUTION
WO-11154363 | 103476370 | 2023-08-24 13:10 | 2023-08-23 |  | 2023-08-23 14:39 | IH14000100 | IH14000100 | IH14000100 |  | UBER PROJECT LIGHTING PRIVATE LIMITED-1.pdf Please arrange service engineer for service issue at Sukhi Ubantu project. Material given through Uber projects. 4channep relays 2 no not working Contact number: +918309150236 Contact name : Amit. Site Location: Puppalguda , Manikonda, Hyd 500089. | 2023-08-23 | 2023-09-12 09:52 | No | Warranty | Amit Amit | Sy no. 447/p, Puppalguda, | Ranga Reddy | 500075 | Telangana | India FS ED&I CSP South Team Master Electrical Solutions Hyderabad | VEERESH KUMAR Master Electrical Solutions SECUNDERABAD | Master Electrical Solutions | visited the site and replaced the defective relay with new one | Repair |  | 9- Service Validated | 2023-09-12 09:55 |  |  | 28 | INR | 28 | ENM HOME DISTRIBUTION
WO-11161695 | 103543110 | 2023-08-25 10:17 | 2023-08-25 |  | 2023-08-25 08:26 | UNS5STFAN2M_GY | UNS5STFAN2M_GY | UNS5STFAN2M_GY |  | UNICAPURE BLACK GLASS, FAN REGLATOR COMPLAIN Name of Customer MR.HARSH SHAH 2 Site Address NAVSARI 104,CHINTAMANI PARASHWANATH APP,BEHIND TIGHRA WADI,NAVSARI NAVSARI - GUJARAT 396445 3 Name of contact person at site MR. HARSH SHAH 4 Contact Phone / Mob. No: 8469527665 5 Defective product details UNS5STAFAN2M_GY, UNPSP4M_GB, UNPSP6M_GB, UNPSP12M_GB. FAN REGULATOR SPEED CONTROL ISSUE , GLASS COME OUT IN BLACK COLOUR PLATE, AND SILVER LINE REMOVE IN BLACK GLASS. 6 Nature of Defect NOT WORKING 7 Shutdown availability if applicable No 8 Warranty status yes 9 Commissioned / Installed date 10 Serial No: or DOM of the product 11 Name & phone No: of person registering the complaint 8469527665 | 2023-08-25 | 2023-08-26 10:27 | No | Warranty | HARSH SHAH | 104,CHINTAMANI PARASHWANATH APP,BEHIND TIGHRA WADI | NAVSARI | 396445 | Gujarat | India FS ED&I CSP West Team SHIV SAI ELECTRICALS Vapi | SHIVAM LAD SHIV SAI ELECTRICALS VAPI | shivsai electricals | AS PER SITE VISIT WE CHECK THE PRODUCT AND FOUND OK ON VISUAL INSPECTION.AFTER THAT CHECK THE COVER PLATE AND FOUND THE COVER PLATE IS COLOUR ISSUE.WHEN WE CHECK THE PRODUCT WARRNTY STATUS AND FOUND THE PRODUCT IS UNDER WARRNTY NEEDS TO BE REPLACED. | Repair |  | 9- Service Validated | 2023-09-26 10:30 | =S= Consig Fill up 226019148 |  | 131 | INR | 131 | ENM HOME DISTRIBUTION
WO-11167249 | 103570085 | 2023-08-27 15:50 | 2023-08-31 | We have visited the site for the Door bell installation. Wifi is not avilable in the site. we have requsted the customer for the wifi and site requirments for the doorbell installation. the customer requested the 10-15days time period. after that customer will log a case for the installation support. | 2023-08-26 13:05 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Re: Smart door bell Installation [ thread::Oc94oMl_ek6-lJsjQ_jwiz4:: ] Installation KVN.Radhika NGOs colony,Narasaraopet-522601 opp Govt hospital KVN Radhika 9440800377 Installation 1 | 2023-08-26 | 2023-08-31 11:51 | No | Commercial Action - Sales | KVN Radhika | NGOs colony, opp Govt hospital | Narasaraopeta | 522601 | Andhra Pradesh | India FS ED&I CSP South Team ENERPRO ENGINEERING SOLUTIONS Vijayawada | SK SIRAJUDDIN_ENERPRO ENGINEERING SOLUTIONS VIJAYAWADA | Enerpro Engineering Solutions - 500012682 | DOORBELL INSTALLATION REQUIRMENT | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-01 12:08 |  |  | 67 | INR | 67 | ENM HOME DISTRIBUTION
WO-11167282 | 103569793 | 2023-08-26 14:15 | 2023-08-26 | NA | 2023-08-26 13:58 | A9N16201 | A9N16201 | A9N16201 |  | Dear Team, Good Morning!! Request you to register complaint and arrange service engineer Name of Customer Shandiliya Villa Site Address " Floor 21&22 10A, khan Abdul Ghaffar khan road Worli sea face , Worli , Mumbai - 400030 Name of contact person at site Ms. Shilpa Contact Phone / Mob. No: 9773701522 Cont Person E mail Id project@ves.co.in Defective product details "A9N16201 A9N16254 A9N16204 A9N16208 Nature of Defect RCBO--Not tripping on Fault Shutdown availability if applicable NA Warranty status YES Commissioned / Installed date Invoice No: / Date "9008583717/Dt: 31.05.2023 9008296811/Dt: 21.10.2022 9008492102/Dt: 23.03.2023 Thanks & Regards, | 2023-08-26 | 2023-08-29 15:58 | No | Warranty | Shilpa Kumari | Floor 21&22 10A, khan Abdul Ghaffar khan road, Worli sea face , Worli | Mumbai | 400030 | Maharashtra | India FS ED&I CSP West Team East India Power Engineers Mumbai | Ratnesh Shigvan East India Power engineers Mumbai | East India Power Engineers (5043) | Visited the site & checked the RCCB by giving input supply and push test trip found that RCCB working okay. Also, RCCB visually checked and found no abnormalities. As per customer feedback, they observed in their testing activity of RCCB not ripping as required and current. There is a need for Schneider standard testing with a kit for the RCCB test. | Repair |  | 8- Service Completed | 2023-09-05 14:18 |  |  | 16 | INR | 16 | ENM HOME DISTRIBUTION
WO-11167337 | 103570243 | 2023-08-28 11:14 | 2023-08-26 |  | 2023-08-26 15:18 | UNS4STFAN1M_WE | UNS4STFAN1M_WE | UNS4STFAN1M_WE |  | Conplain Clint name vinod,9639005332 Uns4stfan1m_we-2pcs 122 shiv garden colony shiv mandir kr samne panki ki tanki dohra road Bareilly 243001 Not working | 2023-08-26 | 2023-09-01 17:07 | No | Warranty | Vinod Vinod | 122 shiv garden colony shiv mandir kr samne panki ki tanki dohra road | Bareilly | 243001 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Abhishek Patel Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found fan regulator having speed variation issue so we replaced. | Repair |  | 9- Service Validated | 2023-09-01 17:10 |  |  | 260 | INR | 260 | ENM HOME DISTRIBUTION
WO-11167445 | 103571786 | 2023-08-28 12:55 | 2023-08-26 |  | 2023-08-26 18:12 | A9KR11463 | A9KR11463 | A9KR11463 |  | DEAR SIR , I HAVE PURCHASED SCHNEIDER RCCB 63AMP 4P 30 MA FROM ONE OF YOUR DEALER FROM LUCKNOW . THE RCCB IS NOT TRIPPING . DETAILS OF THE PROUDUCT: PRODUCT NAME : SCHNEIDER RCCB 63AMP 4P 30MA (IDK 63A) PROBLEM : NOT TRIPPING QTY: 01 NOS Model NO. A9KR11463 PLEASE RESPONSE BACK AND SOLVE THE PROBLEM AS SOON AS POSSIBLE. CONTACT DETAILS; NAME: J.P. GUPTA CONTACT: 9415070664, 8574062219 SHOP NAME : AGRAHARI ENTERPRISES ADDRESS : NEAR NTPC MAIN GATE , BAHERWA UNCHAHAR , DISTRICT: RAEBARELI , U.P. | 2023-08-26 | 2023-09-01 18:01 | No | Warranty | Agrahari Enterprises | NTPC Gate # 3 Unchahar Aliganj Dehat | Raebareli | 229406 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Aman Khare_Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found rccb having pole open issue so we replaced. | Repair |  | 9- Service Validated | 2023-09-01 18:05 |  |  | 120 | INR | 120 | ENM HOME DISTRIBUTION
WO-11167451 | 103571836 | 2023-08-28 19:28 | 2023-08-28 | Validated By Prashant | 2023-08-26 18:29 | IN8486/32(BZ) | IN8486/32(BZ) | IN8486/32(BZ) |  | Re: COMPLAINT [ thread::zUKym_L3cdyvH41IzclfPz4:: ] IN8486/32(BZ) - 1 NOS. NOT WORKING Dear All, M/s. Shree Krishna Electricals 158, Kanji Gokuldas Building, Lohar Chawl, Mumbai :- 400 002 Tel # 9820736737 | 2023-08-26 | 2023-09-06 18:30 | No | Warranty | Shree Krishna Electricals | 158, Kanji Gokuldas Building, Lohar Chawl, | Mumbai | 400002 | Maharashtra | India FS ED&I CSP West Team S K SERVICES Mumbai | Hemant Patel S K SERVICES Mumbai | S.K. Services (10237) | We Visited Site 32A DP Switch is Properly Not Operating So Stuck issue We Raise The ZVO Next Visit | Repair |  | 9- Service Validated | 2023-09-06 20:12 | =S= Consig Fill up 226005722 |  | 28 | INR | 28 | ENM HOME DISTRIBUTION
WO-11172819 | 103589306 | 2023-08-28 16:13 | 2023-08-28 | NA | 2023-08-28 13:13 | E8315_6_WG | E8315_6_WG | E8315_6_WG |  | COMPLAINT E8315_6_WG_G8 - 2 NOS. NOT WORKING Dear All, House no 745, Thelma villa, Opposite Tilari colony, Tilari colony road, Sawantwadi, 416510 Maharashtra Contact No 9920696487 & 9421149044 -- Regards Dhaval Jariwala / Nirav Jariwala Handheld:- 9987767377 / 9867363285 | 2023-08-28 | 2023-08-29 15:31 | No | Warranty | Gabriel Gabriel | House no 745, Thelma villa, Opposite Tilari colony, Tilari colony road, Sawantwadi | Sindhudurg | 416510 | Maharashtra | India FS ED&I CSP West Team East India Power Engineers Mumbai | Abhishek Parab_East India Power engineers Mumbai | East India Power Engineers (5043) | Visited the site & checked the 5-step electronic fan regulator and found that not function properly. hence the regulator needs to be replace with a new one. | Repair |  | 8- Service Completed | 2023-09-03 11:18 | =S= Consig Fill up 226010062 |  | 45 | INR | 45 | ENM HOME DISTRIBUTION
WO-11178291 | 103618664 | 2023-08-29 15:01 | 2023-08-29 |  | 2023-08-29 11:43 | UNSMTSTART2M_GY | UNSMTSTART2M_GY | UNSMTSTART2M_GY |  | Multiple Defected Switches, sockets, MCB,Starter, Isolaters Model number: Issue : Not working Inovice Date: 13 My 2023 Contact person and number: Manish Johari UNSMTSTART2M_G4 SWITCH " UNS32DP2M_G4 Address: 39, Jaydevi Nagar, Garh road, near vishal mega mart, Meruth UP 250002 | 2023-08-29 | 2023-09-06 14:32 | No | Warranty | Manish Johari | 39, Jaydevi Nagar, Garh road, near vishal mega mart | Meerut | 250002 | Uttar Pradesh | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the switches and sockets and found switches have stuck issue and sockets have output issue. Check the MCB and Isolater and found phase missing issue and output issue, We replace the faulty switches and sockets and MCB or Isolater with new. | Repair |  | 9- Service Validated | 2023-09-07 08:08 |  |  | 83 | INR | 83 | ENM HOME DISTRIBUTION
WO-11178343 | 103619271 | 2023-08-29 14:58 | 2023-08-29 |  | 2023-08-29 11:58 | IN8486_20_BZ | IN8486_20_BZ | IN8486_20_BZ |  | Zencelo swetches Defect Model Number: IN8486/32 8 switches Not working Zencelo 32 apr Invoice Date: 6 oct 2022 Vijay Kumar 9650514974 TOWEN HOME, Narmada Gate, 8/6 JP Greens Grater Noida UP 201303 | 2023-08-29 | 2023-09-05 17:58 | No | Warranty | Vijay Kumar | TOWEN HOME, Narmada Gate, 8/6 JP Greens Grater Noida | Noida | 201303 | Uttar Pradesh | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the switches and found switches have stuck issue, We replace the faulty switches with new. | Repair |  | 9- Service Validated | 2023-09-05 17:59 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11178526 | 103621603 | 2023-09-01 10:56 | 2023-08-29 |  | 2023-08-29 12:58 | A9N1P06C | A9N1P06C | A9N1P06C |  | Defected MCB6mpr single pole, Router Switch July 2023 Model no: A9n1p06c Contact Person: Keshav Issue :Not working Address: Plot no 542 DLF Industrial area phase I faridabad Haryan 121003 | 2023-08-29 | 2023-08-31 18:01 | No | Warranty | Keshav Keshav | House number 1067 urban estate phase 2 jamalpur coloney | Ludhiana | 141010 | Punjab | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mcb found dolly free after repairing now mcb found working ok. Resolved by repair. Email : id not provided by customer . | Repair |  | 9- Service Validated | 2023-09-01 11:11 |  |  | 45 | INR | 45 | ENM HOME DISTRIBUTION
WO-11178912 | 103627092 | 2023-08-29 18:05 | 2023-08-29 |  | 2023-08-29 15:28 | X1001WH_N | X1001WH_N | X1001WH_N |  | Switch Not working FMD OFFICE SOBHA CITY DWARKA EXPRESSWAY GURUGRAM HARYANA 1220171 switch not workingManoj kumar 9810210704Invoice date 22-02-2022 | 2023-08-29 | 2023-09-02 16:47 | No | Warranty | Manoj Kumar | FMD OFFICE SOBHA CITY DWARKA EXPRESSWAY GURUGRAM null | Gurgaon | 122017 | Haryana | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the switches and found switches have breaking issue and stuck issue, We replace the faulty switches with new. Mail ID. fm.scg@sobha.com | Repair |  | 9- Service Validated | 2023-09-02 16:54 |  |  | 1 | INR | 1 | ENM HOME DISTRIBUTION
WO-11178950 | 103628026 | 2023-09-01 11:35 | 2023-08-29 |  | 2023-08-29 15:46 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Wiser complaint Name: Rajat Rustagi Address : 25/3-B Aravali View Rail Vihar, Sector 56 City: Gurgaon , State: Haryana Pin: 122011 , INDIA Contact Number: 9731474488 Product : IH100WFVDP Invoice dt. : MARCH 2023 | 2023-08-29 | 2023-08-30 04:09 | No | Commercial Action - Sales | Rajat Rustagi | 25/3-B Aravali View Rail Vihar, Sector 56 City | Gurgaon | 122011 | Haryana | India FS ED&I CSP North Team Seamtek International Pvt. Ltd. GHAZIABAD | Satish Raika Seamtek International Pvt. Ltd. GHAZIABAD | Seamtek International Pvt. Ltd. | following wiser components has benn reparired smart door bell : 1 no | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-07 16:10 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11181308 | 103634783 | 2023-08-31 09:48 | 2023-08-30 |  | 2023-08-30 09:43 | P3200_N | P3200_N | P3200_N |  | Respected Sir / Madam, We would like to inform you that we have supplied your Material at Site & there is complaint regarding it. Sharing the details for the same Site Address : A/703, Chintamani flora, Beside Ajay Continental Street, Beside Pulkit School Fatehpura Ahmedabad -380007 Contact Person : Mr. Manish K Desai Mobile No : 9428104755 Material Issue : 2M Step Regulator & 12M Plate Model no: P3200_N Attaching Images of Product & Invoice's copy of Schneider Purchase Requesting you to arrange the Service Engineer & resolve the issue at the earliest. Regards JAINAM SHAH Parag Electric Co. | 2023-08-30 | 2023-09-01 14:28 | No | Warranty | Manish Desai | A/703, Chintamani flora, Beside Ajay Continental Street, Beside Pulkit School Fatehpura | Ahmedabad | 380007 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Mistri Anik Engineering Ahmedabad | Anik Engineering (554) | Visited t he site and checked the product found physically observed ok. P3200 SR NO : 18415 obseved ok but 3 step less than 2 step speed. so give free replacement. P0712 SR NO : 21153 observed ok but lightly click observed ok cover so free replacement. | Repair |  | 9- Service Validated | 2023-09-01 14:28 | =S= Consig Fill up 226011919 |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11183095 | 103651490 | 2023-08-31 12:44 | 2023-08-30 |  | 2023-08-30 11:58 | P11201 | P11201 | P11201 |  | Dear Sir, We have a complaint with the product P11201,P1132, kindly register the complaint, kindly avail service technician at the site as soon as possible which is very critical. Contact Name: Gafoor Puthur Account Name: Samas Home concepts LLP Samas Home Concepts LLP Samas Tower, Ooty Road Cherani, Manjeri-676122 Malappuram, Mob: +91 9048 980 999 Invoive date 21 july 2023 Invoice no: 5732 Samas Home Concepts LLP Samas Tower, Ooty Road Cherani, Manjeri-676122 Malappuram, Mob: +91 9048 980 99 | 2023-08-30 | 2023-09-01 16:19 | No | Warranty | Samas Home concepts LLP | MM 6/81-F, Cherani, Nelliparambu, | Malappuram | 676121 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found livia switchs indicator not working P1181 2NOS P1132 1NOS replaced problem solved | Repair |  | 9- Service Validated | 2023-09-01 16:23 |  |  | 60 | INR | 60 | ENM HOME DISTRIBUTION
WO-11183313 | 103655134 | 2023-08-30 13:43 | 2023-08-30 | NA | 2023-08-30 13:28 | A9N16208 | A9N16208 | A9N16208 |  | Dear sir, In Invoice number MEPL/03651/23-24 one 63A,dp,30mA,RCCB is not working at site(Not tripping). Kindly visit the site and do the needful. Site Address: Runwal Bliss,Crompton Greaves Compound, Kanjur Village Rd,Nr kanjurmarg Station Road, Kanjurmarg East Mumbai-400042 Model no: A9N16208 Contact person name Mr. Sudama Contact number: 7208710090 Mon to Fri 9:00 am to 6:00 pm. Kindly find attachment of invoice and photos of same. Best regards M.N.Badra Contact number:+91 9167616799/9920567308 Integral Switchgear and Controls Vasai East Palghar Maharashtra | 2023-08-30 | 2023-09-02 20:17 | No | Warranty | M.N.Badra | Runwal Bliss,Crompton Greaves Compound, Kanjur Village Rd, Nr kanjurmarg Station Road, null | Mumbai | 400042 | Maharashtra | India FS ED&I CSP West Team East India Power Engineers Mumbai | Sandeep Ingavale East India Power engineers Mumbai | East India Power Engineers (5043) | Visited the and checked the RCCB by given supply to the incoming sidey and checked the outgoing not showing voltage in on condition. RCCB Pol found open. | Repair |  | 8- Service Completed | 2023-09-08 16:50 | =S= Consig Fill up 226015069 |  | 13 | INR | 13 | ENM HOME DISTRIBUTION
WO-11183655 | 103659920 | 2023-08-31 15:27 | 2023-08-30 |  | 2023-08-30 16:31 | X7003WH_N | X7003WH_N | X7003WH_N |  | Opale switc complaint USB charging socket faulty X7003wh---2 nos Inv dated :- April 2023 Attached House number 147, Main road nurmahal to jalandhar cant. Village Diwali Jalandhar 144020 9041705188--Suprinder | 2023-08-30 | 2023-09-02 16:56 | No | Warranty | Suprinder Suprinder | House number 147, Main road nurmahal to jalandhar cant. Village Diwali | Jalandhar | 144020 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the socket switch found not giving output. Hence faulty replaced. X7003WH - 2 Nos. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-02 17:01 |  |  | 75 | INR | 75 | ENM HOME DISTRIBUTION
WO-11185942 | 103665482 | 2023-08-31 12:51 | 2023-08-31 |  | 2023-08-31 09:43 | P1002_6_DG | P1002_6_DG | P1002_6_DG |  | Dear team, Name of Customer AJMAL CHIRAKKAL Site Address CHIRAKKAL HOUSE KAMMANKODE KALLACHI (PO), NADAPURAM KOZHIKODE - 673504 Name of Contact Person at Site AJMAL CHIRAKKAL Contact Phone / Mob. No: 7560833373, 8606779981 Defective Product Details P1002 : 3 PCS P1001 : 4 PCS P3200 : 1 PCS Nature of Defect Not working Quotation no: 134 Quotation Date : 22 may 2023 Kindly arrange the site visit and solve the issue as soon as possible. -- Thanks & RegardsLAN MARKETING 12/16 M-S Opp.Juma Masjid Areekode-Kondotty Road Chemrakkattur Pin-673639 Customer Care: 8304903103 | 2023-08-31 | 2023-09-04 15:28 | No | Warranty | AJMAL CHIRAKKAL | Site Address CHIRAKKAL HOUSE KAMMANKODE KALLACHI (PO), NADAPURAM | KOZHIKODE | 673504 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found livia switchs struck issue and fan regulater speed variation issue P1001 1NOS P1002 1NOS P3200 1NOS P0708 1NOS part replaced problem solved | Repair |  | 9- Service Validated | 2023-09-05 15:31 | Hi Team, Material booked zfre Zvo : 226022893 |  | 70 | INR | 70 | ENM HOME DISTRIBUTION
WO-11187646 | 103684007 | 2023-08-31 13:24 | 2023-08-31 |  | 2023-08-31 11:43 | UNS61SW1M_GY | UNS61SW1M_GY | UNS61SW1M_GY |  | Hi, PFA, complaint registration details for a newly installed site for Unica switch Please send a technician to this site as soon as possible. Name of Customer Prajeesh kp Site Address kanhirakole puthiyaveetil,Thondanore, Pariyaram(PO) pincode - 670502 Kannur Name of contact person at site Prajeesh kp Contact Phone / Mob. No: 7907395926,8714284998 Defective product details Unica Pure 6AX 1WAY SWITCH GRAY Nature of Defect UNS61SW1M_GY Customer is facing issues with Unica Pure 6ax 1WAY SWITCH Warranty status Under Warranty Commissioned / Installed date One month Serial No: or DOM of the product Name & Phone No: of person registering the complaint Mohammed Jebrood- 9743182896 Invoice Date : 14/ 07/ 2023 Invoice NO: A2741 Thanks & Regards, MJ Marketing 33/480, AM Building, Railway Station Road, Near Keloth Juma Masjid, Keloth, Payyanur - 670307 PH : 04985 209896, 9188 209896 Email : contact@mjmarketing.in "We know you have many choices in doing business and we THANK YOU for choosing us!" | 2023-08-31 | 2023-09-02 19:26 | No | Warranty | Prajeesh kp | kanhirakole puthiyaveetil,Thondanore, Pariyaram(PO) | Kannur | 670502 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Rejilesh APSMarketingCompany Calicut | APS Marketing Company | visited this site found unica one way and 16a switch struck issue unica 16a 1nos unica 1way 2nos replaced problem solved | Repair |  | 9- Service Validated | 2023-09-02 19:30 |  |  | 120 | INR | 120 | ENM HOME DISTRIBUTION
WO-11188426 | 103697319 | 2023-09-01 11:17 | 2023-08-31 |  | 2023-08-31 17:22 | A9N16205 | A9N16205 | A9N16205 |  | Fwd: Case : 103516934 dt. 24.8.23 ear Sir, Mr. Deepak Yadav VPO Lookhi,Nr Govt High School, Teh Kosli,Rewari Mr. Deepak Yadav 9813824124 Product : A9N16205 Not Tripping -- *WITH REGARDS-* Sarabjit Singh SHARMA ELECTRIC WORKS | 2023-08-31 | 2023-09-01 11:19 | No | Warranty | Deepak Yadav | VPO Lookhi, Nr Govt High School, Teh Kosli | Rewari | 123303 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the Rccb found tripping issue due to customer not use valid method to check RCCB. Product found working ok. Email : id not provided by customer . | Repair |  | 9- Service Validated | 2023-09-01 11:24 |  |  | 85 | INR | 85 | ENM HOME DISTRIBUTION
WO-11018187 | 102679537 | 2023-08-03 14:35 | 2023-07-21 |  | 2023-07-21 14:21 | A9HTND06 | A9HTND06 | A9HTND06 |  | DOP: A9HTND06 ? 350 No?s A9HTND08 -04 P: Rust issue M/s:Naresh Electricals C/o: Utopia ( Casa Grande ) Project Sriram Gardens Indira Nagar Manapakkam Chennai Ramapuram Tamil Nadu ? 600125 Contact Person: Mr. Chinna Durai / Project Manager Contact No: 9206413122 | 2023-07-21 | 2023-09-19 17:35 | No | Warranty | M/s:Naresh Electricals C/o: Utopia ( Casa Grande ) Project | Sriram Gardens Indira Nagar Manapakkam Chennai Ramapuram null | Kanchipuram | 600125 | Tamil Nadu | India FS South2 ED&I CSP UpservePowerSystems Chennai | HARI PRASATH UpservePowerSystems Chennai | Upserve Power Systems | Arranged Spray paint & gasket from factory. | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-19 17:47 |  |  | 10 | INR | 10 | ENM HOME DISTRIBUTION
WO-11191456 | 103701042 | 2023-09-01 11:52 | 2023-09-01 |  | 2023-09-01 10:28 | A9KF71463BQS | A9KF71463BQS | A9KF71463BQS |  | 1) MCB K60H 4P 63A C 10kA Serial No.- A9KF71463BQ 2) Acti 9 RCCBxID 4P 30mA AC type Serial No.- A9N16254 This Two Products Not Working. Please Help. Invoice NO: NS1214/23-24 Invoice Date: 10/06/2023 Praveen Pandhare Mob.- 7024210076 Kartvya Bulding, Plot no 154 C Sheme no: 103 , Kesarbag Road, Near Awasa Colony Indore 452009 MP | 2023-09-01 | 2023-09-01 15:15 | No | Warranty | Praveen Pandhare | Kartvya Bulding, Plot no 154 C Sheme no: 103 , Kesarbag Road, Near Awasa Colony | Indore | 452009 | Madhya Pradesh | India FS ED&I CSP West Team ABR Technical Service Indore | Chirag Jain_ABR Tecneical Services Indore | ABR Technical Services (9574) | Reached at retailer office and as per customer RCCB and MCB not working properly. Then we check RCCB ON/OFF operation and found ok. Then we check RCCB continuity and found ok. Checked RCCB ON load (415VAC) and found working properly. Also checked with test button Rccb tripping ok. Then we check MCB on/off operation and found dolly free. So we rectified the issue and checked ON-OFF 5-6 times now it's working properly. Then We checked MCB on load (415VAC) and found it working properly. So we are now closing this case. | Repair |  | 9- Service Validated | 2023-09-01 15:16 |  |  | 17 | INR | 17 | ENM HOME DISTRIBUTION
WO-11193940 | 103720514 | 2023-09-02 11:04 | 2023-09-01 |  | 2023-09-01 12:58 | IN8486/32>SZ-OS | IN8486/32>SZ-OS | IN8486/32>SZ-OS |  | Zencelo Switches 32 apr Invoice Date 17 august 2023 Invoice Numb 2109/23-24 IN8486/32 1 Switch is not working Nitin Dehmiwal 965062399 Address flat no 21 Karuna vihar, Plot number 09, Sector 18 A Dwarka , Nwe Delhi 110078 | 2023-09-01 | 2023-09-04 16:22 | No | Warranty | Nitin Dehmiwal | flat no 21 Karuna vihar, Plot number 09, Sector 18 A Dwarka | New Delhi | 110078 | Delhi | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the switches and found switches have stuck issue, As per serial number switches not cover under warranty. Customer providing the invoice. We replace the faulty switches with new. | Repair |  | 9- Service Validated | 2023-09-04 16:28 |  |  | 42 | INR | 42 | ENM HOME DISTRIBUTION
WO-11194480 | 103719874 | 2023-09-01 20:24 | 2023-09-04 | Validated By Prashant | 2023-09-01 13:54 | IN8401_BZ | IN8401_BZ | IN8401_BZ |  | ---------- Forwarded message ---------From: pinku Jha <pinkumar1994@gmail.com>Date: Wed, Aug 2, 2023, 18:21Subject: Complaint or Suresh eleTo: Schneider Electric <customercare.in@schneider-electric.com> Juhu vikrant / juhu acropolis. 9th road juhu B - 901. Mr Santosh - 9867887403. Faulty switch - INI401(BZ) | 2023-09-01 | 2023-09-05 17:30 | No | Warranty | Santosh Kumar | Juhu vikrant / juhu acropolis. 9th road juhu B - 901. | Mumbai, | 400049 | Maharashtra | India FS ED&I CSP West Team S K SERVICES Mumbai | Ganesh Tati_S K SERVICES Mumbai | S.K. Services (10237) | We Visited Site 6A 1 Way Switches is Properly Not Operating So Stuck issue We Replace The Product From Our Stock Closed The Complaint We Check All Switches Boards All Operating Ok We Solved & Closed | Repair |  | 9- Service Validated | 2023-09-05 22:27 | =S= Consig Fill up 226030280 |  | 16 | INR | 16 | ENM HOME DISTRIBUTION
WO-11195040 | 103723936 | 2023-09-02 10:41 | 2023-09-01 |  | 2023-09-01 15:44 | IN84SFR_WE | IN84SFR_WE | IN84SFR_WE |  | Ashok Jalota 20 06 2023 Regulator is not working 1 Pc IN84SFRW Inv no 2314565 Addre 13/C Grounffloor singarnagar Alambag Lucknow Central India tubewell coorporation citc_lko@yahoo.co.in | 2023-09-01 | 2023-09-07 16:29 | No | Warranty | Ashok Jalota | 13C Sringar nagar Alambagh | Lucknow | 226005 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Abhishek Patel Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found Fan regulator having speed variation issue so we replaced. | Repair |  | 9- Service Validated | 2023-09-07 16:33 | You need to book two reference 1 each against your UNPCP8ML_ML. UNPSP8ML_ML : 1 Pcs UNPGP8ML : 1 Pcs |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-11195230 | 103723125 | 2023-09-04 09:54 | 2023-09-01 |  | 2023-09-01 17:13 | A9N4P63C | A9N4P63C | A9N4P63C |  | Om parkash m.no 9815409842 7837426747 Invoice number: RL1262 Invoice date : 26 04 2023 omelectricworks04@gmail.com Laye 9 14 LRD16 MCB: A9n4p63c Nwekidwai nagar House no. 45/2/A Street no. 2 near Devki devi jain collage Ludhiana 141008 | 2023-09-01 | 2023-09-04 11:13 | No | Warranty | Om Electric Works | Nwekidwai nagar House no. 45/2/A Street no. 2 near Devki devi jain collage null | Ludhiana | 141008 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the mcb found phase missing and relay found nc contact not working, Hence faulty replaced. LRD16 - 1 nos A9N4P63C - 1 nos Email : omelectricworks04@gmail.com | Repair |  | 9- Service Validated | 2023-09-04 13:10 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11195237 | 103724569 | 2023-09-02 11:45 | 2023-09-01 |  | 2023-09-01 17:14 | CPX32DP2M_WE | CPX32DP2M_WE | CPX32DP2M_WE |  | Complaint in ClipsalX range lease send your technical engineer at the site as the client is facing issues in the ClipsalX range. CPX32DP2M_WE - 5 pieces CPX6BP2M_WE - 2 pieces CPX4STFAN1M_WE - 2 pieces CPX5STFAN2M_WE - 2 pieces CPX101SW1M_WE - 2 pieces CPX102SW1M_WE - 1 piece CPX161SW1M_WE - 2 pieces Customer Details Avdesh Kumar Sharma Address - MIG-135, Ramganga Vihar, Moradabad - 244001, (U.P.) Contact number - 9897048770 | 2023-09-01 | 2023-09-11 14:25 | No | Warranty | Akashdeep Electricals | MIG A-135 Near Sonakpur Stadium, Ramganga Vihar Phase-1 | Moradabad | 244001 | Uttar Pradesh | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the switches and found switches have dolly free issue and breaking issue and fan regulator have output issue. As per serial number switches not cover under warranty. Customer provide the invoice. We replace the faulty switches and fan regulators with new. | Repair |  | 9- Service Validated | 2023-09-11 14:25 |  |  | 164 | INR | 164 | ENM HOME DISTRIBUTION
WO-11199078 | 103731093 | 2023-09-02 11:31 | 2023-09-02 | Part order request validated by Mr. Chandrakant Panchal Sir | 2023-09-02 10:13 | A9N16263 | A9N16263 | A9N16263 |  | Sir/Mam, Pls Register complain of RCCB & find invoice copy against which RCCB supplied Invoice Date : 2 Jun 2023 Invoice number : SIE/G-237/23-24 RCCB 80 A 4 POLE 300mA CAT. NO.A9N16263 IS NOT WORKING Customer details as follows SAGAR SERVICES & RESOURCES PVT. LTD E/2/4 ARERA COLONY , BHOPAL CONTACT PERSON NAME :Mr. Rohit Gurjar M-8435573605 mail id.:ssr.purchase@thesagar.in ssrpl.mep@thesagar.in Thanks & Regards Dipak SIDDHANT INSTRUMENTS & EQUIPMENTS B-76, Crystal Tower, Kasturba Nagar, Near Chetak Bridge, Bhopal-462023 (M.P.) Ph. : 0755 - 4231614 Mob: +91 9399064701 (Rakesh), +91 9826014838 (Sanjeev Gupta) We are registered in MSME, WIRES / CABLES / GLAND / LUGS / PRESSURE GAUGE / THERMOCOUPLES / RTD / MCCB / MCB / CONTROLLER ...... MORE ELECTRICALS & INSTRUMENTS ITEMS | 2023-09-02 | 2023-09-04 14:54 | No | Warranty | Siddhant Instruments & Equipments | B-76, Crystal Tower, Katurba Nagar null | Bhopal | 462023 | Madhya Pradesh | India FS ED&I CSP West Team ABR Technical Service Indore | Lalu Sen_ABR Tecneical Services Indore | ABR Technical Services (9574) | Reached at site and checked the RCCB (A9N16263) is found details are given below.1) Checked the RCCB (A9N16263) ON/OFF found its ok. the we checked the power pole continuity is not ok then we checked the RCCB Test switch is also not trip the RCCB. So customer satisfaction we recommended to replace 1 NO. RCCB & Defective RCCB collected from the site | Repair |  | 9- Service Validated | 2023-09-05 14:56 | =S= Consig Fill up 226023044 |  | 220 | INR | 220 | ENM HOME DISTRIBUTION
WO-11024976 | 102706312 | 2023-07-27 15:02 | 2023-07-24 |  | 2023-07-24 10:19 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | DOP: 29/6/2023 IH100WFVDP Smart Doorbell Qty:1 P: installation RINSHAD RASHEED Address:-PERIYAR HERMITAGE FLAT NO : A1C5aluva ,company padi, spw Road,Near SPW school Pincode : 683106 Ph No:-8289830063 | 2023-07-24 | 2023-09-02 12:38 | No | Commercial Action - Sales | RINSHAD RASHEED | PERIYAR HERMITAGE FLAT NO : A1C5aluva ,company padi spw Road Near SPW schoo | Ernakulam | 683106 | Kerala | India FS South2 ED&I CSP PrinterPeople Cochin | Renjith PR PrinterPeople Cochin | PRINTER PEOPLE-COCHIN | INSTALATION DONE | Commissioning & Installation | Start-up | 8- Service Completed | 2023-09-02 12:40 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11200487 | 103740657 | 2023-09-02 11:30 | 2023-09-02 | VDP not working | 2023-09-02 11:13 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Dear Team, Please arrange a technician for Service of Following Components at below Location: Product to be Serviced: Wiser Smart Doorbell ( IH100WFVDP ) ?> Quantity = 1. Invoice Number : P05080/22-23 Invoice Date : 16 Nov 2022 IH100WFVDP Type of Request Installation / Break fix Break fix Name of Customer V Uptown by Tatvam Constructions Site Address Ravet Kiwale Link Road, Kiwale Pune Near Jai Ganesh Lawns, Pimpri Chinchwad 412101. Name of contact person at site V Uptown by Tatvam Constructions 5 Customer Mail ID - 6 Contact Phone / Mob. No: Mr. Ravindra - 8355925730 Product To Be installed / Faulty Qty Wiser Smart Doorbell 1 Issue Smart Doorbell is Disconnected from the Internet. Project Name: V-Uptown by Tatvam Constructions Location: Ravet Kiwale Link Road, Kiwale Pune Near Jai Ganesh Lawns, Pimpri Chinchwad 412101. Contact: Mr. Ravindra (Flat no.702) ? 8355925730. | 2023-09-02 | 2023-09-02 15:47 | No | Warranty | V Uptown by Tatvam Constructions | Ravet Kiwale Link Road, Kiwale Pune Near Jai Ganesh Lawns, Pimpri Chinchwad null | Pune | 412101 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Kunal jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the VDP not working . observed The VDP Camera is not showing video footage. camera showing pink color footage. this problem is not repairable. So VDP needs to be replaced. Required Material : IH100WFVDP - 01 nos | Repair |  | 9- Service Validated | 2023-09-02 16:21 | =S= Consig Fill up 226023462 |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11200723 | 103742414 | 2023-09-04 16:46 | 2023-09-02 |  | 2023-09-02 16:08 | IN8408SC_BZ | IN8408SC_BZ | IN8408SC_BZ |  | Dear team, Pls register complaint of Zencelo Fitment of IN8408SC & IN8486/32 Prshant Goyal #72 greencity1,Bathinda 151001 Punjab pH = 9517102618 2 way = 2 pcs not working In voice number : 834/2023-24 Invoice date : 30-04-2023 Thanks & Regards, SANJAY KUMAR Manager-Sales Home and Distribution DivisionSchneider Electric http://www.facebook.com/SchneiderElectric Landline: +91 7087045622 Mobile: +91 9802600986 Email: sanjay.kumar1@se.com CC 18001030011/ 18004254272 2nd Floor, SCO 23,Sector 32,Chandigarh Road Ludhiana - 141010INDIA Download mySchneider app 24/7 support. Mobile catalog. Access to expert help. *Please consider the environment before printing this e-mail Internal | 2023-09-02 | 2023-09-07 13:24 | No | Warranty | Prshant Goyal | #72 greencity1 ,Bathinda | Bathinda | 151001 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | checked the switches found working properly. On site plates fitting issue. Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-07 13:28 |  |  | 150 | INR | 150 | ENM HOME DISTRIBUTION
WO-11200757 | 103742600 | 2023-09-04 17:06 | 2023-09-02 |  | 2023-09-02 16:58 | P1001_N | P1001_N | P1001_N |  | Dear team, Pls register complaint of LIVIA p1001_n Gurpreet Ankhi R/o near bus stand Mehal klan 148104 Dist. Barnala Punjab 9914565135 Invoice date : 02-08-2023 Invoice Number ; 243 Thanks & Regards, SANJAY KUMAR Manager-Sales Home and Distribution DivisionSchneider Electric http://www.facebook.com/SchneiderElectric Landline: +91 7087045622 Mobile: +91 9802600986 Email: sanjay.kumar1@se.com CC 18001030011/ 18004254272 2nd Floor, SCO 23,Sector 32,Chandigarh Road Ludhiana - 141010INDIA Download mySchneider app 24/7 support. Mobile catalog. Access to expert help. *Please consider the environment before printing this e-mail Internal | 2023-09-02 | 2023-09-07 13:28 | No | Warranty | Gurpreet Ankhi | R/o near bus stand Mehal klan 148104 Dist. Barnala | Barnala | 148104 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | checked the switches found not working properly. Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-07 13:30 |  |  | 85 | INR | 85 | ENM HOME DISTRIBUTION
WO-11200797 | 103742804 | 2023-09-05 11:33 | 2023-09-02 |  | 2023-09-02 17:58 | EZ9F76316 | EZ9F76316 | EZ9F76316 |  | Hi, Please find the inline response for your reference: Invoice number ; 2160/PE/22-23 Invoice date : 06-sept-2022 EZ9F76316 616139 D2138 Nikhil Agarawal 9414978819 Aaraji No. 622/372, SATYAM INDUSTRIES, NAUGAWAN ROAD, Mujras/Behind Gas Boundary, Mujras, Bhilwara, Rajasthan, 311802 If you need anything else, let me know. Best Regards, S.N. Agarwal Satyam Industries satyamindustries622@gmail.com | 2023-09-02 | 2023-09-11 15:43 | No | Warranty | SATYAM INDUSTRIES | Aaraji No. 622/372, SATYAM INDUSTRIES, NAUGAWAN ROAD, Mujras/Behind Gas Boundary, Mujras, null | Bhilwara | 311802 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | checked the mcb found phase missing . Hence faulty, replaced . EZ9F76316 - 1 Nos. Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-11 15:45 |  |  | 250 | INR | 250 | ENM HOME DISTRIBUTION
WO-11208828 | 103754271 | 2023-09-04 11:06 | 2023-09-04 | NA | 2023-09-04 09:58 | A9N4P40C | A9N4P40C | A9N4P40C |  | Dear Sir/Madam, I would like to inform you that I have purchased 7 Nos. of MCB from AMAZON (E-commerce), which were delivered to me between 24.05.2023 to 27.05.2023. It was installed on 03.06.2023 but three out of seven were not working properly and I raised a complaint against it being replaced by your service centre but another three no. of MCB not working now and photograph of same attached herewith. Arjun Kumar Flat no: 3h Block 3 , Rajwada garden, Kamalgazi Kolkata, WB 700103 A9N4P40C Invoice Date : 22;05;2023 arajunkumar@gmail.com Arjun Kumar +91-9830201800 I am attaching all seven MCB invoice copy and warranty slips for your reference and attaching faulty MCB photographs. We request you to kindly replace faulty MCB at the earliest. Thanks & Regards Arjun Kumar +91-9830201800 | 2023-09-04 | 2023-09-05 13:30 | No | Warranty | Arjun Kumar | Flat No. 3 H, Block 3, Rajwada Grand, Kamalgazi | Kolkata | 700103 | West Bengal | India FS ED&I CSP East Team B.D Electroservices Kolkata | RAHUL RAY_B.D Electroservices Kolkata | B.D Electroservices(500017330) | On received of ZVO material will delivered to customer. | Repair |  | 9- Service Validated | 2023-09-05 12:31 |  |  | 24 | INR | 24 | ENM HOME DISTRIBUTION
WO-11210576 | 103756140 | 2023-09-04 20:08 | 2023-09-04 | Validated By Prashant | 2023-09-04 11:28 | IN8401_N | IN8401_N | IN8401_N |  | Zencelo 1 switcheches IN8401_N Invice date : 2 september 2023 801 e wingh ABT appartment Rnai city marg M 400097 Neha poddar. | 2023-09-04 | 2023-09-05 14:54 | No | Warranty | Neha Poddar | 801, ABT Apartment, A wing, Ranisati Marg, Malad | Mumbai | 400097 | Maharashtra | India FS ED&I CSP West Team S K SERVICES Mumbai | Ganesh Tati_S K SERVICES Mumbai | S.K. Services (10237) | We visited the site Product Ref No:-IN8486/32-1Nos Serial No-23353 We check the material 32A DP switch is operating ok Some other switches like IN801 is facing contact problem we change the contact now operating ok. | Repair |  | 9- Service Validated | 2023-09-05 14:55 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11210631 | 103755642 | 2023-09-05 12:13 | 2023-09-04 |  | 2023-09-04 11:55 | A9N4P32D | A9N4P32D | A9N4P32D |  | RE: Fwd: Schneider makes 4P MCB 32A A9N4P32D MCB ON/OFF not working [ thread::ZDGOyrAGclyOqdX-WtIuND4:: ] Please arrange replacement/ depute our service engineer on priority. Part number A9N4P32D ? 1 QTY Schneider invoice number - 9008606393 Contact Person ? Mr. Neeraj Sharma (9760010550) Address - Plot No.1A, Sector-8C, Integrated Industrial Estate, Ranipur-249403, Hardiwar, UK Mobile: +91 9760010550. Mail id - neeraj.sharma@cselectric.co.in Ashish Bhatt | 2023-09-04 | 2023-09-05 15:35 | No | Warranty | Neeraj Sharma | Plot No.1A, Sector-8C, Integrated Industrial Estate, Ranipur- | Haridwar | 249403 | Uttarakhand | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the mcb found dolly free & not getting on. Hence faulty replaced. A9N4P32D - 1 Nos. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-06 11:30 |  |  | 215 | INR | 215 | ENM HOME DISTRIBUTION
WO-11210829 | 103759035 | 2023-09-05 11:47 | 2023-09-04 |  | 2023-09-04 12:46 | A9N4P32C | A9N4P32C | A9N4P32C |  | Re: COMPLAINT [ thread::Nsttg228cb2MlKUm4mQHSz4:: ] Dear sir Pls check the depute your engg. at our company Contactor & MCB Not working Contactor 9A 3P, 220V AC LC1D09 Not working -1Nos MCB 32A 4P, 10KA C-Curve ( A9N4P32C) Screw Problem -1Nos MCB 20A 4P, 10KA C-Curve ( A9N4P20C) Screw Problem -1Nos -- Thanks & Regards Rakesh Yadav M/S Anubhav Power & Controls Plot No 138,Sec-6, IMT Manesar Gurgaon Haryana Ph: +0124-4367438-439 Fax: +0124-4367440 Mob : +91-9953589525, Email: salesanubhavpower138@gmail.com www.anubhavpowercontrols.com | 2023-09-04 | 2023-09-11 12:59 | No | Warranty | Anubhav Power & Controls | Plot No. 138, Sec-6, IMT Manesar | Gurgaon | 122050 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mcb found screw free and contactor found coil not working, Hence faulty replaced. A9N4P32C - 1 nos LXD1M7 - 1 nos Email : | Repair |  | 9- Service Validated | 2023-09-12 13:07 | 226031690 |  | 55 | INR | 55 | ENM HOME DISTRIBUTION
WO-11210933 | 103759819 | 2023-09-04 13:53 | 2023-09-04 |  | 2023-09-04 13:06 | EZ9F76116 | EZ9F76116 | EZ9F76116 |  | MCB--Complaint Product : EZ9F76116 MCB Sr No. D 2213 DOM March 2022 Yes, in Warranty Phase Not Passing Current ?Metalink Engineers 3636, Sector 32 A Chandigarh Road Ludhiana 145526 Mr Ashwani 6284763485,9023506414 Mail Id : aakash@nmaindia.com | 2023-09-04 | 2023-09-04 13:55 | No | Warranty | Metalink Engineers | Sector 32-A ,3636 Chandigarh Road | Ludhiana | 141010 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the mcb found Phase Not Passing Current due to knob broken and capacitor found derated and USB found not power up & not working. Hence faulty replaced. EZ9F76116 - 1 Nos. MEHVBHDY250A44 - 2 Nos. UNS21USB1P1M_WE - 4 Nos. email : aakash@nmaindia.com | Repair |  | 9- Service Validated | 2023-09-04 16:15 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11210968 | 103760354 | 2023-09-04 13:59 | 2023-09-04 |  | 2023-09-04 13:22 | A9KF71463 | A9KF71463 | A9KF71463 | D2231 | A9KF71463 ---Pole Open / phase missing Product :A9KF71463 MCB Sr no. D2231 DOM Aug - 2022 Warranty YES Pole Open / phase missing DARSHAN ELECTRIC STORE SHOP NO - 27, Near Modern International School Ganganagar 335001 Mr. Ajeet Singh 7347381906 | 2023-09-04 | 2023-09-04 14:10 | No | Warranty | DARSHAN ELECTRIC STORE | SHOP NO - 27, Near Modren Internation SChool | Ganganagar | 335001 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | Checked the contactor found open pole issue and mcb found phase missing , Hence faulty replaced. LC1D1150046M7 - 1 nos A9N4P63C - 1 nos Email : | Repair |  | 9- Service Validated | 2023-09-04 16:12 |  |  | 460 | INR | 460 | ENM HOME DISTRIBUTION
WO-11210997 | 103758540 | 2023-09-04 13:49 | 2023-09-04 |  | 2023-09-04 13:35 | IN84213IS_BZ | IN84213IS_BZ | IN84213IS_BZ |  | Dear Sir/Madam Please Provide Complain number has per Attached Deta Checklist for Complaint Registration 1 Name of Customer M/S SHAH ELECTRIC CO. 2 Site Address G-13, GROUND FLOOR, BELGIUM SQUARE, RING ROAD,SURAT- Contact Phone / Mob. No: 7698897074 3 Name of contact person at site MR.BHAVESH BHAI 5 Defective product details IN84213IS (BZ) - QTY - 04 , IN8401 - 07 6 Product Make SCHNEIDER-TruGlobal Soc. - DG , 6A 1W Full-Flat Switch w/Indi-DG 7 Nature of Defect NOT WORKING 8 Shutdown availability if applicable 9 Warranty status UNDER WARRANTY 10 Commissioned / Installed date 11 Serial No: or DOM of the product BILL NO - : 1067/22-23 DATE - 10-05-2022 12 Name & phone No: of person registering the complaint JOHNSON- 8780431402 13 NOTE Note : Point Nos: 1 to 9 are compulsory JOHNSON..Mob No:8780431402 EPABX No: 0261-2432308, 2420774 / 7383732308 / 9737326676 Hi-Tech Marketing NOTE: our new address is Hi-Tech Marketing"HI-TECH House"SHOP NO: 209, SNS INTERIO, E-Block,Bhatar-Althan Road,Surat-395007E mail:- hitech.surat@gmail.com www.hitechmarketing.co.in Location: https://www.google.com/maps/place/21%C2%B009'36.9%22N+72%C2%B048'41.0%22E/@21.1602815,72.8117754,20z Ashok K. Gandhi - 09376932308 - Kamal N. Parikh - 09376920774 - Hemen K. Gandhi - 09374726676 - Akash H Gandhi - 09173063086 | 2023-09-04 | 2023-09-05 16:11 | No | Warranty | SHAH ELECTRIC INC. | G-13, Ground Floor, Belgium Square, Ring Road null | Surat | 395002 | Gujarat | India FS ED&I CSP West Team SHIV SAI ELECTRICALS Vapi | SHIVAM LAD SHIV SAI ELECTRICALS VAPI | shivsai electricals | AS PER SITE VISIT WE CHECK THE PRODUCT AND FOUND OK ON VISUAL INSPECTION.AFTER THAT CHECK THE SWITCH AND FOUND THE SWITCH IS BOROKEN.WHEN WE CHECK THE PRODUCT WARRNTY STATUS AND FOUND THE PRODUCT I UNDER WARRNTY NEEDS TO BE REPLACED. | Repair |  | 9- Service Validated | 2023-09-06 16:12 | =S= Free Order 226038497 |  | 139 | INR | 139 | ENM HOME DISTRIBUTION
WO-11211049 | 103759118 | 2023-09-04 16:25 | 2023-09-04 | VDP Installation | 2023-09-04 13:43 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Fwd: WO-11106487 from Schneider Electric Main Installed Product Name : IH100WFVDP Main IP Serial Number : Work Order Reason:Regarding Wiser Smart Doorbell Installation at Mr. Ashok Kori Product to be Installed: Wiser Smart Doorbell ( IH100WFVDP ) ?> Quantity = 1. Arihant Electric Corp--8 Aug 2023 | 2023-09-04 | 2023-09-04 17:04 | No | Commercial Action - Sales | Ashok Kori | Shailesh Society, Near Alankar Police Chowky, Plot No 61, Karvenagar | Pune | 411052 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Sachin Jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the product IH100WFVDP - 01 nos. we given 220V supply to doorbell and set up the i9n mobile. then we mount in on wall. then installed device in customer mobile. then taken operation found ok/ | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-04 17:06 |  |  | 40 | INR | 40 | ENM HOME DISTRIBUTION
WO-11211122 | 103759420 | 2023-09-04 14:18 | 2023-09-04 |  | 2023-09-04 14:11 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | RE: VDP Replacement Please raise the Wiser Smart Door Bell Repair Wo for Following Customer SM Industries. Add. = 106 /313 A Gandhi Nagar Kanpur. 208012 Contact. Parson = Abhishek Gupta. Contact No. = 7318001155 Issue : IH100WFVDP is Not working , Unable to Reset @Aman : Please book the ZVO for Smart door bell Warm Regards Ramakanth Kumathe | 2023-09-04 | 2023-09-09 16:51 | No | Warranty | Abhishek Gupta | 106 /313 A Gandhi Nagar | Kanpur | 208012 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Aman Khare_Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found VDP having internal issue so we replaced. | Repair |  | 9- Service Validated | 2023-09-09 16:54 |  |  | 115 | INR | 115 | ENM HOME DISTRIBUTION
WO-11211171 | 103761763 | 2023-09-05 13:39 | 2023-09-04 |  | 2023-09-04 14:30 | A9N4P40C | A9N4P40C | A9N4P40C |  | HelloI am Sakshi from kalinga international I want to register a complaint regarding MCB. all information is mentioned below&#128071;&#128071; Name - sakshi Contact - 9625575030 Address - kalinga international, 5/1, west patel nagar , new delhi - 110008 product - MCB 40 AMP FP Serial no - 3 606480 497865 MCB 40 APR A9N4P40C Not working Invoive Date: 16 dec 2022 Sakshi Rawat 9625575030 Kalinga International 5/1 west Ptel Ngar New DEelhi 11008 sakalinga179@gmail.com | 2023-09-04 | 2023-09-11 14:02 | No | Warranty | Kalinga International | Kalinga International 5/1 west Ptel Ngar New DEelhi null | New Delhi | 110008 | Delhi | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mcb found dolly free , Hence faulty replaced. A9N4P40C - 1 nos Email : id not provided by customer. | Repair |  | 9- Service Validated | 2023-09-12 14:04 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11211422 | 103765768 | 2023-09-05 15:26 | 2023-09-04 |  | 2023-09-04 16:07 | A9N26643 | A9N26643 | A9N26643 |  | Re: [ thread::55Y7-pV1dTyHyd5zK3x7tD4:: ] VIGI A9N26643 for the below address. Regards, Team Tayan TAYAN TECHNOLOGY PLOT NO. 12/2 BASAI INDUSTRIAL AREA ¦ GURGAON 122001 ¦ INDIA Mobile: +91 98965 25241 ¦ +91 79064 58722 ¦ +91 72100 67671 Mail: tayan@tayantech.in Web: www.tayantech.in | 2023-09-04 | 2023-09-12 15:27 | No | Warranty | TAYAN TECHNOLOGY | PLOT NO. 12/2 BASAI INDUSTRIAL AREA null | GURGAON | 122001 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mcb found dolly free and contactor found screw free , rccb found on / off issue, Hence faulty replaced. A9N26643---2 nos LC1E3210M7--1 nos A9R11491--1 nos Email : id not provided by customer. | Repair |  | 9- Service Validated | 2023-09-12 15:32 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11215307 | 103769712 | 2023-09-05 11:39 | 2023-09-05 |  | 2023-09-05 11:07 | A9N18374 | A9N18374 | A9N18374 |  | Dear Sir, We have purchased 02nos 100 Amps, 3 pole MCB from Mayfair Electricals (Visakhapatnam) on dated 27 May 2023 vide Invoice No. MFE/22-23/5828. Now 01no MCB is not working properly. Kindly replace defective MCB with new MCB. Invoice copy attached for your necessary action. 100ATPMCB A9N18374 Invoice date : 27-March-2023 Invoice number : 23/5828 Sadhav Offshore engineering PVT LTD Flat no. 203, Madhuraraman Residential And Commercial Complex 30.11.9, Dabagardens, Visakhapatnam. AP 6302939352 Kingshuk Sadhav Offshore Engg. Pvt. Ltd vizag@sadhav.com Thanks & Regards Kingshuk Jena Executive (Admin) Sadhav Offshore Engg. Pvt. Ltd sadhav.com email powered by Google, setup by www.WeSetup.in | 2023-09-05 | 2023-09-11 10:04 | No | Warranty | Sadhav Offshore engineering PVT LTD | Convert JN Sea Port Ship Yard null | Visakhapatnam | 530020 | Andhra Pradesh | India FS ED&I CSP South Team Voltamp Electrical Works Visakhapatnam | Chinni SaiKumar_VOLT AMP ELECTRICAL WORKS Visakhapatnam | Voltamp Electrical Works | Visited the site and found above the Acti 9 100 A 3P MCB off time out put connecting so today we have observed the problem of MCB in put voltage is 415V MCB running condition is ok but of time MCB out put voltage pole to anther polo 170 are 140 R 20V is connecting | Repair |  | 9- Service Validated | 2023-09-11 10:05 |  |  | 20 | INR | 20 | ENM HOME DISTRIBUTION
WO-11215424 | 103783255 | 2023-09-06 12:31 | 2023-09-06 |  | 2023-09-05 11:39 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | VDP-Installation Rajat Rustagi Address : 25/3-B Aravali View Rail Vihar, Sector 56 City: Gurgaon , State: Haryana Pin: 122011 , INDIA Contact Number: 9731474488 Product : IH100WFVDP Invoice dt. : April 2023 | 2023-09-05 | 2023-09-08 04:04 | No | Commercial Action - Sales | Rajat Rustagi | 25/3-B Aravali View Rail Vihar, Sector 56 City | Gurgaon | 122011 | Haryana | India FS ED&I CSP North Team Seamtek International Pvt. Ltd. GHAZIABAD | Satish Raika Seamtek International Pvt. Ltd. GHAZIABAD | Seamtek International Pvt. Ltd. | following wiser components has benn reparired smart door bell : 1 no | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-07 16:06 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11215479 | 103783494 | 2023-09-05 12:32 | 2023-09-05 | Wiser Installation | 2023-09-05 11:52 | IH14000100 | IH14000100 | IH14000100 |  | Regarding Wiser Home Automation Installation at Mr. Parind Dedhia Please arrange a technician for Installation of Following Components at below Location: Product to be Installed: Wiser IP Gateway ?> Quantity = 1. Wiser 4 Channel Relay -> Quantity = 6. Wiser Fan Controller ?> Quantity = 3. Customer Name: Mr. Parind Dedhia Address: Tower 7, Flat No. 2001, Lodha Belmondo, Mumbai-Pune Expressway, Opp. MCA Cricket Stadium, Gahunge - 412101. Contact: 9820350090. | 2023-09-05 | 2023-09-07 11:37 | No | Commercial Action - Sales | Parind Dedhia | Tower 7, Flat No. 2001, Lodha Belmondo, Mumbai-Pune Expressway, Opp. MCA Cricket Stadium, Gahunge - | Pune | 412101 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Kunal jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the product gateway - 01 nos. AC & Light Relay - 06 nos, and fan controller - 03 nos are installed. first of all we make a proper wiring and set up the all realy and gateway in customer mobile. and installed gateway then we mount in on wall. then installed device in customer mobile. then taken operation found ok | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-07 11:48 |  |  | 45 | INR | 45 | ENM HOME DISTRIBUTION
WO-11215799 | 103788484 | 2023-09-05 16:48 | 2023-09-06 |  | 2023-09-05 14:02 | IH101ZWIFI | IH101ZWIFI | IH101ZWIFI |  | Wiser installation Phase 3 for HT Automation Gateway IH101ZWIFI - Qty--1 pc 4 Channel Automation Relay-IH14000100 - Qty--5 pcs Installation support CHOTE LAL--9811523799 | 2023-09-05 | 2023-09-06 22:27 | No | Commercial Action - Sales | Chote Lal | 7/A1 Hindustan Times Apartments, Shashi Park Rd, Mayur Vihar | Delhi | 110091 | Delhi | India FS ED&I CSP North Team Seamtek International Pvt. Ltd. GHAZIABAD | Satish Raika Seamtek International Pvt. Ltd. GHAZIABAD | Seamtek International Pvt. Ltd. | following components has been installed : gateway: 1no 4 ch. relay : 5 no. | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-06 22:27 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11215818 | 103788786 | 2023-09-06 12:46 | 2023-09-07 |  | 2023-09-05 14:09 | IH101ZWIFI | IH101ZWIFI | IH101ZWIFI |  | Wiser installation Phase 3 for HT Automation Gateway IH101ZWIFI - Qty--1 pc 4 Channel Automation Relay-IH14000100 - Qty--5 pcs Installation support SAMIR DHEERAJLAL TRIVEDI 9910495772 | 2023-09-05 | 2023-09-07 22:34 | No | Commercial Action - Sales | SAMIR DHEERAJLAL TRIVEDI | 1/C1 Hindustan Times Apartments, Shashi Park Rd, Mayur Vihar, null | Delhi | 110091 | Delhi | India FS ED&I CSP North Team Seamtek International Pvt. Ltd. GHAZIABAD | Satish Raika Seamtek International Pvt. Ltd. GHAZIABAD | Seamtek International Pvt. Ltd. | following components has been installed : gateway: 1no 4 ch. relay : 5 no. | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-11 10:38 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11215841 | 103789030 | 2023-09-05 16:36 | 2023-09-05 |  | 2023-09-05 14:16 | IH101ZWIFI | IH101ZWIFI | IH101ZWIFI |  | Wiser installation Phase 3 for HT Automation Gateway IH101ZWIFI - Qty--1 pc 4 Channel Automation Relay-IH14000100 - Qty--5 pcs Installation support VIPIN KAUSHIK 9818561421 | 2023-09-05 | 2023-09-05 22:58 | No | Commercial Action - Sales | VIPIN KAUSHIK | 12/D4 Hindustan Times Apartments, Shashi Park Rd, Mayur Vihar | Delhi | 110091 | Delhi | India FS ED&I CSP North Team Seamtek International Pvt. Ltd. GHAZIABAD | Satish Raika Seamtek International Pvt. Ltd. GHAZIABAD | Seamtek International Pvt. Ltd. | following wiser components has been installed gateway: 1no 4 channel relay :5 no | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-05 22:58 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11215944 | 103790069 | 2023-09-05 16:31 | 2023-09-05 |  | 2023-09-05 14:44 | IH101ZWIFI | IH101ZWIFI | IH101ZWIFI |  | Wiser installation Phase 3 for HT Automation Gateway IH101ZWIFI - Qty--1 pc 4 Channel Automation Relay-IH14000100 - Qty--5 pcs Installation support RENU KAUSHIK 9999031514 | 2023-09-05 | 2023-09-05 23:02 | No | Commercial Action - Sales | RENU KAUSHIK | 12B/03 Hindustan Times Apartments, Shashi Park Rd, Mayur Vihar | Delhi | 110091 | Delhi | India FS ED&I CSP North Team Seamtek International Pvt. Ltd. GHAZIABAD | Satish Raika Seamtek International Pvt. Ltd. GHAZIABAD | Seamtek International Pvt. Ltd. | following wiser components has been installed gateway: 1no 4 channel relay :5 no | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-11 11:04 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11215972 | 103790474 | 2023-09-05 16:44 | 2023-09-06 |  | 2023-09-05 14:53 | IH101ZWIFI | IH101ZWIFI | IH101ZWIFI |  | Wiser installation Phase 3 for HT Automation Gateway IH101ZWIFI - Qty--1 pc 4 Channel Automation Relay-IH14000100 - Qty--5 pcs Installation support RAKESH NARAYANA MATHUR 9871050405 | 2023-09-05 | 2023-09-06 10:39 | No | Commercial Action - Sales | RAKESH NARAYANA MATHUR | 15 A/1 Hindustan Times Apartments | Delhi | 110091 | Delhi | India FS ED&I CSP North Team Seamtek International Pvt. Ltd. GHAZIABAD | Satish Raika Seamtek International Pvt. Ltd. GHAZIABAD | Seamtek International Pvt. Ltd. | following components has been installed : gateway: 1no 4 ch. relay : 5 no. | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-11 10:40 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11216002 | 103790814 | 2023-09-05 16:13 | 2023-09-05 |  | 2023-09-05 15:03 | IH101ZWIFI | IH101ZWIFI | IH101ZWIFI |  | Wiser installation Phase 3 for HT Automation Gateway IH101ZWIFI - Qty--1 pc 4 Channel Automation Relay-IH14000100 - Qty--5 pcs Installation support MAYANK JOSHI 9560449920 | 2023-09-05 | 2023-09-06 00:30 | No | Commercial Action - Sales | MAYANK JOSHI | 10 C/1 Hindustan Times Apartments | Delhi | 110091 | Delhi | India FS ED&I CSP North Team Seamtek International Pvt. Ltd. GHAZIABAD | Satish Raika Seamtek International Pvt. Ltd. GHAZIABAD | Seamtek International Pvt. Ltd. | following wiser copnents has been installed gateway: 1 no 4 ch. relay: 5 no | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-07 15:23 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11216112 | 103784850 | 2023-09-05 17:00 | 2023-09-05 |  | 2023-09-05 15:58 | X1001WH_N | X1001WH_N | X1001WH_N |  | Sir / Madam Have been getting repeated defects in Opal range of switches. Hope you understand my concern & replace the defective product's. Thanks & Regards Manjunath 9845092750 On Thu, 11 Mar, 2021, 2:14 pm Deepak Ram Varanashi, <deepak.varanashi@se.com> wrote: Dear customer care Team Please look into the below case and do the needful. Regards Deepakram From: GLOWING LIGHTS <glowinglightsblr@gmail.com> Sent: Tuesday, March 9, 2021 1:58 PMTo: Deepak Ram Varanashi <deepak.varanashi@se.com>Subject: Opal range Defective [External email: Use caution with links and attachments] Sir I have purchased Opal range of switches for my residence & the switches are frequently popping out & had got replaced a couple of times & there seems to be manufacturing defects & still in date i am facing same issues. Request you to check & do the needful. Thanks & Regards Manjunath 9845092750 ______________________________________________________________________This email has been scanned by the Symantec Email Security.cloud service.______________________________________________________________________ | 2023-09-05 | 2023-09-06 16:39 | No | Warranty | Majunath Majunath | Number 73 2nd Stage 3rd cross Oklipuram Bangalore 560021 | Bangalore | 560021 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Chethan SC P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | Inspected and found below mentioned 1)Ref: X100WH S/N:152851 = 3 No'S switches Switches was not working and after switches replaced and fixed and tested working found ok. Hence we have replaced new good warranty replacement from our PSK stock. Defective taken back to our ASC. | Repair |  | 9- Service Validated | 2023-09-06 16:40 |  |  | 8 | INR | 8 | ENM HOME DISTRIBUTION
WO-11216266 | 103794780 | 2023-09-06 10:45 | 2023-09-05 |  | 2023-09-05 17:10 | A9N4P63C | A9N4P63C | A9N4P63C | D2040. | complaint number required Dear Team, M/S Shri Ambey Engineering ID/100 NIT Faridabad Haryana. Mr.Jitender Kaushik 9811677616 Product : A9N4P63C Serial Number : D2215 Phase missing -- *WITH REGARDS-* Sarabjit Singh | 2023-09-05 | 2023-09-06 10:47 | No | Warranty | Shri Ambey Engineering | 1D/100, NIT | Faridabad | 121001 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | checked the mcb found thread faulty and coil found short. Hence faulty, replaced. A9N4P63C - 1 Nos. LAEX4F7 - 1 Nos. Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-08 15:46 | Please ignore LAEX4F7 contactor coil in this zvo order. Coil replacement done by distributor stock and distributor would register new case for full contactor with coil from his end. |  | 45 | INR | 45 | ENM HOME DISTRIBUTION
WO-11216299 | 103795171 | 2023-09-07 13:31 | 2023-09-05 |  | 2023-09-05 17:28 | E8315_16_WG | E8315_16_WG | E8315_16_WG |  | Gaurav 203 Adarshnagar Jalandhar Back side of Kanta churi resturant 144001 Punjab chadamobilehouse@gmail.com 2 not worling | 2023-09-05 | 2023-09-16 16:41 | No | Warranty | Gaurav Kumar | 203 Adarshnagar Jalandhar Back side of Kanta churi resturant | Jalandhar | 144001 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the USB switches found not giving output. Hence faulty, replaced. E8332USB_WD_G8 - 2 Nos. E8332USB_WG_G8 - 1 Nos. email : id not provided by the customer. | Repair |  | 8- Service Completed | 2023-09-16 16:44 |  |  | 65 | INR | 65 | ENM HOME DISTRIBUTION
WO-11216340 | 103793041 | 2023-09-06 11:18 | 2023-09-05 |  | 2023-09-05 17:49 | P1002_N | P1002_N | P1002_N |  | COMPLAINT SAIFU MK 1 Name of Customer SAIFU MK 2 Site Address MELE PARASSERI PERUVALLUR PO PARAMBIL PEEDIKA MALAPPURAM - 676315 3 Name of Contact Person at Site SAIFU MK 4 Contact Phone / Mob. No: 8592866034 5 Defective Product Details P1002 - 2 PCS P1181 - 2 PCS 6 Nature of Defect Not working 7 Shutdown availability if applicable Yes 8 Warranty Status Under Warranty 9 Commissioned / Installed date Before Three Months 10 Serial No: or DOM of the Product 11 Name & Phone No: of Person Registering the Complaint LAN Marketing 8075581561 | 2023-09-05 | 2023-09-06 21:24 | No | Warranty | SAIFU MK MK | MELE PARASSERI PERUVALLUR PO PARAMBIL PEEDIKA | MALAPPURAM | 676315 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found livia two way swiitch 16ah switch not working and db door lock compalint. P1002 1 NOS replaced db door lock replaced problem solved | Repair |  | 9- Service Validated | 2023-09-07 21:30 |  |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11221358 | 103814302 | 2023-09-07 10:41 | 2023-09-06 |  | 2023-09-06 12:47 | A9N3P63C | A9N3P63C | A9N3P63C |  | Re: 3 POLE 63A MCB COMPLAINT [ thread::Id3b2zeVe0eNQCxm7ZcKuz4:: ] Schneider mcb 3 pole 63a (2pc) .This mcb is not working, It's having an internal problem.Please solve this issue. DETAILS ARE GIVEN BELOW - NAME : RUPINDER SINGH (9779121953) ADDRESS : M/S SHIV ELECTRIC STORE OPP. UPPER INDIA STEEL, GURU NANAK MARKET, NEAR GIASPURA RAILWAY CROSSING, FOCAL POINT, LUDHIANA-141010 | 2023-09-06 | 2023-09-07 10:43 | No | Warranty | SHIV ELECTRIC STORE | Opposite Upper India Steels,Near Giaspura railway Crossing | LUDHIANA | 141010 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | checked the mcb found screw thread faulty, replaced. A9N3P63C - 1 Nos. Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-07 13:23 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11034998 | 102804860 | 2023-07-27 11:04 | 2023-07-26 |  | 2023-07-26 12:51 | IH14000100 | IH14000100 | IH14000100 |  | DOP: 22/7/2023 Smart Doorbell 4 Channel Automation Relay Curtain Controller Automation Gateway Wiser IR Controller Flush/Surface Mount Single-Load 360 degree PIR Flush Mount Dual Load 360 degree sensor 2 Channel Dimmer Controller Ebenezer E7A, Shresta Emerald Apartments, 4th Avenue, MICO Colony, Besant Nagar, Chennai - 600090 Pavithran ebenezer@orangeretailfinance.com 9566507360 | 2023-07-26 | 2023-09-09 11:49 | No | Commercial Action - Sales | Ebenezer Ebenezer | E7A, Shresta Emerald Apartments, 4th Avenue, MICO Colony, Besant Nagar, | Chennai | 600090 | Tamil Nadu | India FS South2 ED&I CSP UpservePowerSystems Chennai | HARI PRASATH UpservePowerSystems Chennai | Upserve Power Systems | installation completed working fine IH14000100-20 nos IH101ZWIFI -1 nos IH101ZWZIR - 5nos | Commissioning & Installation | Start-up | 8- Service Completed | 2023-09-09 11:56 |  |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-11221437 | 103818281 | 2023-09-06 13:35 | 2023-09-06 |  | 2023-09-06 13:20 | IN8401_16_BZ | IN8401_16_BZ | IN8401_16_BZ |  | Fwd: WO-11140544 from Schneider Electric Complaint in Zencelo Switches Dear Team, Please find the below mail. Please login a new complaint. Because some more switches have problem. | 2023-09-06 | 2023-09-13 13:57 | No | Warranty | Ram Sharma | G-1502, La Lagune Apartment Sector 54 Golf course road | Gurgaon | 122001 | Haryana | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the switches and found switches have stuck issue, We replace the faulty switches with new. | Repair |  | 9- Service Validated | 2023-09-13 13:57 |  |  | 54 | INR | 54 | ENM HOME DISTRIBUTION
WO-11221497 | 103813300 | 2023-09-07 13:16 | 2023-09-06 |  | 2023-09-06 13:43 | UNS61SW1M_GY | UNS61SW1M_GY | UNS61SW1M_GY |  | Dear Sir, "Greeting From Eco Power Solution" Please Attend the following complaint. Name :- JASKIRAT SINGH Address :- H.N.1 partap colony, Nai Abadhi khanna Punjab, 141401 Contact number :- 98883 53091 Contact number :- Complaint :- 1 ) UNS61SW1M_GY - 15 pcs 2) UNS6SK3P2MNS_GY - 5 pcs 3) UNS62SW1M_GY - 5 pcs 4) UNS616SK2M_GY - 5 pcs. Problem :- This item is not working properly. Kindly attend the complaint on priority basis. Attached Sale invoice Invoice Date 07-04-23 Thanks & Regards ASHISH KUMAR ECO POWER SOLUTIONS (Sister Concern of M/s Automation Systems Ludhiana) Cabin No. 1, 90-C, Shakti Enclave Near Toor Complex, Dugri Road Ludhiana-141002 PUNJAB Virus-free.www.avast.com | 2023-09-06 | 2023-09-07 13:18 | No | Warranty | JASKIRAT SINGH | H.N.1 partap colony, Nai Abadhi khanna | Ludhiana | 141401 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | checked the switches found working ok. Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-07 13:21 |  |  | 45 | INR | 45 | ENM HOME DISTRIBUTION
WO-11221633 | 103818088 | 2023-09-07 13:00 | 2023-09-06 |  | 2023-09-06 14:07 | IH14000100 | IH14000100 | IH14000100 |  | RE: Fw: 8 Relays not working- Mr. Mobeen / Mr. Prince, jalandhar [ ] [ thread::OakT7Z_LdYuNRvwl3F2tKj4:: ] As per customer, automation not working at site properly. It is not operateable by mobile and alexa. Kindly schedule a technician visit at site. Some of the relays gets disconnected from gateway, it is not responding. 1. Customer Name : Mr. Deepak (mànager) 2. Customer Address : House Number 392, Lajpat Nagar, Jalandhar, Near mama's pride school, punjab- 144022 3. Installation Type : Done 4. Product : A) Wiser Home Automation Gateway installed: 05 Relay 4 channel : 08 Nos 5. Contact Number : +91 99886 29292, 8360361651 6. Site Status: Ready | 2023-09-06 | 2023-09-07 13:05 | No | Warranty | Deepak Deepak | House Number 392, Lajpat Nagar, Jalandhar, Near mama's pride school, | Jalandhar | 144022 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the gateway relay (IH101ZWIFI) found working properly. Relay srn :- > 011130150 > 011131136 > 011131155 email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-07 13:13 |  |  | 65 | INR | 65 | ENM HOME DISTRIBUTION
WO-11221655 | 103818586 | 2023-09-07 10:13 | 2023-09-06 |  | 2023-09-06 14:15 | UNS61SW1M_WE | UNS61SW1M_WE | UNS61SW1M_WE |  | Hi, Name of Customer Abdul Rahman Site Address Al-Badar Manzil, Kalanad (p o ) Kalanad ,pincode - 671317 Kasaragod Name of contact person at site Abdul Rahman Contact Phone / Mob. No: 9567422422 Defective product details Unica Pure 6AX 1WAY SWITCH Nature of Defect Customer is facing issues with Unica Pure 6ax 1WAY SWITCH Shutdown availability if applicable Warranty status Under Warranty Commissioned / Installed date One month Serial No: or DOM of the product PFA, complaint registration details for a newly installed site for Unica switch Please send a technician to this site as soon as possible. Thanks & Regards, MJ Marketing 33/480, AM Building, Railway Station Road, Near Keloth Juma Masjid, Keloth, Payyanur - 670307 PH : 04985 209896, 9188 209896 Email : contact@mjmarketing.in "We know you have many choices in doing business and we THANK YOU for choosing us!" | 2023-09-06 | 2023-09-18 13:28 | No | Warranty | Abdul Rahman | Al-Badar Manzil, Kalanad (p o ) Kalanad | KASARGOD | 671317 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found unica one way and two switchs contact issue and abnormality sound comeing. unica one way 40nos unica two way 30nos replacement booked, replacement material received , but customer not available. | Repair |  | 9- Service Validated | 2023-09-21 13:36 |  |  | 130 | INR | 130 | ENM HOME DISTRIBUTION
WO-11221734 | 103817796 | 2023-09-06 16:42 | 2023-09-06 |  | 2023-09-06 14:43 | IN8401/16(BZ)-A | IN8401/16(BZ)-A | IN8401/16(BZ)-A |  | Hai Team Please find the below attached file for complaint registration and request to register Thanking you Regards M.Yagappa 9666278687 | 2023-09-06 | 2023-09-08 13:33 | No | Warranty | Hanumanth Reddy | Plot no-7,srinivasa nagar coluony Kapra,ECIL post | HYDERABAD | 500062 | Telangana | India FS ED&I CSP South Team Master Electrical Solutions Hyderabad | DEBANGSHU BOSE Master Electrical Solutions SECUNDERABAD | Master Electrical Solutions | visited the site and carried out the following job. During visit customer have Zencello in8401(BZ) model switch ,which indication is not properly showing. And customer required In8481 BZ LED indication. So switched is ok .so we closed the complaint | Repair |  | 9- Service Validated | 2023-09-08 13:38 |  |  | 10 | INR | 10 | ENM HOME DISTRIBUTION
WO-11221781 | 103821782 | 2023-09-07 11:25 | 2023-09-06 | DB B Phase output not show | 2023-09-06 14:59 | A9HVD08H | A9HVD08H | A9HVD08H |  | A9HVD08H Not working | 2023-09-06 | 2023-09-08 15:36 | No | Warranty | Hamid Khan | 7th floor Banre one bulding Baner | Pune | 411045 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Samadhan S_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the DB B Phase output not show . DB found in installed condition. DB incomer MCCB found ok. we observed Busbar section output connection B phase link not show. removed cover and checked connection hardware found loose. so we tight proper and then taken operation found ok. | Repair |  | 9- Service Validated | 2023-09-08 15:44 |  |  | 40 | INR | 40 | ENM HOME DISTRIBUTION
WO-11222001 | 103820278 | 2023-09-06 18:50 | 2023-09-06 |  | 2023-09-06 16:58 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Hi team, IH100WFVDP Manjunath Phone number : 9900065440 No. 7 and 8 Sy,No 79/4 1st and 2nd floor 4th cross , Doddamma Industrial Area, Bannerghatta Road, Hulimalvu Bangalore 560076 Please find the invoice for the same . Warm Regards Ramakanth Kumathe Lighting Controls Home and DistributionSchneider Electric M +91 80073 65462E ramakanth.kumathe@se.com Bearys Global Research Traingle 63/3B, Whitefield Ashram Road Govigere Village, Bidarahalli Hobli Bangalore - 560067 India Now Raise Wiser Installation or troublshoot through chat https://www.se.com/in/en/work/support/customer-care/contact-schneider-electric.jsp *Please consider the environment before printing this e-mail Internal From: Neel MS <neel.ms@non.se.com> Sent: Wednesday, September 6, 2023 1:23 PM To: SM APA Customercare IN <Customercare.IN@schneider-electric.com> Cc: Ramakanth Kumathe <Ramakanth.Kumathe@se.com> Subject: Installation For Smart Door Bell Hi, Please initiate the work order for Smart Door Bell For client Manjunath. @Ramakanth Kumathe Please attach the Invoice please. Regards Neel MS Senior Sales AssociateHome & Distribution DivisionSchneider Electric M 98861840484MS TEAMS neel.ms@non.se.comE neel.ms@non.se.comCustomer Support Contact Us Schneider Electric India Pvt Limited3, 1, Millers Rd, Vasanth NagarBengaluru560051India Internal | 2023-09-06 | 2023-09-25 16:33 | No | Commercial Action - Service Ops | Manjunath K | No. 7 and 8 Sy,No 79/4 1st and 2nd floor 4th cross , Doddamma Industrial Area, Bannerghatta Road, Hulimalvu | Bangalore | 560076 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Mohammad Riyaz_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | i had visited the site and installed wiser doorbell, after installation checked found working ok thru app and manually, the same shown to the customer. - IH100WFVDP-1nos | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-25 19:41 |  |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11222026 | 103823149 | 2023-09-08 12:35 | 2023-09-06 |  | 2023-09-06 17:05 | A9N4P63D | A9N4P63D | A9N4P63D |  | Re: 63A FP MCB IS NOT WORKING [ thread::nPc1Ti-UcK21lZ7aSHFIeD4:: ] We have purchased 63A FP MCB D CURVE (A9N4P63D) from your dealer in Faridabad. One pole is not working, please send your engineer to resolve the issue. Dealer - Shree Nath Enterprises Faridabad Invoice - 645 Dt. 4.8.23 Site Address :- APG Engineers and Consultant 14/7 Parmeshwar Colony Behind DP Door Sector 31 faridabad Thanks & Regards!! Pranjal Gupta +91 - 9811676469 | 2023-09-06 | 2023-09-12 15:44 | No | Warranty | APG Engineers And Consultant | 14/7, Parmeshwar Colony, Behind D.P. Door, Sector - 28, Metro Station, | Faridabad | 121008 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | checked the mcb found phase missing. hence faulty, replaced A9N4P63D - 1 Nos. Email ; id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-12 15:46 |  |  | 52 | INR | 52 | ENM HOME DISTRIBUTION
WO-11222040 | 103822896 | 2023-09-07 15:56 | 2023-09-06 |  | 2023-09-06 17:13 | A9N1P63C | A9N1P63C | A9N1P63C |  | Dear Sir/Ma?am, Good Afternoon!! Please find the attachment and arrange the service engg asap. And also need RCA for same. Name of Customer DELTA ELCTRONICS INDIA PVT LTD Site Address PLOT NO 15 SEC-33 INFOCITY 2 NEAR BY HERO HONDA CHOWK GURUGRAM 122003 Name of contact person at site Chaman Ranga -9212796973 Contact Phone / Mob. No: 9910015705 Defective product details A9N1P63C=01, A9N4P63C=04 Nature of Defect Countinuity Isuue Shutdown availability if applicable Warranty status 1 YEAR Distributor Name,Invoice # & Date ELECTRICAL CONTROL SYSTEMS, INV N0- 9008653834 dt. 24/07/23, 9008684060 dt. 21/08/23 Serial No: or DOM of the product Name & phone No: of person registering the complaint Ashish Malik : 9910015705 Thanks & Best Regards Ashish Malik Second floor, Plot No-14-15 Sec-33,Opposite Info City 2, Gurgaon-122001 Tel. no:- 0124-2226666, +91-9910015705 | 2023-09-06 | 2023-09-07 15:58 | No | Warranty | Delta Elctronics India Pvt Ltd | Plot No 15 Sec-33 Infocity 2 Near By Hero Honda Chowk | Gurgaon | 122003 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | checked the mcb found phase missing, Hence faulty, replaced. A9N4P63C - 1 Nos. Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-08 10:22 |  |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11038775 | 102824744 | 2023-07-27 13:37 | 2023-07-27 |  | 2023-07-27 09:54 | UNS6BPL2M_GY | UNS6BPL2M_GY | UNS6BPL2M_GY |  | DOP: 8/10/2022 UNS6BPL2M_GY Qty:1 P: Not Working Jerry huduson Kurisunkal Mararikulam North po 688523 Alapuzha suresh 9061646563, 9526082492 | 2023-07-27 | 2023-09-14 15:29 | No | Warranty | Suresh Suresh | Jerry huduson Kurisunkal Mararikulam North po | Alappuzha | 688523 | Kerala | India FS South2 ED&I CSP PrinterPeople Cochin | Renjith PR PrinterPeople Cochin | PRINTER PEOPLE-COCHIN | bell push fault. onsite done.. replacement received. send to alapuzha eng. tried to contact cust.. cust phone incoming not available. information send to customer as mesaage. will do onsite on gettting call back | Repair |  | 9- Service Validated | 2023-09-14 15:33 |  |  | 56 | INR | 56 | ENM HOME DISTRIBUTION
WO-11222105 | 103826396 | 2023-09-07 16:21 | 2023-09-06 |  | 2023-09-06 17:43 | UNS4STFAN1M_GY | UNS4STFAN1M_GY | UNS4STFAN1M_GY |  | Unica Pure 1 MOD 4 Step mo HSN8414 UNS4STFAN1M_GY INVOICE DATE 12 MAY 2022 55/a Anandvihar colony , outside bhandari gate batala, Gurdaspur Punjab 143505 Sham Lal 8847085205 | 2023-09-06 | 2023-09-14 17:08 | No | Warranty | Sham Lal | 55/a Anandvihar colony , outside bhandari gate batala | Gurdaspur | 143505 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the fan regulator found speed variation issue. Hence faulty replaced. UNS4STFAN1M_GY - 1 Nos. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-14 17:21 |  |  | 2 | INR | 2 | ENM HOME DISTRIBUTION
WO-11222129 | 103824885 | 2023-09-07 10:53 | 2023-09-06 |  | 2023-09-06 17:58 | A9N4P50C | A9N4P50C | A9N4P50C |  | Dear Sir, Complaint received from the ACCURATE INDUSTRIAL CONTROLS PVT.LTD. Saying MCB A9N4P50C- 1 Qty has an issue MCB dolly not operating. SO.NO. - 300773624 Site address- NDRF Camp Raispur Village, Ghaziabad, Uttar Pradesh, 201002) for G20 Summit. Contact Person- Mr.Shubham Thorat (9325928114) Please find the attached our Invoice. ?Invoice date 15 June 2023 Thanks & Regards, Mohini Bali 8805008503 A B Controls / Simply Electrifying Pvt. Ltd. 201 Varsha Avenue, 104 Anand Park Aundh, Pune 411007 Tel : +91- 20- 25890010 / 25890030 Tollfree : +91 - 1800 233 4333 Please do visit us at www.simply-electrifying.com | 2023-09-06 | 2023-09-12 15:52 | No | Warranty | Shubham Thorat | NDRF Camp, Raispur Village | Ghaziabad | 201002 | Uttar Pradesh | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mcb found dolly free, Hence faulty replaced A9N4P50C - 1 nos Email : | Repair |  | 9- Service Validated | 2023-09-12 15:54 |  |  | 52 | INR | 52 | ENM HOME DISTRIBUTION
WO-11222160 | 103824529 | 2023-09-08 10:33 | 2023-09-06 |  | 2023-09-06 18:13 | IN8401_16 | IN8401_16 | IN8401_16 |  | Hi Team , There is a Zencelo Model 6A Switch (IN8401) Which is not working . Please find the attached invoice file and visit the below mention address and give the solution . Customer Name : Nirmal Jain Mb No.- 9711442717 Zencelo Model 6A Switch (IN8401) : 6Pcs Address- B-137, Surajmal Vihar, Delhi-92, (110092) Thanks & Regards Zarrar Ahamad Manager - Sales, NCR Home and Distribution DivisionSchneider Electric Location: Gurgaon Landline: +91 124 6899000Mobile: +91 9990728046 Email: zarrar.ahamad@se.comCustomer Care 18001030011/ 18004254272 9th Floor, Building 10 CDLF Cyber City, Phase II Gurgaon - 122002INDIA Download mySchneider app 24/7 support. Mobile catalog. Access to expert help. Internal Internal | 2023-09-06 | 2023-09-13 15:45 | No | Warranty | Nirmal Jain | B-137, Surajmal Vihar | Delhi | 110092 | Delhi | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the switches and found switches have stuck issue, We replace the faulty switches with new. | Repair |  | 9- Service Validated | 2023-09-13 18:05 |  |  | 12 | INR | 12 | ENM HOME DISTRIBUTION
WO-11224388 | 103847444 | 2023-09-07 12:10 | 2023-09-07 |  | 2023-09-07 11:11 | P2106_N | P2106_N | P2106_N |  | Complaint no. reqd. A/c Kavi Dutt Dear Team Please issue Complaint No. Kavi Dutt Nirankari bhawan Village garshankar ,District - Hoshiarpur Mr.Kavi dutt ji Nirankari 9815693678 Product : P2106_N ,(Livia socket) Invoice dt. : 23/1/2023 Not Working properly with Shutters | 2023-09-07 | 2023-09-07 12:12 | No | Warranty | Kavi Dutt | Nirankari bhawan Village - garshankar | Hoshiarpur | 144527 | Punjab | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Karnail Singh Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the socket found working properly. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-07 14:38 |  |  | 145 | INR | 145 | ENM HOME DISTRIBUTION
WO-11224805 | 103727806 | 2023-09-11 11:22 | 2023-09-07 |  | 2023-09-07 14:14 | X1001WH_N | X1001WH_N | X1001WH_N |  | Poor quality of the Electric Switch which threat to human life and Electrical Equipments Considering safety concern WO created I am Abdulla Bin Ahamed, residing at the above addressed Apartment. In this Apartment, the electrical Switches are supplied by Schneider Electrical. Even though the project was commissioned during the year 2015, but I started living in the Apartment a year back. Since then the electrical switches manufactured and supplied by you are giving problems. Between January 2022 - March 2022, my electrical and electronic equipments worth Rs 3.50 Lakhs got damaged due to malfunctioning of the switches. This was reported to your Cochin Office and they arranged replacement of 8 or 9 switches. But the issue is still continuing. The quality of the Switches are poor and they break very quickly. Now switches are becoming a threat to human life as well. One of the pictures is enclosed. 1: Total Number of one way / normal switches - 86 Nos 2: Total Number of Two way switches - 18 Nos. Abdulla Bin Ahamed 9A, Sreerosh Midtown Apartment Thalikkavu, Kannur 670 001, Kerala. Mob : 97460 30571 | 2023-09-07 | 2023-09-11 22:08 | No | Warranty | Abdulla Bin Ahamed Abdulla Bin Ahamed | 9A, Sreerosh Midtown Apartment Thalikkavu, null | Kannur | 670001 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Rejilesh APSMarketingCompany Calicut | APS Marketing Company | visited this customer site and found the complaint of opela switches ( 2012 batch) dolly crack issue.customer demanded that he wanted all his switches to be changed even though there is only 43 switches to be fixed but as per our policy the warranty is already finished.same inform to dealer. X1001 78NOS X1002 22NOS X1181 11NOS AAKX1232 7NOS | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-11 22:22 |  |  | 100 | INR | 100 | ENM HOME DISTRIBUTION
WO-11224868 | 103854839 | 2023-09-07 15:25 | 2023-09-07 |  | 2023-09-07 14:36 | IH14000100 | IH14000100 | IH14000100 |  | Wiser complaint There is a wiser complaint in below address Regards Sherine beegum nazeer Medical college Trivandrum 695011 8086222277 Invoice attached | 2023-09-07 | 2023-09-07 17:46 | No | Warranty | Sherine beegam Nazeer | Medical College | Thiruvananthapuram | 695614 | Kerala | India FS South2 ED&I CSP PrinterPeople Cochin | Renjith PR PrinterPeople Cochin | PRINTER PEOPLE-COCHIN | Gateway reset done. Installed in cust phone. Configuration done. | Repair |  | 9- Service Validated | 2023-09-07 17:46 |  |  | 220 | INR | 220 | ENM HOME DISTRIBUTION
WO-11225044 | 103856829 | 2023-09-08 10:21 | 2023-09-08 |  | 2023-09-07 15:36 | A9KR11225 | A9KR11225 | A9KR11225 |  | Customer complaint-Schneider Make RCCB 4P/25Amp defective. Dear team , Complaint reported from ICF-Chennai, regarding defective RCCB. During the operation observed manually test trip not working as well as during short-circuit RCCB not getting trip. Request you kindly log the complaint and provide urgent replacement at below mentioned address. since unit is hold in our account due to non availability of the said item. Address details:- HIND RECTIFIERS LTD NO.403,4TH FLOOR, C BLOCK, SHIVALAYA BUILDING, ETHIRAJ SALAIEGMORE, CHENNAI-600008 CONT NO -MR. SATISH KUMAR Mob:-8939899307 | 2023-09-07 | 2023-09-12 09:30 | No | Warranty | Hind rectifiers Ltd | NO:403, 4th FLOOR, C - BLOCK,, SHIVALAYA BUILDING, Ethiraj Salai, Egmore | Chennai | 600008 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Visited Done | Repair |  | 9- Service Validated | 2023-09-12 14:42 |  |  | 23 | INR | 23 | ENM HOME DISTRIBUTION
WO-11225127 | 103856093 | 2023-09-11 10:58 | 2023-09-07 | NA | 2023-09-07 16:25 | E8334L2_WG | E8334L2_WG | E8334L2_WG |  | Problem with Avatar-on Please arrange to send the service personnel at the following site : Mr, Nilesh Sonthalia Swarnamani near - Bengal Chamical Bus stop Zarina 3ZA Kolkata-700054 M- 98300-77963 | 2023-09-07 | 2023-09-13 15:15 | No | Warranty | Nilesh Sonthalia | Swarnamani,Near Bengal Chamical Bus stop Zarina 3ZA | Kolkata | 700054 | West Bengal | India FS ED&I CSP East Team B.D Electroservices Kolkata | KOUSHIK MONDAL_B.D Electroservices Kolkata | B.D Electroservices(500017330) | On received of ZVO material will deliveded to customer. | Repair |  | 9- Service Validated | 2023-09-13 17:34 |  |  | 22 | INR | 22 | ENM HOME DISTRIBUTION
WO-11225234 | 103860514 | 2023-09-08 11:16 | 2023-09-07 |  | 2023-09-07 17:10 | P3200_N | P3200_N | P3200_N |  | COMPLAINT SOUJATH AV KAINATTY 1 Name of Customer SOUJATH A V 2 Site Address ASY'S KALLARAKKAL HOUSE MUTTUNGAL WEST (PO), MEETHALANGADI ROAD NEAR KADAPPURAM PALLI, KAINATTY KOZHIKODE - 673106 3 Name of Contact Person at Site SOUJATH A V 4 Contact Phone / Mob. No: 9048041263 5 Defective Product Details P3200 : 2 PCS 6 Nature of Defect Not Working 7 Shutdown availability if applicable Yes 8 Warranty Status Under Warranty 9 Commissioned / Installed date Before Three Months 10 Serial No: or DOM of the Product 11 Name & Phone No: of Person Registering the Complaint LAN Marketing 8075581561 | 2023-09-07 | 2023-09-08 17:00 | No | Warranty | SOUJATH A V | ASY'S KALLARAKKAL HOUSE MUTTUNGAL WEST (PO), MEETHALANGADI ROAD NEAR KADAPPURAM PALLI, KAINATTY | KOZHIKODE | 673106 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Rejilesh APSMarketingCompany Calicut | APS Marketing Company | visited this site found livia switchs struck issue, switchs clean done , its working fine and fan regulater speed issue P3200 replaced | Repair |  | 9- Service Validated | 2023-09-08 17:03 |  |  | 60 | INR | 60 | ENM HOME DISTRIBUTION
WO-11225418 | 103862955 | 2023-09-08 10:29 | 2023-09-07 |  | 2023-09-07 18:19 | X1181WH_N | X1181WH_N | X1181WH_N |  | Complaint Register- Liji Nair RDS 1 Name of Customer Liji Nair 2 Site Address 9A RDS Aura, KP Vallon Road, Girinagar with pincode Kadavanthra,Kochi Kerala-682020 3 Name of contact person at site Liji 4 Contact Phone / Mob. No: 9769079972 5 Defective product details X1181WH-10 Nos, X3200WH-5 nos 6 Nature of Defect Complaint 7 Shutdown availability if applicable 8 Distributor Name,Invoice # & Date 9008297071 9 Serial No: or DOM of the product 10 Name & phone No: of person registering the complaint | 2023-09-07 | 2023-09-07 10:02 | No | Warranty | Liji Nair | RDS Aura Flat no.9A, K P Vallon Road Kadavanthra Ernakulam, Kerala | Ernakulam | 682020 | Kerala | India FS South2 ED&I CSP PrinterPeople Cochin | Renjith PrinterPeople Cochin | PRINTER PEOPLE-COCHIN | serial no out of warranty.. invoice nor provided.. | Repair |  | 8- Service Completed | 2023-09-13 10:03 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11228800 | 103879126 | 2023-09-08 13:40 | 2023-09-08 |  | 2023-09-08 10:43 | X1001WH_N | X1001WH_N | X1001WH_N |  | opeal switches 15 to 17 switches are not working. 1101 NCC limted Madhavpur Inorbit mall road Hydrabad Telanegan 500081 Nagesh 8008552817 ho.bms@nccltd.in invoice date : 19 may 23 d0612/23 24 | 2023-09-08 | 2023-09-15 10:06 | No | Warranty | NCC Ltd. | NCC ltd. Madhavpur Inorbit mall road null | Hyderabad | 500081 | Telangana | India FS ED&I CSP South Team Master Electrical Solutions Hyderabad | DEBANGSHU BOSE Master Electrical Solutions SECUNDERABAD | Master Electrical Solutions | IN OUR FIRST VISIT WE WENT AND TAKEN THE QUANTITY OF SWITCHES .SO HW DONE THE ORDER AFTER RECEIVED THE MATERIAL WE REPLACED THE MATERIAL . | Repair |  | 9- Service Validated | 2023-09-15 10:06 | Dear Devendra ji, Kindly unblock below reference for booking as it in blocked status.,, And we also have stock in the DC X2007WH Kindly do the needful |  | 20 | INR | 20 | ENM HOME DISTRIBUTION
WO-11229180 | 103879173 | 2023-09-08 11:49 | 2023-09-08 | VDP not working | 2023-09-08 11:28 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Dear Team, Please arrange a technician for Service of Following Components at below Location: Product to be Serviced: Wiser Smart Doorbell ( IH100WFVDP ) ?> Quantity = 1. Project Name: V-Uptown by Tatvam ConstructionsLocation: Ravet Kiwale Link Road, Kiwale Pune Near Jai Ganesh Lawns, Pimpri Chinchwad 412101.Contact: Mrs. Pallavi Sajne ? 9075967490. Invoice Date : 16 nov 2022 Invoice number : P05080/22-23 Note: Please check Invoice & Break Fix check list attached with this mail. Thanks & Regards, Hrushikesh JadhavSenior Executive-Sales Connected Living Wiser Business Home & Distribution DivisionSchneider Electric M - +91 8928528885Customer Care - 1800-103-0011E - hrushikesh.jadhav@non.se.com Schneider Electric India Pvt Ltd Amar Calibre ,CTS no 911, BMCC Road. Off. FC Road.PUNE -411004 INDIA Internal Internal | 2023-09-08 | 2023-09-08 12:39 | No | Warranty | Pallavi Sajne | V-Uptown by Tatvam Constructions Ravet Kiwale Link Road,Near Jai Ganesh Lawns, Pimpri Chinchwad | Pune | 412101 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Kunal jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the Doorbell - 01 nos not working . VDP not showing SD card again. so we removed SD card and fitted again, but problem is not repairable, So Problem observed in VDP. Required Material : IH100WFVDP - 01 nos. We arranged from our stock and replaced it. | Repair |  | 9- Service Validated | 2023-09-08 15:28 | =S= Consig Fill up 226038724 |  | 40 | INR | 40 | ENM HOME DISTRIBUTION
WO-11229247 | 103837454 | 2023-09-09 13:26 | 2023-09-08 |  | 2023-09-08 11:56 | X1001WH_N | X1001WH_N | X1001WH_N |  | Re: Regarding switches [ thread::4EZfDXeFfQOVPQKGEdTQ2T4:: ] I bought switches but they r of no use same problem. Ultra low quality switches. I think I have to made my mind to remove the schneider switches with the local ones. If u cannot provide good switches with faith in ur company then how can I tell people to use schnider products.. Opale switch --Inv attached--2022 Dr. Navneet Bhardwaj Rama Hospital Nur pur bedi Teh Shri Anandpur Sahib Distt Roopnagar Punjab 140117 9501812122 | 2023-09-08 | 2023-09-09 13:30 | No | Warranty | Navneet Bhardwaj | Rama Hospital Nurpur bedi Anandpur Sahib Rupnagar Punjab | Nurpur Bedi | 140117 | Punjab | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Ram Ashish Sharma Electric Chandigarh | Sharma Electric works(1003) | checked the switches found cracked and side lock broken. hence faulty, but switches found out of warranty from date code and belongs to 2013 batch code. hence no replacement given to customer. Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-09 13:35 |  |  | 85 | INR | 85 | ENM HOME DISTRIBUTION
WO-11229317 | 103882119 | 2023-09-08 12:58 | 2023-09-08 | Cover plate not getting fix properly | 2023-09-08 12:28 | UNSCP2M_WE | UNSCP2M_WE | UNSCP2M_WE |  | Dear Team, Please find attached order booked in July 23. Material reached at site but on installation front client facing some issue on metal box. Please arrange service engineer visit on 6th Sep 2023,as contractor will also be present. Client have opening on 7 th sep so all switch installation should be done before 1 day. Client name : Dr Pankaj Ingle 70284 42080 Distributor Name : Tirupati electronics & electricals Agency, Cotton Market Rd, near Balaji Mandir Road, Behind indrapuri hotel,jaystambh, Amaravti 444601 | 2023-09-08 | 2023-09-12 16:23 | No | Warranty | Tirupati electronics & electricals Agency | Cotton Market Rd, near Balaji Mandir Road, Behind indrapuri hotel,jaystambh | Amaravti | 444601 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Kunal jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the Cover found that the not getting fix properly.we observed POP and Paint on grid plate So that's why cover plate is not fix it. so we open it and clean the all dust. and fix it properly. No any problem found in our product. | Repair |  | 9- Service Validated | 2023-09-12 16:44 |  |  | 315 | INR | 315 | ENM HOME DISTRIBUTION
WO-11229427 | 103852461 | 2023-09-08 14:11 | 2023-09-08 |  | 2023-09-08 13:13 | METSEEM6436HCL10RS | METSEEM6436HCL10RS | METSEEM6436HCL10RS | 540430053685 | Dear Team,Please reassign this case as earlier it was cancelled.---------- Forwarded message ---------From: Complaints SEW Date: Mon, Sep 4, 2023 at 3:39?PMSubject: Case : 103764348 dt. 4.9.23To: Complaints SEW , SharmaElectric Cc: Ramkaran Yadav , Mukesh Kumar, Rajan SinghDear Sir,KGK Jewellery Manufacturing Pvt LtdE-71, Basement, Gems & Jewellery Zone, EPIPRIICO Ind. Area, Sitapura JaipurMr. Mohit Sharma8386990381Product : METSEEM6436HCL10RS - 2 nosSr. no : 540430053685Display faulty--*WITH REGARDS-*Sarabjit SinghSHARMA ELECTRIC WORKS I CHANDIGARH I ADMIN. AUTH. SERVICE & SPARESDEALER : CROMPTON GREAVES & SCHNEIDER ELECTRIC INDIA*Tele FAX 0172-4629871E MAIL : complaints@sharmaelectricworks.com *Address : PLOT NO. 279, GF, INDUSTRIAL AREA,**PHASE-II, CHANDIGARH-160002 , Website : www.sharmaelectricworks.com**** Please consider the environment before printing this e-mail-- *WITH REGARDS-*Sarabjit SinghSHARMA ELECTRIC WORKS I CHANDIGARH I ADMIN. AUTH. SERVICE & SPARESDEALER : CROMPTON GREAVES & SCHNEIDER ELECTRIC INDIA*Tele FAX 0172-4629871E MAIL : complaints@sharmaelectricworks.com *Address : PLOT NO. 279, GF, INDUSTRIAL AREA,**PHASE-II, CHANDIGARH-160002 , Website : www.sharmaelectricworks.com**** Please consider the environment before printing this e-mail | 2023-09-08 | 2023-09-08 14:18 | No | Warranty | KGK Jewellery Manufacturing Pvt Ltd | E-71, Basement, Gems & Jewellery Zone, EPIP, RIICO Ind. Area, Sitapura | Jaipur | 302022 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | checked the meter found display issue due to parameters not set. set right the same, now working ok. Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-08 14:25 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11229518 | 103883431 | 2023-09-09 12:47 | 2023-09-08 |  | 2023-09-08 13:43 | E8315_6_WD | E8315_6_WD | E8315_6_WD |  | Dear Sir, "Greeting From Eco Power Solution" Please Attend the following complaint. Name :- NARESH BANSAL Address :- H. NO 11, FARM HOUSE LANE SARABHA NAGER, EXT PAKHOWAL ROAD LUDHIANA- 142022 Contact number :- 9876002414 Complaint :- E8315_6_WD Qty 2 PCS. Problem :- This item is not working properly. Kindly attend the complaint on priority basis. Attached sale invoice. Thanks & Regards ASHISH KUMAR ECO POWER SOLUTIONS (Sister Concern of M/s Automation Systems Ludhiana) Cabin No. 1, 90-C, Shakti Enclave Near Toor Complex, Dugri Road Ludhiana-141002 PUNJAB Virus-free.www.avast.com | 2023-09-08 | 2023-09-29 13:36 | No | Warranty | NARESH BANSAL | H.No 11, Farm House Lane Sarabha Nager,Ext Pakhowal Road | Ludhiana | 142022 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | checked the socket found not giving output. Hence faulty, replaced. E8315_6_WD - 1 No. Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-29 13:40 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11229618 | 103885996 | 2023-09-11 14:57 | 2023-09-08 |  | 2023-09-08 14:13 | A9N3P63C | A9N3P63C | A9N3P63C |  | Jateesh Kumar TECHNO CHTRAR INDIA 46 Esidc indl area narela delhi 110040 Delhi India Defected Products 3 MCB 3 Contctor , 25 ampr, 18 apr, 38 mpr | 2023-09-08 | 2023-09-18 17:01 | No | Warranty | MSP Mall | 46 esidc indl area narela | delhi | 110040 | Delhi | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mcb found dolly free and contactor found phase missing, Hence faulty replaced. A9N2P32C - 1 nos A9N3P63C - 2 nos LC1D38M7 - 1 nos LC1D18M7 - 1 nos Email : jateeshtechnocratindia@rediffmail.com | Repair |  | 8- Service Completed | 2023-09-19 14:06 |  |  | 40 | INR | 40 | ENM HOME DISTRIBUTION
WO-11229699 | 103880002 | 2023-09-08 15:14 | 2023-09-08 |  | 2023-09-08 14:43 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Hello, I would like to raise a complaint regarding the doorbell not functioning at my residence. IH100WFVDP Invoice : 29/6/2022--NT Light Address-Yash bhai cont no-8849544735 R-233,Ashirwad palace,Bhatar,395007 Please solve the issue as soon as possible. Thank you, Yash Jhunjhunwala | 2023-09-08 | 2023-09-08 13:26 | No | Warranty | Yash Yash | R-233, Ashirwad Palace, Bhatar Road | Surat | 395007 | Gujarat | India FS ED&I CSP West Team SHIV SAI ELECTRICALS Vapi | SHIVAM LAD SHIV SAI ELECTRICALS VAPI | shivsai electricals | AS PER SITE VISIT WE CHECK THE PRODUCT AND FOUND OK ON VISUAL INSPECTION.THEN WE CHECK INTERNET STATUS AND FOUND OK.THEN WE CONNECTION THE GATEWAY WITH ROUTER AND CHECK FUCTION AND FOUND OK.SO WE CLOSED THE CASE | Repair |  | 9- Service Validated | 2023-09-12 13:27 |  |  | 138 | INR | 138 | ENM HOME DISTRIBUTION
WO-11229794 | 103830410 | 2023-09-08 16:08 | 2023-09-08 |  | 2023-09-08 15:13 | IN8401_N | IN8401_N | IN8401_N |  | Warning: Email body is too large and was truncated at 32 000 characters. Information may have been lost. Dear Team, Please find the attached complaint of the Zencelo Switches. Name of Customer OM SREE BUILDERS Site Address: Grand Hyderabad , TELANGANA Telangana Name of contact person at site Mr.Shiva Gopinath Contact Phone / Mob. No: 8142388006 Defective product details Zencelo Nature of Defect Not Working Shutdown availability if applicable NA Warranty status NA Commissioned / Installed date Supplied through Raj Marketing Serial No: or DOM of the product SO No - 225674955 Name & phone No: of person registering the complaint OM SREE BUILDERS Material Supplied against ? SO No - 225674955Please register the complaint and attend the same Thanks & Regards, Kothapally Phani KrishnaGeneral Manager - Sales ? Contractors & Building End UsersPartner BusinessGlobal OperationsSchneider Electric D +91-40-39404000 x364M 9908077991F +91-40-3913131E kothapallyphani.krishna@se.com D.No:1-8-271 to 273,401-404A4th Floor,Ashoka Bhoopal ChambersSP Road,SecunderabadSecunderabad, Telangana - 500003India Internal From: OmSree Purchase <purchase@omsree.com> Sent: Wednesday, September 6, 2023 6:43 PM To: KOTHAPALLY PHANI KRISHNA <Kothapallyphani.Krishna@se.com> Cc: grand store <store3@omsree.com>; Dharmender Nayak <logistics@omsree.com>; Signet Store <store1@omsree.com>; SRICHARAN VELIDANDI <sricharan@omsree.com>; PM OD <pm.od@omsree.com>; Ajay Patel <ajay@omsree.com>; Prakash Patel <prakash@omsree.com> Subject: Re: Reg: Need to be take return of Damage & excess material of ?Schneider ( Zencelo ) make ( Omsree Grand ) [External email: Use caution with links and attachments] Dear Phani Krishna, As discussed with you, please find the attached file of Not working ( Technical issue) material details of schneider make zencelo & unicapure models. On Wed, Sep 6, 2023 at 2:42?PM grand store <store3@omsree.com> wrote: Dear Sir, Damage switches not replaced till now please look into this issue sir Thanks & Regards Siva Gopinath, Om Sree Delight / Prithvi / Glory Store In charge, 7032225270. On Tue, Jul 25, 2023 at 4:59?PM OmSree Purchase <purchase@omsree.com> wrote: Dear Phani Krishna, It is to inform you that we received the materials supplied by you against Schneider make Zecelo model, acknowledged by our sites as per some quantity will need to be returned due to excess quantities. These are kept in store due to being surplus. We are requested. The discrepancy of amount needs to be generated in the "Credit Note" as well as the same Credit Note to be required of damage materials which have to be returned for equalizing the stores accordingly with the ledger . S.NO DESCRIPTION UOM SITE NAME EXCESS REMARKS 1 2 MODULAR PLATE IN8402C NOS GRAND 130 ZENCELO SCHNEIDER 2 3 MODULAR PLATE IN8403C NOS 70 3 6 MODULAR PLATE IN8406C NOS 170 4 8 MODULAR PLATE IN8408HL NOS 10 5 6A 1W SWITCH NOS 20 6 6A 2W SWITCH NOS 10 7 DUMMY SWITCH IN8430X NOS 640 8 20A 3 PIN SOCKET IN84220 NOS 3 9 TV SOCKET IN8131TV NOS 5 10 TELEPHONE SOCKET 8431RJS4 NOS 20 11 RJ45 SOCKET IN8431RJ6 NOS 20 12 FAN REGULATOR NOS 20 In this way the damage list is attached to this mail for your reference. DAMAGE SWITCHES SCHINDER MAKE ZENCELO GRAND S.NO ITEM DESCRIPTION UOM QTY 1 6A 1W SWITCH IN8481 NOS 20 2 16A 1W SWITCH IN8481/16 NOS 4 | 2023-09-08 | 2023-09-22 10:06 | No | Warranty | OM SREE BUILDERS | Om shree Grand, Kowkoor Near Yapral null | Hyderabad | 500010 | Telangana | India FS ED&I CSP South Team Master Electrical Solutions Hyderabad | DEBANGSHU BOSE Master Electrical Solutions SECUNDERABAD | Master Electrical Solutions | VISITED THE SITE AND CARRIED OUT THE FOLLOWING JOB.ALL THE SWITCHES HAVING STUCKING PROBLEM .SO WE REPLACED THE OLD SWITCHES WITH NEW ONE . | Repair |  | 9- Service Validated | 2023-09-22 10:09 | Hi Team, Below guven reference is in blocked in status kindly check and provide alternate or unblock the reference. IN8426U Rest below is booked zfre Zvo : 226041565 IN8481 IN8402 IN8481/16 IN8426/16 IN8486/20 IN8431RJS4 IN8431RJ6 IN8490FLW |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-11230114 | 103891956 | 2023-09-08 17:53 | 2023-09-08 |  | 2023-09-08 17:22 | IN8486/32>SZ-PP | IN8486/32>SZ-PP | IN8486/32>SZ-PP |  | Zencelo switch complaint Zencelo Switch--32 amp / 6amp--- Purchased last month Fault: not working | 2023-09-08 | 2023-09-20 16:14 | No | Warranty | Palak Jain | Mohit Jain 12/480 Villa 10 B Harmony Society Macrovvart Ganj | Kanpur | 208001 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Aman Khare_Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found DP switch having on/off issue so we replaced. | Repair |  | 8- Service Completed | 2023-09-20 16:16 |  |  | 115 | INR | 115 | ENM HOME DISTRIBUTION
WO-11230133 | 103891763 | 2023-09-10 16:51 | 2023-09-08 |  | 2023-09-08 17:28 | IN8401 | IN8401 | IN8401 |  | To tal 10 switches are not working IN8401 address : J530 W23 lane sanik farm Delhi 110062 Delhi India | 2023-09-08 | 2023-09-21 14:05 | No | Warranty | Taran Bhatia | J530 W23 lane sanik farm | Delhi | 110062 | Delhi | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the switches and found switches have stuck issue , As per serial number switches not cover under warranty. We replace the switches only this time. We suggest to customer please contact to dealer next time. | Repair |  | 8- Service Completed | 2023-09-21 18:04 |  |  | 38 | INR | 38 | ENM HOME DISTRIBUTION
WO-11231521 | 103892763 | 2023-09-09 11:06 | 2023-09-08 | product needed to be replaced. A9N18367-1Nos. | 2023-09-08 22:07 | A9N18367 | A9N18367 | A9N18367 |  | COMPLAINT FORM SCHNEIDER Bhumi Enterprises Shop No-12,Rachana Industrial Complex T-Block Indrayani Corner Telco Road M.I.D.C Bhosari Pune-411026 VIJAY MO 9325787521 / 9325012236 bhumient2012@gmail.com 1) 100AMP 3POLE A9N18367 This is regarding the non-latching problem RELIABALE ENETERPRISES BILL NO- 13040 DA- 14-11-2022 1) QQ-2022-W45-2 VIJAY MO9326584899 / 9325787521 | 2023-09-08 | 2023-09-13 12:58 | No | Warranty | Bhumi Enterprises | Shop No. 12, Rachna Industrial Complex, T-Block, Indrayani Corner, Telco Raod, MIDC Bhosari | Pune | 411026 | Maharashtra | India FS ED&I CSP West Team Alliance Controls Pvt Ltd Pune | Rohit Srivastav_Alliance Controls Pvt. Ltd | Alliance Controls Pvt. Ltd. (7966) | We visited at site & checked 01 Nos A9N18367 with D.O.M QQ-2022-W45-2 .(1) We checked screw tightness found OK.(2) We checked continuty Y-phase & B-phase pole is open so continuity not getting. Hence , product needed to be replaced. A9N18367-1Nos | Repair |  | 9- Service Validated | 2023-09-13 13:01 |  |  | 1 | INR | 1 | ENM HOME DISTRIBUTION
WO-11234328 | 103908733 | 2023-09-09 14:34 | 2023-09-09 |  | 2023-09-09 13:43 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Dear Team, Please reassign this case as earlier it was cancelled. *WITH REGARDS*Sarabjit Singh*ANANYAA ELECTRICALS I PLOT NO-279, INDUSTRIAL AREA PHASE-II,CHANDIGARH-16002 I ADMIN. AUTH. SERVICE & SPARES DEALER : C&S ELECTRIC ABBINDIA LIMITED, EPCOS & SCHNEIDER ELECTRIC INDIA*E MAIL : ananyaa.ae@gmail.com, MOBILE NO - 7355622336 ---------- Forwarded message ---------From: M SHARMA <ananyaa.ae@gmail.com>Date: Tue, Aug 29, 2023 at 2:46?PMSubject: Case : 103622955 dt.29.8.23To: Lalit KUMAR <Lalit.Kumar@se.com>Cc: Mukesh Kumar <mukesh.kumar@sharmaelectricworks.com>, Brahm Prakash Pandey <brahm.pandey@se.com> Dear Sir, Nitin Mahajan 111 Army Enclave Near subhana Jalandhar punjab . Mr. Nitin Mahajan 9779714156 Product : IH100WFVDP Invoice dt. : MARCH 2023 Doorbell Not Working *WITH REGARDS*Sarabjit Singh*ANANYAA ELECTRICALS I PLOT NO-279, INDUSTRIAL AREA PHASE-II,CHANDIGARH-16002 I ADMIN. AUTH. SERVICE & SPARES DEALER : C&S ELECTRIC ABBINDIA LIMITED, EPCOS & SCHNEIDER ELECTRIC INDIA*E MAIL : ananyaa.ae@gmail.com, MOBILE NO - 7355622336 | 2023-09-09 | 2023-09-09 14:37 | No | Warranty | Nitin Mahajan | 111,Army Enclave, near Subhana, | Jalandhar | 144022 | Punjab | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Ram Ashish Sharma Electric Chandigarh | Sharma Electric works(1003) | Installation done. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-09 14:44 |  |  | 2 | INR | 2 | ENM HOME DISTRIBUTION
WO-11234413 | 103910823 | 2023-09-09 17:37 | 2023-09-09 | Validated By Prashant | 2023-09-09 16:43 | CSS54E_WE | CSS54E_WE | CSS54E_WE |  | Faulty Occupancy Sensor Kindy arrange for an engineer at below site for faulty sensor (CSS54E_WE). Invoice copy attached. Details : Mr Dinesh 2202, Pinacolo NX, Beverly Park, RBK School lane, Mira Bhyander, Mira road East. Thane 401107. M: 7710090070 Parth Chamria | 2023-09-09 | 2023-09-09 18:30 | No | Warranty | Dinesh Dinesh | 2202, Pinacolo NX, Beverly Park, RBK School lane, Mira Bhyander, Mira road East. | Thane | 401107 | Maharashtra | India FS ED&I CSP West Team S K SERVICES Mumbai | Ganesh Tati_S K SERVICES Mumbai | S.K. Services (10237) | We Visited Site Sensor Is Properly Not Operating So Time Setting issue We Set The Time 1 Min Now Operating Ok We Solved & Closed | Repair |  | 9- Service Validated | 2023-09-09 21:20 |  |  | 20 | INR | 20 | ENM HOME DISTRIBUTION
WO-11234417 | 103911768 | 2023-09-11 13:02 | 2023-09-09 |  | 2023-09-09 16:58 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | I have bought this product Schneider Electric WiFi Smart Doorbell 1080P Full HD Camera Home Security Mobile App Regulated Door Alarm System with Motion Sensors & Night Vision Technology (230V AC) (IH100WFVDP-1) last year. It seems like dead. Satyam Gupta127/126 W2 Juhi Kalan Behind Nakshatra Vatika Park, Barra bypass, Kanpur 208027 Satyam Gupta 9795588186 | 2023-09-09 | 2023-09-12 17:43 | No | Warranty | Satyam Gupta | 127/126 W2, Juhi Kala, Barra, Near Sachan Guesthouse | Kanpur | 208027 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Aman Khare_Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found VDP having internal issue so we replaced. | Repair |  | 9- Service Validated | 2023-09-12 17:46 |  |  | 115 | INR | 115 | ENM HOME DISTRIBUTION
WO-11234436 | 103911890 | 2023-09-11 16:10 | 2023-09-09 |  | 2023-09-09 17:43 | IN8401(BZ)-A | IN8401(BZ)-A | IN8401(BZ)-A |  | DEFFCTIVE product IN8401(BZ)-4NOS IN8426/16(BZ)-2 NOS IN8426U(BZ)=2NOS IN8401/16(BZ)-2NOS IN8431RJ6(BJ)=1 NOS EZ9F71463=1 NOS CONTACT DETELIS SHYAM SINGH JI FLAT NO 2 MANGLAM GARND JAIPUR PIN CORD =302020 MOB NO- 9719866311 THANKS | 2023-09-09 | 2023-09-12 17:04 | No | Warranty | SHYAM SINGH | FLAT NO 2 MANGLAM GARND | JAIPUR | 302020 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Sunny Sharma Sharma Electric Jaipur | Sharma Electric Works | Checked the switch found not working and mcb found phase missing, Hence faulty replaced. IN8401(BZ) -4 nos IN8426(BZ) - 2 nos IN8426UNS_BZ- 2 nos IN8401/16(BZ) - 2 nos IN8431RJ(BZ) - 1 nos EZ9F71463 - 1 nos Email : id not provided by customer. | Repair |  | 9- Service Validated | 2023-09-12 17:08 | Ok book alternate Regards Ramkaran Yadav Field Service Representative International Operations Schneider Electric M +91-9929442228 Customer Care 18001030011 E Ramkaran.yadav@se.com Schneider electric India Pvt ltd 309,sangam tower , church road Jaipur, Rajastahan -302001 India Download mySchneider app 24/7 support. Mobile catalog. Access to expert help. *Please consider the environment before printing this e-mail Internal From: Vibhuti Arora <vibhuti.arora@se.com> Sent: 11 September 2023 17:56 To: Ramkaran Yadav <Ramkaran.Yadav@se.com>; Complaints SEW <complaints@sharmaelectricworks.com> Subject: WO-11234436 Hi sir, Pls confirm to book the alternate as the respective material is under block. IN8426U(BZ) 2~3 Pin Universal Soc. w/Shutter-DG IN8426UNS_BZ |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11234437 | 103911936 | 2023-09-11 16:41 | 2023-09-09 |  | 2023-09-09 17:47 | IN8431RJ6_N | IN8431RJ6_N | IN8431RJ6_N |  | Please depute engineer at the site client is facing problam ZENCELO WH $ MCB NOT WORKING DEFFCTIVE product IN8401 = 6 NOS IN84SFR-2 NOS IN8402- 2 NOS IN8405-2 NOS IN8490 FLY -1 NOS IN8431RJ6-2 NOS EZ9F71463=1 NOS CONTACT DETELIS AADHAR KUMAR 92/282 SHIPRA PATH 302020 JAIPUR MOB - 9918038522 | 2023-09-09 | 2023-09-12 11:21 | No | Warranty | AADHAR KUMAR | 92/282 SHIPRA PATH | Jaipur | 302020 |  | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Sunny Sharma Sharma Electric Jaipur | Sharma Electric Works | Checked the switch found not working , Hence faulty replaced. IN8401 - 7 nos IN84SFR - 2 nos IN8402 - 2 nos IN8405 - 2 nos IN8490FLY - 1 nos IN8431RJ6 - 1 nos EZ9F71463 - 1 nos Email : durga.sons2021@gmail.com | Repair |  | 9- Service Validated | 2023-09-12 11:24 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11240009 | 103916469 | 2023-09-13 13:02 | 2023-09-11 |  | 2023-09-11 10:05 | P3200_N | P3200_N | P3200_N |  | Complaint Dr. Kusal deep Dcm colony gali no. 3 near Shana punjab factory, Malout,152107 Punjab 7009795723 Thanks, Sanjay kumar inv attached | 2023-09-11 | 2023-09-13 13:03 | No | Warranty | Kusal deep Kusal deep | Dcm colony gali no. 3 near Shana punjab factory, Malout, | Muktsar | 152107 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the fan regulator found speed variation issue. Hence faulty replaced. P3200 - 1 No. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-13 15:47 |  |  | 195 | INR | 195 | ENM HOME DISTRIBUTION
WO-11241172 | 103913780 | 2023-09-12 08:36 | 2023-09-13 |  | 2023-09-11 11:06 | IH101ZWIFI | IH101ZWIFI | IH101ZWIFI |  | Wiser Installation This mail is regarding Wiser installation in the home of Dr. Mathur in Kashipur, Uttarakhand. We need to send our technical engineer. All mandatory things are done and available on site. I attached the invoice for your reference. Customer Details:- Address -- Hitech eye hospital, opposite girital mandir, Girital, Kashipur, Uttrakhand - 244713. Contact Person -- Mr. Mathur Contact Number -- 98371 20191 IH101ZWIFI---1pc IH14000100---3 pcs IH101ZW2IR---3 pcs IH11000200--2 pcs | 2023-09-11 | 2023-09-14 03:03 | No | Commercial Action - Sales | Mathur Mathur | opposite girital mandir, Girital, Kashipur, |  | 244713 | Uttarakhand | India FS ED&I CSP North Team Seamtek International Pvt. Ltd. GHAZIABAD | Satish Raika Seamtek International Pvt. Ltd. GHAZIABAD | Seamtek International Pvt. Ltd. | following wiser components has been installed gateway: 1qty 4ch relay : 3 qty curtain controller : 2 qty ir controller : 1 qty | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-16 15:05 |  |  | 230 | INR | 230 | ENM HOME DISTRIBUTION
WO-11241447 | 103921415 | 2023-09-11 13:02 | 2023-09-11 |  | 2023-09-11 12:44 | A9N4P63C | A9N4P63C | A9N4P63C |  | A9N4P63C D2215 Qty:1 P: Tripping issue | 2023-09-11 | 2023-09-12 14:08 | No | Warranty | Nishkam Sales | Noorvala rd Near by Sabji Mandi Shivpuri Chownk null | Ludhiana | 141007 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the mcb found tripping issue. Hence faulty replaced. A9N4P63C - 1 Nos. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-13 10:14 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11241496 | 103922240 | 2023-09-11 15:41 | 2023-09-11 |  | 2023-09-11 13:04 | UNS161SW1M_GY | UNS161SW1M_GY | UNS161SW1M_GY |  | Mcb tpn 63 amp not working & sone switches unica not working Hi Team Kindly register a complaint for , unica greay switches easy 9 Mcb tpn 63 amp Mcb . Details as mentioned below: Mcb not trip UNS161SW1M_GY Customer Name - Shubham garg Address - House no 21 Amrawati enclave, newr chokhi dhani,panchkula Contact no - 9999604834 | 2023-09-11 | 2023-09-11 15:50 | No | Warranty | Shubham Garg | House no 21 Amrawati enclave, newr chokhi dhani | Panchkula | 134109 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Karnail Singh Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the Switches found Play issue & fitment issue. and mcb found "R" Phase missing. Hence faulty replaced. UNS61SW1M_GY - 6 Nos. EZ9F71463 - 1 Nos. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-11 17:18 |  |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11241522 | 103919968 | 2023-09-12 09:37 | 2023-09-11 |  | 2023-09-11 13:15 | X1186WH_N | X1186WH_N | X1186WH_N |  | Complaint in Opale Motor starter We have supplied material at following address : Mr. Vijay Pal yadav ( Phone - 8800773859 ) H.No- 934A Sector - 17B Nature of Complaint : X1186WH - 4 Pcs not working X3200WH - 2 NOT WORKING INVOICE ATTACHED. Thanks & Regards Pardeep sachdeva Mobile No : 0-9899806665 | 2023-09-11 | 2023-09-12 15:57 | No | Warranty | VP Yadav | 934A Sector - 17B Gurgaon -122001 (HRY) | Gurgaon | 122001 | Haryana | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the fan regulators and motor starter and found regulators have output problem and motor starter have stuck issue. As per serial number product not cover under warranty. We suggest to customer please contact to dealer for replacement. We reject the replacement and close the complaint. | Repair |  | 9- Service Validated | 2023-09-12 15:57 |  |  | 52 | INR | 52 | ENM HOME DISTRIBUTION
WO-11241672 | 103912866 | 2023-09-11 15:39 | 2023-09-11 | its product need to be replaced .X1001WH-02 Nos | 2023-09-11 14:23 | X1001WH_N | X1001WH_N | X1001WH_N |  | Re: Opale switch to replace I have an Opale switch which is not working. Please find attached herewith the warranty letter and other details. Quantity - 3 Switch - Opale Address- Geetha Sarang Dani Greens, K 1002 Opp Pudumjee Paper Mills, Thergaon, Pune Mobile no 8007844007 Could you please do the needful. Regards, Sarang Dani +918007844007 | 2023-09-11 | 2023-09-11 17:39 | No | Warranty | Geetha Sarang Dani | Greens, K 1002,Opp Pudumjee Paper Mills,Thergaon | Pune | 411033 | Maharashtra | India FS ED&I CSP West Team Alliance Controls Pvt Ltd Pune | Rohit Srivastav_Alliance Controls Pvt. Ltd | Alliance Controls Pvt. Ltd. (7966) | We visited at site & disscuss with customer regarding switch and done following point . (1)checking (02) Nos of pole switch found faulty checking ON/OFF operation .(2) Open cover plate and check switch side hock broken . (3) this product switch os out of warranty but customer moving 10 year warranty certification so this come under warranty & its product need to be replaced .X1001WH-02 Nos | Repair |  | 9- Service Validated | 2023-09-12 10:41 | =S= Consig Fill up 226047061 |  | 10 | INR | 10 | ENM HOME DISTRIBUTION
WO-11241731 | 103920987 | 2023-09-14 08:27 | 2023-09-15 |  | 2023-09-11 14:41 | IH101ZWIFI | IH101ZWIFI | IH101ZWIFI |  | Wiser Installation Request: Seamtek Dear Team, Please arrange to install wiser components to below address: Delivery address Sobha city Tower A2 Flat no. 144 Sector 108 Dwarka Expressway Gurgaon Contact Person: Mr Ankit: 9810733059 IH101ZWIFI---1 pc IH14000100---4 pcs IH11000200--1 pc Inv attached | 2023-09-11 | 2023-09-16 02:02 | No | Commercial Action - Sales | ANKIT GARD | Sobha city Tower A2 Flat no. 144 Sector 108 Dwarka Expressway | Gurgaon | 122001 | Haryana | India FS ED&I CSP North Team Seamtek International Pvt. Ltd. GHAZIABAD | Satish Raika Seamtek International Pvt. Ltd. GHAZIABAD | Seamtek International Pvt. Ltd. | Following wiser has been installed Gateway:1 4 channel relay: 4 Curtain controller: 1 | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-16 14:10 |  |  | 52 | INR | 52 | ENM HOME DISTRIBUTION
WO-11241969 | 103925459 | 2023-09-12 10:19 | 2023-09-11 |  | 2023-09-11 16:30 | UNSCP12M_GY | UNSCP12M_GY | UNSCP12M_GY |  | Re: Three pin socket is lock problem [ thread::RFIvP6Gqcyil4x0gVV7Emj4:: ] I have purchase the three pin socket from Aarcee Mittal Electrical Pvt Ltd Invoice Date 19 July 2023 T.SB. OVERSEAS Mr Bindra Plot no 34 Road No. 55 West Punjabi Bagh New Delhi- 110026 9811505554 | 2023-09-11 | 2023-09-14 15:09 | No | Warranty | TSB OVERSEAS | Plot no 34, Road no 55, West Punjabi Bagh | New Delhi | 110026 | Delhi | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the socket and found socket have output issue, We replace the faulty socket with new. Mail Id. dkrpandey@hotmail.com | Repair |  | 9- Service Validated | 2023-09-15 11:22 |  |  | 32 | INR | 32 | ENM HOME DISTRIBUTION
WO-11241992 | 103925887 | 2023-09-12 11:11 | 2023-09-11 |  | 2023-09-11 16:45 | IH11000200 | IH11000200 | IH11000200 |  | RE: FW: Installation of wiser [ thread::qxQYY0akdWGETh-N1LURSj4:: ] Please create work order for Installation of wiser automation at given locations ; Mr. Sushil jain , 1402, Cloud-9, Vaishali, Ghaziabad. Mobile : Contact Person : Surjeet kumar 8810357952. Following components to be installed: Wiser gate way : 1 No. 4 Channel relay 10 No. Best regards, SK Jain 8800336081 | 2023-09-11 | 2023-09-13 02:15 | No | Commercial Action - Sales | Sushil Jain | 1402, Cloud-9, Vaishali, | Ghaziabad | 201010 |  | India FS ED&I CSP North Team Seamtek International Pvt. Ltd. GHAZIABAD | Satish Raika Seamtek International Pvt. Ltd. GHAZIABAD | Seamtek International Pvt. Ltd. | Following wiser components has been installed Gateway: 1 qty Relay : 10 | Commissioning & Installation | Start-up | 8- Service Completed | 2023-09-16 14:21 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11242061 | 103930124 | 2023-09-11 17:50 | 2023-09-11 | Switch not operating | 2023-09-11 17:01 | X1001WH_N | X1001WH_N | X1001WH_N |  | Part replacement/ repair under warranty 1. Name of Customer: Nirnay Chaudhari 2. Site Address: - Flat no. 204, Wing-J, Greens society, opp.Pudumjee paper mill, Thergaon, Pune. Maharashtra. 3. Name of contact person at site :- Nirnay Chaudhari 4. Contact Phone / Mob. No: - 8149979517 5. Defective product details:- Electric switch not working properly. 6. Product Make:- Schneider Electric 7. Nature of Defect: Functioning defect. 8. Shutdown availability if applicable :nil 9. Serial No: or DOM of - not available on product. 10. Dealer Name /OA no. /Invoice Details: - NIL 11. Commissioned / Installed date:- NIL 12. Name & phone No: of person registering the complaint: Mr. Nirnay Chaudhari. ( Flat owner) phone -8149979517. | 2023-09-11 | 2023-09-12 15:58 | No | Warranty | Nirnay Chaudhari | Flat no. 204, wing- J, Greens, opposite Pudumjee paper mill, Thergaon | Pune | 411033 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Kunal jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the switches found that the not operating. but we observed switch is working properly. and then taken operation working found ok. | Repair |  | 9- Service Validated | 2023-09-12 16:12 |  |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11242343 | 103930380 | 2023-09-14 15:48 | 2023-09-11 |  | 2023-09-11 18:20 | IN8405_N | IN8405_N | IN8405_N |  | Please depute engineer at the site client is facing problam ZENCELO DEFFCTIVE product IN8401 = 6 NOS IN8486/32 WH = 3 NOS IN8405 = 1 NOS CONTACT DETELIS ARVIND KUMAR JAIN 64/415 HEERA PATH MANSARTOWAR JAIPUR MOB - 9462420501 | 2023-09-11 | 2023-09-14 15:50 | No | Warranty | Arvind Kumar Jain | 69/415, madhyam Marg, heera path, mansarovar, | Jaipur | 302020 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Sunny Sharma Sharma Electric Jaipur | Sharma Electric Works | Checked the switch found not working and switch found out of warranty, Hence no replacement given to customer. Email : id not provided by customer. | Repair |  | 9- Service Validated | 2023-09-14 15:54 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11242353 | 103927871 | 2023-09-12 15:00 | 2023-09-11 |  | 2023-09-11 18:26 | A9KF71432 | A9KF71432 | A9KF71432 |  | FW: Request for faulty MC REPLACEMENT Item Sr. No.1, 63A, 4P MCB(A9KF71463), and Item Sr. No. -2, 32A 4P MCB (A9KF71432) 1 Nos. Each not Working, YOU ARE REQUESTED PLEASE DEPUTE YOUR SERVICE ENGINEER FOR RECTIFY THE FAULT OR ARRANGE FOR REPLACEMENT. | 2023-09-11 | 2023-09-18 14:25 | No | Warranty | Kandi Electrical Solutions PVT. Ltd. | Khasra No. 981/330 , Block -3 Basai Industrial area village Basai Near Basai Flyover Basai . . | Gurgaon | 122006 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mcb found dolly free , Hence faulty replaced. A9N4P63C - 1 nos Email : id not provided by customer . | Repair |  | 8- Service Completed | 2023-09-19 14:29 |  |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11247052 | 103957857 | 2023-09-12 14:25 | 2023-09-12 | Part order request validated by Mr. Chandrakant Panchal Sir | 2023-09-12 13:10 | A9KF71440 | A9KF71440 | A9KF71440 |  | Complaints A9KF71463 A9KF71440 each 1 qty Site Address- Site Kasturba Nagar Bhopal B76 Crystal Tower Name ? Sanjeev Gupta Number - 9302253628 Pincode ?462023 | 2023-09-12 | 2023-09-16 10:48 | No | Warranty | Siddhant Instruments & Equipments | B-76, Crystal Tower, Katurba Nagar | Bhopal | 462023 | Madhya Pradesh | India FS ED&I CSP West Team ABR Technical Service Indore | Lalu Sen_ABR Tecneical Services Indore | ABR Technical Services (9574) | Reached at site (at dealer office) and checked 2 Nos. MCBs and found details are given below 1) A9KF71140-(D2225)-dolly free 2) A9KF71463-(D2223)-dolly free So only for customer we replace 2 Nos. MCBs Booked direct customer address | Repair |  | 9- Service Validated | 2023-09-18 10:50 | =S= Consig Fill up 226061171 |  | 220 | INR | 220 | ENM HOME DISTRIBUTION
WO-11247190 | 103959147 | 2023-09-12 17:23 | 2023-09-12 |  | 2023-09-12 14:21 | CSS54E_WE | CSS54E_WE | CSS54E_WE |  | COMPLAINT CSS54E_WE - 2pcs customer name - guddu ji customer address- shyaml milk dairy 0 krishna nagar palia kalan kheri , lakhimpur uttar pradesh 262902 customer no- 7275467183 | 2023-09-12 | 2023-09-18 15:31 | No | Warranty | SHYAMAL MILK PRODUCTS PRIVATE LIMITED | KRISHNA NAGAR PALIA KALAN LAKHHIMPUR PALIAKHERI null | Lakhimpur Kheri | 262902 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Abhishek Patel Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found sensor having internal issue, so we replaced. | Repair |  | 8- Service Completed | 2023-09-18 15:33 |  |  | 220 | INR | 220 | ENM HOME DISTRIBUTION
WO-11247631 | 103959336 | 2023-09-13 13:14 | 2023-09-12 |  | 2023-09-12 14:58 | P1101_N | P1101_N | P1101_N |  | Livia P1001-8 pcsP1101-2 pcsContact number 8171373666Bareilly 243001Rahul je297 army salavition road near praveen singh kothi Sent from my iPhone | 2023-09-12 | 2023-09-15 18:01 | No | Warranty | Rahul Rahul | 297 army salavition road near praveen singh kothi null | Bareilly | 243001 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Abhishek Patel Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Switches having on/off issue. So engineer reached near to site for replacement but customer denied for today visit. So call is closed. Material will be replace as per customer availability. | Repair |  | 9- Service Validated | 2023-09-15 18:06 |  |  | 265 | INR | 265 | ENM HOME DISTRIBUTION
WO-11247989 | 103961148 | 2023-09-14 13:58 | 2023-09-12 |  | 2023-09-12 16:43 | UNSMTSTART2M_WE | UNSMTSTART2M_WE | UNSMTSTART2M_WE |  | Hi Team Kindly arrange to attend the complaint of our Distributor-Bold Evolution Infotech, photo attached for your reference. Product: Unica White Motor Starter Complaint: Motor Starter buttons not working Address: Bold Evolution Infotech, Kesho Ram Tower, Nakodar Road, Jalandhar- 144001 Contact Person: Mr Rakesh Contact No: 9464786148 Thanks & Regards Rageni SharmaMANAGERHOME & DISTRIBUTIONRetail DivisionSchneider Electric Location: Jalandhar D +91 9910033280M +91 9910033280Customer Care 18001030011E rageni.sharma@se.com 2nd FloorTower -A, Bestech Business TowerSector - 66Mohali - 160062India *Please consider the environment before printing this e-mail Download mySchneider app 24/7 support. Mobile catalog. Access to expert help. *Please consider the environment before printing this e-mail Internal | 2023-09-12 | 2023-09-14 14:01 | No | Warranty | Bold Evolution Infotech India Pvt Ltd. | Kesho Ram Tower, Nakodar Road, Opp Downtown Hotel | Jalandhar | 144001 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | checked the starter switch found button stucking issue. hence faulty, replaced. UNSMTSTART2M_WE -3 Nos. Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-14 16:03 |  |  | 1 | INR | 1 | ENM HOME DISTRIBUTION
WO-11248022 | 103961014 | 2023-09-14 12:30 | 2023-09-12 |  | 2023-09-12 16:58 | IN8402C_BZ | IN8402C_BZ | IN8402C_BZ |  | Hi Kindly arrange to attend complaint of below customer. Invoice copy attached for your reference. Product : Zencelo Switches Contact Person: Kalsi Builders & Contractor Golden View Colony, Near Wadala Chowk, Nakodar Road, Jalandhar Contact No: 9814027218 Thanks & Regards Rageni SharmaMANAGERHOME & DISTRIBUTIONRetail DivisionSchneider Electric Location: Jalandhar D +91 9910033280M +91 9910033280Customer Care 18001030011E rageni.sharma@se.com 2nd FloorTower -A, Bestech Business TowerSector - 66Mohali - 160062India *Please consider the environment before printing this e-mail Download mySchneider app 24/7 support. Mobile catalog. Access to expert help. *Please consider the environment before printing this e-mail Internal | 2023-09-12 | 2023-09-14 12:42 | No | Warranty | Kalsi Builders & contractors, | gloden view colony , near Wadala chownk Nakodar road, null | Jalandhar | 144003 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | checked the switches found play problem. hence faulty, replaced. IN8401 - 10 Nos. Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-14 15:53 |  |  | 1 | INR | 1 | ENM HOME DISTRIBUTION
WO-11248155 | 103966828 | 2023-09-13 15:30 | 2023-09-12 |  | 2023-09-12 17:59 | X1001WH_N | X1001WH_N | X1001WH_N |  | Re: Please depute engineer at the site client is facing problam OPALA RANG [ thread::XPCSwTfGfiWDGMv5Ztvwqz4:: ] Please depute engineer at the site client is facing problam OPALA RANG X1001WH - 40 6/ 16 MANSAROVER 302020 SFS MOB 9829060644 | 2023-09-12 | 2023-09-18 12:18 | No | Warranty | Karthik Karthik | 6/ 16 MANSAROVER SFS | Jaipur | 302020 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Sunny Sharma Sharma Electric Jaipur | Sharma Electric Works | Checked the switch found not working, Hence faulty replaced. X1001WH - 40 nos Email : durga.sons2021@gmail.com | Repair |  | 8- Service Completed | 2023-09-19 12:20 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11248195 | 103966233 | 2023-09-13 09:56 | 2023-09-12 |  | 2023-09-12 18:24 | E8331FR350_WG_G8 | E8331FR350_WG_G8 | E8331FR350_WG_G8 |  | COMPLAIN ? E8331FR350_GH_G8 - QTY - 4 (GULABCHAND VISHNANI.) Name of Customer M/S GULABCHAND VISHNANI 2 Site Address G1/701 HAPPY EXCELLENICA, NEAR JOLLY PARTY PLOT, VESU, SURAT - 395007 Contact Phone / Mob. No: 9722006600 3 Name of contact person at site MR. GULABCHAND VISHNANI 5 Defective product details E8331FR350_GH_G8 - QTY - 4 6 Product Make SCHNEIDER-REGULATOR 7 Nature of Defect NOT WORKING 8 Shutdown availability if applicable 9 Warranty status UNDER WARRANTY 10 Commissioned / Installed date 11 Serial No: or DOM of the product BILL NO - : 1699/22-23 DATE - 15-06-2022 12 Name & phone No: of person registering the complaint JOHNSON- 8780431402 13 | 2023-09-12 | 2023-09-14 16:31 | No | Warranty | GULABCHAND VISHNANI | G1/701 HAPPY EXCELLENICA, NEAR JOLLY PARTY PLOT, VESU, | Surat | 395007 | Gujarat | India FS ED&I CSP West Team SHIV SAI ELECTRICALS Vapi | SHIVAM LAD SHIV SAI ELECTRICALS VAPI | shivsai electricals | AS PER SITE VISIT WE CHECK THE PRODUCT AND FOUND OK ON VISUAL INSPECTION.AFTER THAT CHECK THE FAN REEGULATOR AND FOUND THE FAN REGULATIR IS STUCK.WHEN WE CHECK THE PRODUCT WARRNTY STATUS AND FOUND THE PRODUCT IS UNDER WARRNTY NEEDS TO BE REPLACED. | Repair |  | 9- Service Validated | 2023-09-15 16:33 | =S= Consig Fill up 226049837 |  | 137 | INR | 137 | ENM HOME DISTRIBUTION
WO-11252947 | 103992416 | 2023-09-14 14:21 | 2023-09-13 |  | 2023-09-13 11:26 | IH101ZWIFI | IH101ZWIFI | IH101ZWIFI |  | Wiser installation Phase 4 for HT Installation request Automation Gateway IH101ZWIFI --1- Qty 4 Channel Automation Relay-IH14000100 - 5Qty VIJAY SHANKAR 9971158702 5/ A1 Hindustan Times Apartments, Shashi Park Rd, Mayur Vihar, New Delhi, Delhi, 110091 | 2023-09-13 | 2023-09-14 01:05 | No | Commercial Action - Sales | VIJAY SHANKAR |  | Delhi | 110091 | Delhi | India FS ED&I CSP North Team Seamtek International Pvt. Ltd. GHAZIABAD | Satish Raika Seamtek International Pvt. Ltd. GHAZIABAD | Seamtek International Pvt. Ltd. | following wiser components has been installed gateway: 1no 4 ch relay: 5 no | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-14 17:08 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11253420 | 103993061 | 2023-09-13 16:40 | 2023-09-13 |  | 2023-09-13 14:31 | LSS100100 | LSS100100 | LSS100100 |  | Techincal Issues - Wiser For KNX 729A, DLF Camellias, Phase -5 Gurgaon , Haryana Harshit - 8218612352 Nariender - 7807652063 harshit.sharma@iiiot-infotech.com Software/communication Issue No LSS100100 Cloud connection not established | 2023-09-13 | 2023-09-20 14:23 | No | Warranty | IIIOT-Infotech | 729A, DLF Camellias, Phase -5 null | Gurgaon | 122002 | Haryana | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the KNX logic wiser and found KNX wiser have communication issue. As per serial number KNX wiser not cover under warranty. Customer provide the invoice. So we arrange the replacement. Mail Id. harshit.sharma@iiiot-infotech.com | Repair |  | 8- Service Completed | 2023-09-20 14:52 |  |  | 54 | INR | 54 | ENM HOME DISTRIBUTION
WO-11253701 | 104001674 | 2023-09-14 16:27 | 2023-09-13 |  | 2023-09-13 16:21 | A9N4P40C | A9N4P40C | A9N4P40C | DD-2023-W27-5-11 | Faulty mcb Below Product failed under warranty. Kindly arrange replacement to the customer. 1. A9N4P40C ( Serial N0 ?DD-2023-W27-5-11 ) - 1 Nos ? Dolly Free Customer Details :- LAKSHYA ENTERPRISES 279 OPP.EKLINGNATH PETROL PUMP, SUKHER, UDAIPUR, Rajasthan 313001 Contact. Narendra ji 8233594464 | 2023-09-13 | 2023-09-14 16:30 | No | Warranty | Lakshya Enterprises | 279,EKLINGNATH PETROL PUMP Udyog Vihar, Gaurav Path Road, NH-8, Near Witty Intl School, Sukher, Udaipur-313001 | Udaipur | 313001 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | checked the mcb found dolly free, hence faulty, set right the same. now working ok. Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-14 16:33 |  |  | 398 | INR | 398 | ENM HOME DISTRIBUTION
WO-11253808 | 104004730 | 2023-09-14 11:09 | 2023-09-13 | NA | 2023-09-13 17:03 | E8331D20N_DG | E8331D20N_DG | E8331D20N_DG |  | Visit Requirement Avatron switches --Not working Location - 9 Sunnypark, Flat 1C, Ballygunge, Kolkata - 700019. West Bengal, India. Contact Person - Mrs. Anju Agarwal Contact Number - +919830230573 inv attached | 2023-09-13 | 2023-09-16 02:00 | No | Warranty | Anju Agarwal | 9 Sunnypark, Flat 1C, Ballygunge, | Kolkata | 700019 | West Bengal | India FS ED&I CSP East Team B.D Electroservices Kolkata | KOUSHIK MONDAL_B.D Electroservices Kolkata | B.D Electroservices(500017330) | On received of ZVO material will delivered to customer. | Repair |  | 9- Service Validated | 2023-09-16 14:38 |  |  | 16 | INR | 16 | ENM HOME DISTRIBUTION
WO-11253829 | 104004172 | 2023-09-14 17:30 | 2023-09-13 |  | 2023-09-13 17:14 | IN8431RJ6_N | IN8431RJ6_N | IN8431RJ6_N |  | Please depute engineer at the site client is facing problam ZENCELO WH $ MCB NOT WORKING DEFFCTIVE product IN8401 = 6 NOS IN8401/16=4nos IN84SFR-2 NOS IN8402- 2 NOS IN8405-2 NOS IN8490 FLY -1 NOS IN8431RJ6-2 NOS EZ9F71463=1 NOS IN8486/32-1 NOS CONTACT DETELIS AADHAR KUMAR 92/282 SHIPRA PATH 302020 JAIPUR MOB - 9918038522 | 2023-09-13 | 2023-09-14 17:33 | No | Warranty | AADHAR KUMAR | 92/282 SHIPRA PATH | Jaipur | 302020 |  | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Sunny Sharma Sharma Electric Jaipur | Sharma Electric Works | Checked the switch found not working, Hence faulty replaced. IN8486/32 - 4 nos IN8401 - 7 nos IN8405 - 1 nos IN8401/16 - 4 nos Email : id not provided by customer. | Repair |  | 9- Service Validated | 2023-09-15 11:16 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11253868 | 104002922 | 2023-09-14 11:35 | 2023-09-13 |  | 2023-09-13 17:24 | A9N3P32C | A9N3P32C | A9N3P32C |  | Mcb faulty Dear sir Model - A9N3P32C Serial no - D2234 Problem - Dolly free So please dispute the service engineer to check and resolve the issue As soon as possible Customer name - S.P. Hidroulic Contact person - vibhuti Kumar Contact no - 8279957087 Address - near Bhagwati dhaba Shri ji puram Sikandra Agra up 282007 | 2023-09-13 | 2023-09-19 15:30 | No | Warranty | SP HYDRAULIC | BEHIND BHAGWATI DHABA | AGRA | 282007 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Monu Pandey_Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found contactor having pole open issue & MCB having dolly free, so we replaced. | Repair |  | 8- Service Completed | 2023-09-19 15:38 |  |  | 360 | INR | 360 | ENM HOME DISTRIBUTION
WO-11253919 | 104001114 | 2023-09-16 09:59 | 2023-09-13 |  | 2023-09-13 17:43 | IN8481_BZ | IN8481_BZ | IN8481_BZ |  | Complaint Zencelo Dear team, Pls register complaint of Zencelo Detail as per below? Sukhpal 117, New Town Ratia 125051 Distt Fatehabad Haryana 9354202263 Thanks & Regards, SANJAY KUMAR Manager-Sales | 2023-09-13 | 2023-09-16 13:44 | No | Warranty | Sukhpal Sukhpal | 117, New Town Ratia 125051 | Fatehabad | 125051 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Rakesh Kumar Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the DP switches found not properly on / off and switches found not giving output. Hence faulty replaced. IN8486/32 - 2 nos. IN8481 - 1 nos. IN8402 - 1 nos. IN8401 - 2 nos. IN8481/16 - 2 nos. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-16 16:34 |  |  | 210 | INR | 210 | ENM HOME DISTRIBUTION
WO-11254012 | 104007064 | 2023-09-14 10:33 | 2023-09-13 |  | 2023-09-13 18:11 | A9N2P16C | A9N2P16C | A9N2P16C |  | REPLACEMENT OF MCB [ thread::g9PDaXNde4SKGwO5c88MLz4:: ] due to mcb part no A9N2P16C is not working. please replacement the mcb same part no A9N2P16C. -- | 2023-09-13 | 2023-09-18 14:09 | No | Warranty | Shikoku Technology | PLOT NO. 46, 1st FLOOR, SECTOR- 4, IMT MANESAR | Gurgaon | 122051 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mcb found dolly free, Hence faulty replaced A9N2P16C - 1 nos Email : id not provided by customer. | Repair |  | 8- Service Completed | 2023-09-19 14:12 |  |  | 55 | INR | 55 | ENM HOME DISTRIBUTION
WO-11256815 | 104024323 | 2023-09-14 10:38 | 2023-09-14 | Replacement has already been given to customer by Hi-tech | 2023-09-14 09:30 | IN8425MS_BZ | IN8425MS_BZ | IN8425MS_BZ |  | COMPLAIN ? IN8425MS (BZ) - QTY - 05, IN84SFR - QTY - 03, IN8426 U(BZ) - QTY - 02 (BAJAJ WORLD.) Name of Customer M/S BAJAJ WORLD 2 Site Address PLOT NO. 1 AND 2 A GROUND FLOOR AND 1ST FLOOR , BALAJI IND CO. OP SERVICE SOCIETY 2, NEAR BHATAR CHAR RASTA U.M, ROAD SURAT - PIN: 395007 Contact Phone / Mob. No: 7698897074 3 Name of contact person at site MR.Bhavesh Bhai 5 Defective product details IN8425MS (BZ) - QTY - 05 , IN84SFR - QTY - 03 , IN8426 U(BZ) - QTY - 02 6 Product Make SCHNEIDER-SWITCH , REGULATOR 7 Nature of Defect NOT WORKING 8 Shutdown availability if applicable 9 Warranty status UNDER WARRANTY 10 Commissioned / Installed date 11 Serial No: or DOM of the product BILL NO - : 5302/23-24 DATE - 28-08-2023 12 Name & phone No: of person registering the complaint JOHNSON- 8780431402 | 2023-09-14 | 2023-09-14 21:30 | No | Warranty | BAJAJ WORLD | Plot No 1 And 2a, Balaji Ind Co Op Service Society 2 Ground Floor And 1st Floor, Near Bhatar 4 Rasta U M Road null | Surat | 395007 | Gujarat | India FS ED&I CSP West Team VARDHAMAN ELECTROSOFT Vadodara | MAHENDRA SINGH VARDHAMAN ELECTROSOFT Vadodara | VARDHAMAN ELECTROSOFT | we visited the site and check 1.IN28425MS- when i checked this equipment i found no pole to pole continuity 2.IN1186WH- on/off stuck issue 3.IN8426U- we found shutter not working 4. IN84SFR-we found speed variation issue | Repair |  | 9- Service Validated | 2023-09-14 17:57 | =S= Consig Fill up 226031712 |  | 20 | INR | 20 | ENM HOME DISTRIBUTION
WO-11258496 | 104025495 | 2023-09-14 16:02 | 2023-09-14 |  | 2023-09-14 11:01 | X1001WH_N | X1001WH_N | X1001WH_N |  | Opale switch complaint SWITCH NOT WORKING Name : Anu Chaudhary Address : C3-242 Sobha City Dwarka Expressway sec 108 Gurugram Haryana 122017 M.No : 8527736999 switch 2 faulty opale Invoice Date : 22-10-2022 | 2023-09-14 | 2023-09-19 15:53 | No | Warranty | ANU CHAUDHARY | C3-242 Sobha City Dwarka Expressway sec 108 | Gurgaon | 122017 | Haryana | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the switches and found switches have output issue, We replace the faulty switches with new. Mail Id. fm.scg@sobha.com | Repair |  | 8- Service Completed | 2023-09-19 16:29 |  |  | 53 | INR | 53 | ENM HOME DISTRIBUTION
WO-11258515 | 104025218 | 2023-09-14 12:00 | 2023-09-14 | Validated By Prashant | 2023-09-14 11:10 | IN8486/32 | IN8486/32 | IN8486/32 |  | Please Register New Complaint 14-08-2023 Name Of Customer Central Electrical Site Address Shop No:-8, Bharadwaj Building .Dr.Dada Vaidya Road,Panaji-Goa.403001 Name Of Contact Person At Site Tushar Contact Phone / Mob. No: 9284521572 Defective Product Details IN8486/32:- 8Nos Serial No:-23093:- 8Nos Nature Of Defect Not Working Shutdown Availability If Applicable Warranty Status Yes | 2023-09-14 | 2023-09-20 12:10 | No | Warranty | Central Electric Enterprises | Shop No 8, Bharadwaj Building Dr. Dada Vaidya Road | Panaji | 403001 | Goa | India FS ED&I CSP West Team East India Power Engineers Mumbai | Abhishek Parab_East India Power engineers Mumbai | S.K. Services (10237) | We Visited the site 32MPR DP switch is not operating properly side lock broken. | Repair |  | 8- Service Completed | 2023-09-20 12:13 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11258644 | 104026374 | 2023-09-14 15:33 | 2023-09-14 |  | 2023-09-14 11:52 | IH101ZWIFI | IH101ZWIFI | IH101ZWIFI |  | Wiser installation Phase 4 for HT NARESH SHARMA 9899116441 12/C4 Hindustan Times Apartments, Shashi Park Rd, Mayur Vihar, New Delhi, Delhi, 110091 Automation Gateway IH101ZWIFI - 1 Qty 4 Channel Automation Relay-IH14000100 - 5 Qty | 2023-09-14 | 2023-09-14 23:00 | No | Commercial Action - Sales | NARESH SHARMA | 12/C4 Hindustan Times Apartments | Delhi | 110091 | Delhi | India FS ED&I CSP North Team Seamtek International Pvt. Ltd. GHAZIABAD | Satish Raika Seamtek International Pvt. Ltd. GHAZIABAD | Seamtek International Pvt. Ltd. | following wiser components has been installed: gateway : 1 no 4 ch relay : 5 no | Commissioning & Installation | Start-up | 8- Service Completed | 2023-09-14 17:03 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11258754 | 104026826 | 2023-09-16 14:25 | 2023-09-16 |  | 2023-09-14 12:16 | IH14000100 | IH14000100 | IH14000100 |  | Re: Product replacement [ thread::4diKUwakc2mJYSZQFj9XAz4:: ] we are facing some problems in using Four No's of 2 Channel Relay and Dimmer controller and One no's of 4 chanel Automation Relay Sanjeev Kumar 9968230446 A-32, Naraina Industrial Area NewDelhi -29 | 2023-09-14 | 2023-09-22 01:51 | No | Warranty | Sanjeev Kumar | A-32, Naraina Industrial Area | Delhi | 110029 | Delhi | India FS ED&I CSP North Team Seamtek International Pvt. Ltd. GHAZIABAD | Satish Raika Seamtek International Pvt. Ltd. GHAZIABAD | Seamtek International Pvt. Ltd. | following wiser components has been repair: (faulty) replace components : 2 ch dimmer controller: 3 qty 4 channel relay : 1 qty | Repair |  | 8- Service Completed | 2023-09-22 17:55 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11258852 | 104028738 | 2023-09-15 15:33 | 2023-09-14 |  | 2023-09-14 12:59 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | VDP-Issue VDP issue Inv attached Mr. Manav Address: House Number : 205 Green Park jalandhar, Pin code : 144003 Contact number :+91 9888200651, , 8360361651 | 2023-09-14 | 2023-09-19 13:48 | No | Warranty | Manav Manav | House Number : 205, Green Park | Jalandhar | 144003 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | checked the vdp found automation reset and push button. hence faulty, replaced. IH100WFVDP- 1 Nos. Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-19 13:50 |  |  | 65 | INR | 65 | ENM HOME DISTRIBUTION
WO-11258910 | 104027298 | 2023-09-15 11:17 | 2023-09-14 |  | 2023-09-14 13:17 | P1002_N | P1002_N | P1002_N |  | Fwd: Case : 103911924 dt. 11.9.23 Product : UNS32DP2M-WE=10 NOS, UNS4STFAN1M-WH-10 NOS UNS6SK3P2MNS-1 NOS,UNS61SW1M-WH - 10NOS, UNS161SW1M-WE-5NOS EZ9S66463-1NOS, EZ9F71463=1 NOS Product : P1002-2NOS,P1101-1NOS,P7001-1NOS P1132-1 NOS,P1086-1NOS,P2005NS-1 NOS P3100=-5 NOS,EZ9S66463-1NOS,EZ9F71463=1 NOS,P1085-7 NOS not working -- *WITH REGARDS-* Sarabjit Singh SHARMA ELECTRIC WORKS I CHANDIGARH | 2023-09-14 | 2023-09-15 15:24 | No | Warranty | UTTAM YADAV | GANGARAM KI DHANI DHAWAS null | Jaipur | 302043 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | Checked the fan regulator found not working, Hence faulty replaced. UNS4STFAN1M_WE - 3 nos Email : id not provided by customer . | Repair |  | 8- Service Completed | 2023-09-19 12:12 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11259102 | 104027350 | 2023-09-14 15:30 | 2023-09-14 |  | 2023-09-14 14:43 | A9KR12263 | A9KR12263 | A9KR12263 |  | Agrasen Engineering Industries Pvt Ltd Road No-9F,VKI Area,jaipur Mr.Akshati 6375776548 Product : A9KR12463BQ Not operating -- *WITH REGARDS-* Sarabjit Singh SHARMA ELECTRIC WORKS I CHANDIGARH I ADMIN. AUTH. SERVICE & SPARES Dear Team, Please reissue the case no. Earlier it was cancelled . ---------- Forwarded message --------- From: Complaints SEW Date: Tue, Sep 12, 2023 at 5:27?PM Subject: Case : 103964944 dt. 12.9.23 To: Complaints SEW , Sharma Electric Cc: Ramkaran Yadav , Mukesh Kumar , Rajan Singh Dear Sir, Agrasen Engineering Industries Pvt Ltd Road No-9F,VKI Area,jaipur Mr.Akshati 6375776548 Product : A9KR12463BQ Not operating -- *WITH REGARDS-* Sarabjit Singh SHARMA ELECTRIC WORKS I CHANDIGARH I ADMIN. AUTH. SERVICE & SPARES DEALER : CROMPTON GREAVES & SCHNEIDER ELECTRIC INDIA* Tele FAX 0172-4629871 E MAIL : complaints@sharmaelectricworks.com * Address : PLOT NO. 279, GF, INDUSTRIAL AREA,* *PHASE-II, CHANDIGARH-160002 , Website : www.sharmaelectricworks.com* *** Please consider the environment before printing this e-mail -- *WITH REGARDS-* Sarabjit Singh SHARMA ELECTRIC WORKS I CHANDIGARH I ADMIN. AUTH. SERVICE & SPARES DEALER : CROMPTON GREAVES & SCHNEIDER ELECTRIC INDIA* Tele FAX 0172-4629871 E MAIL : complaints@sharmaelectricworks.com * Address : PLOT NO. 279, GF, INDUSTRIAL AREA,* *PHASE-II, CHANDIGARH-160002 , Website : www.sharmaelectricworks.com* *** Please consider the environment before printing this e-mail | 2023-09-14 | 2023-09-14 15:40 | No | Warranty | Agrasen Engineering Industries Pvt. Ltd. | G-516 to 518, Road No-9F,Vishwakarma Industrial Area null | Jaipur | 302013 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Sunny Sharma Sharma Electric Jaipur | Sharma Electric Works | Checked the Rccb found nuetral burnt , Hence no replacement given to customer. Email : id not provided by customer. | Repair |  | 8- Service Completed | 2023-09-15 17:05 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11259303 | 104033528 | 2023-09-14 17:07 | 2023-09-14 |  | 2023-09-14 16:23 | IH14000100 | IH14000100 | IH14000100 |  | Wiser installation request ¦ Mr. Shubham Saraf Kindly raise the wiser installation request for the below site. Installation should be done on Saturday ? 16th Sep. Mr. SHUBHAM SARAF, 29A, ORPHANGE GAUNG ROAD, KOLKATA-700023 Ph ? 9830918350 Thanking you, Shivaji Singh 4 Channel Automation Relay---5 nos 1 Channel Curtain Controller----2 nos Smart Doorbell---1 pc 2 Channel Dimmer---9 pcs IR controller---1 pc Automation Gateway (CAM ID)--1 pc | 2023-09-14 | 2023-09-21 11:18 | No | Commercial Action - Sales | SHUBHAM SARAF | 29A, ORPHANGE GAUNG ROAD, | Kolkata | 700023 | West Bengal | India FS ED&I CSP East Team SREYAM SERVICES BHATPARA | AMIT BHATTACHARYA_SREYAM SERVICES BHATPARA | Sreyam Services(8513) | AFTER SITE VISIT 6 NOS WISER RELAY SUCCESSFULLY INSTALLED CHACK FOUND OK. | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-21 11:22 |  |  | 20 | INR | 20 | ENM HOME DISTRIBUTION
WO-11259411 | 104035926 | 2023-09-15 10:46 | 2023-09-14 |  | 2023-09-14 17:13 | 5085EDLW-PW | 5085EDLW-PW | 5085EDLW-PW |  | Dear Sir, "Greeting From Eco Power Solution" Please Attend the following complaint. Name :- JTL INFRA LIMITED Address :- VIJAY SINGLA, 105 SECTOR-28A, CHANDIGARH-160002 Contact number :- 9878922199 Contact number :- 83600 64397 Complaint :- 5085EDLW-PW - 1 PCS Problem :- This item is not working properly. Kindly attend the complaint on priority basis. Attached Sale invoice AND PURCHASE Thanks & Regards ASHISH KUMAR ECO POWER SOLUTIONS (Sister Concern of M/s Automation Systems Ludhiana) Cabin No. 1, 90-C, Shakti Enclave Near Toor Complex, Dugri Road Ludhiana-141002 PUNJAB Virus-free.www.avast.com | 2023-09-14 | 2023-09-16 16:26 | No | Warranty | JTL INFRA LIMITED | VIJAY SINGLA, 105 SECTOR-28A, null | Chandigarh | 160002 | Chandigarh | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Vinod Kumar_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the EDLT switch found not power up. Hence faulty replaced. 5085EDLW-PW - 1 Nos. email : shivam2948@gmail.com | Repair |  | 8- Service Completed | 2023-09-16 16:29 |  |  | 20 | INR | 20 | ENM HOME DISTRIBUTION
WO-11296144 | 104217572 | 2023-09-23 14:53 | 2023-09-22 |  | 2023-09-22 17:43 | TM241CE24T | TM241CE24T | TM241CE24T |  | Dear Sir, We are facing a problem in plc Reference No. TM241CE24T Serial No. 8B22510001479 at our site. Please arrange the expert at site & diagnose the problem. Problem Type ? Not Powering Up Customer Address : SQUARE 'A' CONTROLS & AUTOMATION PLOT NO.20,RAMNEEK INDUSTRIAL ESTATE, VILLAGE DUGRI,TEH.PAYAL,DISTT. LUDHIANA - 141421 Contact Person : Mr. SARABJEET Contact Number : 09501340042 We are requesting you to please solve the problem on priority basis Thank You, Munish Sharma Manager Purchase & Materials ¦ Automation Systems ¦ System Integrator of Schneider Electric ¦ 0161-4613111 ¦ +91 9803018933 munish.s@automationsystems.org http://www.automationsystems.org Address: # 291, Guru Nanak Market, Near Giaspura Railway Crossing, Focal Point, Ludhiana-141010 (PB) | 2023-09-22 | 2023-09-29 10:57 | No | Warranty | SQUARE A CONTROLS & AUTOMATION | PLOT NO.20, RAMNEEK INDUSTRIAL ESTATE,VILLAGE - DUGRI, TEHSIL - PAYAL | LUDHIANA | 141421 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | checked the PLC found not power up. Hence faulty, replaced. TM241CE24T - 1 Nos. Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-29 11:01 |  |  | 25 | INR | 25 | Industrial Automation Ops
WO-11264601 | 104056119 | 2023-09-15 16:06 | 2023-09-15 | As per sr. no. product in warranty raise ZVO for replacement. | 2023-09-15 13:14 | X1001WH_N | X1001WH_N | X1001WH_N |  | POWER PRODUCT COMPLAIN MR. YOGESH BORDER 58-AYODHYA SOC, AT POST -VALAK, KAMREJ ROAD, SURAT 2 Contact Person at Site : Name & Mobile No. YOGESHBHAI-9913003873 Alternate Mobile No : 9825339456 3 Contact Person at Site - Email Address** 4 Product Issue Type (Please select from drop down of column C-9) 5 Are you ready to troubleshoot the issue remotely ? Yes/NO. If Yes, Our technical support engineer will call back to troubleshoot the issue remotely. 6 Defective Product Model/Part No (Pls refer FAQ sheet ) X1001 WH - 2 NO. 7 Nature of Defect* - Defects Video and Photographs 8 Shutdown availability if applicable YES 9 Photograph of product where Serial No/Batch Code or Date of Manufacturing printed - Please refer FAQ sheet to find the Batch code details on the products 10 Proof Of Purchase - Pease attach SE*** Authorised Partner Invoice soft copy along with this check list DATE : 14-3-2022 INVOICE NO -9240 | 2023-09-15 | 2023-09-19 01:17 | No | Warranty | Yogesh Bodder | 58 AYODHYAPURAM SOC PART 1 VALAK PATIA KAMREJ SURAT ROAD null | Surat | 395006 | Gujarat | India FS ED&I CSP West Team VARDHAMAN ELECTROSOFT Vadodara | MAHENDRA SINGH VARDHAMAN ELECTROSOFT Vadodara | VARDHAMAN ELECTROSOFT | We visited site and check the 6A, 16A switch .I checked the Equipment and found that there is pole to pole continuity and ON/OFF stuck issue | Repair |  | 9- Service Validated | 2023-09-18 16:18 | =S= Consig Fill up 226064590 |  | 40 | INR | 40 | ENM HOME DISTRIBUTION
WO-11264629 | 104055969 | 2023-09-15 16:03 | 2023-09-15 | As per sr. no. product in warranty raise ZVo for replacement. | 2023-09-15 13:28 | IN8444/16(BZ) | IN8444/16(BZ) | IN8444/16(BZ) |  | Checklist for the Registration of Service Request Sr. No Particulars Doc. Ref :- SE/CCC/002/V0.1 1 MR. LUCIA MARKETIN 424, CLASSIC COMPLEX, OPP AV SONS, PARLE POINT, SURAT NR. RAM CHOWKE, MOTA VARACHHA, 2 Contact Person at Site : Name & Mobile No. PRATIK SHAH Alternate Mobile No : 9825339456 3 Contact Person at Site - Email Address** 4 Product Issue Type (Please select from drop down of column C-9) 5 Are you ready to troubleshoot the issue remotely ? Yes/NO. If Yes, Our technical support engineer will call back to troubleshoot the issue remotely. 6 Defective Product Model/Part No (Pls refer FAQ sheet ) IN8444/16- 1 NO. 7 Nature of Defect* - Defects Video and Photographs 8 Shutdown availability if applicable YES 9 Photograph of product where Serial No/Batch Code or Date of Manufacturing printed - Please refer FAQ sheet to find the Batch code details on the products 10 Proof Of Purchase - Pease attach SE*** Authorised Partner Invoice soft copy along with this check list DATE OF PURCHASE - 8-3-2022 INVOICE NO-138 11 Name & phone No: of person registering the Service Request PRATIK -9825339456 All fields are mandatory. Free of cost service visit subjected to warranty policy of the product and contract between Schneider Electric and buying party . Warranty will be check either by serial no/Batch code/DOM printed on the product or date of invoice of our authorised partner /Schneider Electric direct invoice or Contract . Warranty policy may be change product to product or contract with the customer.* Kindly share defect symptoms instead of "Not working", Please share the link of large files(product photoes or videoes) ** End user will receive a survey asking feedback on service SE*** - Schneider Electric Please fill above details and send this sheet to customer care, Customer care contact link is give below https://www.se.com/in/en/work/support/customer-care/contact-schneider-electric.jsp Please mention Service Request as key word and Product Name in email subject line e.g for Masterpact NW ACB Service Request - Service Request for Masterpact NW Our web site :- https:+C16+A2:C22+A1:C22 -- For Lucia Marketing Pratik shah Cont.-9825339456 | 2023-09-15 | 2023-09-18 16:35 | No | Warranty | Lucia Marketing | 424, Classic Complex, Opp A.V. Sons, Parle Point, City Light Town, Athwa, Surat | Surat | 395007 | Gujarat | India FS ED&I CSP West Team VARDHAMAN ELECTROSOFT Vadodara | MAHENDRA SINGH VARDHAMAN ELECTROSOFT Vadodara | VARDHAMAN ELECTROSOFT | As per our site visit we found that Zencelo product 16A, 2 gang Switch Bush found broken . so it's not working properly and some time it's stuck. | Repair |  | 9- Service Validated | 2023-09-18 16:41 | =S= Consig Fill up 226061174 |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11264849 | 104061718 | 2023-09-15 16:06 | 2023-09-15 |  | 2023-09-15 14:43 | UNS61SW1M_GY | UNS61SW1M_GY | UNS61SW1M_GY |  | Dear Sir, Mr. Mohammad Arif ji 289 OFFICER CAMPUS VAISALI NAGAR Mr. Mohammad Arif ji 8058514514 Product :UNS61SW1M GY -13, UNS6SK3PMS-GY-3NOS, EZ9F71463=1 NOS UNS6BPL2M-1 NOS, UNS4STFAN1MGY-1NOS, EZ9S66463-1NOS, UNS161SW1M.GY -5 NOS not working -- *WITH REGARDS-* Sarabjit Singh SHARMA ELECTRIC WORKS I CHANDIGARH I ADMIN. AUTH. SERVICE & SPARES DEALER : CROMPTON GREAVES & SCHNEIDER ELECTRIC INDIA* Tele FAX 0172-4629871 E MAIL : complaints@sharmaelectricworks.com * Address : PLOT NO. 279, GF, INDUSTRIAL AREA,* *PHASE-II, CHANDIGARH-160002 , Website : www.sharmaelectricworks.com* * | 2023-09-15 | 2023-09-16 12:13 | No | Warranty | Mohammad Arif ji | 289 officer-s campus vaishail nagar | Jaipur | 302021 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | Checked the switch found not working, Hence faulty replaced. UNS61SW1M_GY - 13 nos UNS6SK3P2M_GY - 3 nos UNS6BPL2M_GY -1 nos UNS4STFAN1M_GY - 1 nos UNS161SW1M_GY - 5 nos Email : | Repair |  | 8- Service Completed | 2023-09-19 12:17 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11264982 | 104060701 | 2023-09-16 11:47 | 2023-09-15 |  | 2023-09-15 15:35 | X1001WH_N | X1001WH_N | X1001WH_N |  | PROBLEM- ON/OFF ISSUE Dear sir, Model - X1001WH Serial no. - 23121L Problem- On/Off issue So plzz dispute the service engineer to check the switches and resolve the issue as soon as possible Coustmer name - Darshil rastogi Contact person - Darshil rastogi Contact no. - 9984094777 Address - 3/110 a, vishnupuri, kanpur 208002 | 2023-09-15 | 2023-09-30 13:49 | No | Warranty | Darshil Rastogi | 3/110, A Vishnupuri , | Kanpur | 208002 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Aman Khare_Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found switches having on/off issue , so we replaced. | Repair |  | 8- Service Completed | 2023-09-30 13:52 |  |  | 115 | INR | 115 | ENM HOME DISTRIBUTION
WO-11265322 | 104064892 | 2023-09-16 16:16 | 2023-09-15 |  | 2023-09-15 18:13 | IH14000100 | IH14000100 | IH14000100 |  | Dear Team, One of the relay replaced of customer is still not working. Kindly contact with customer and arrange a technician visit at the site. 1. Customer Name : Mr. Manav Dhawan 2. Customer Address : House no - 91, Model Town , ambala city, 134003 3. Installation Type : Done 4. Product : A) Wiser Home Automation Relay 4 channel : 01 No 5. Contact Number : +91 89299 99998 6. Site Status: Automation Not working Regards Pardeep kumar Schneider Electric Mohali M: 8360361651Sent from Yahoo Mail on Android ----- Forwarded message ----- From: "Pardeep Kumar" <engineerpardeepkumar@yahoo.com> To: "customercare.in@se.com" <customercare.in@se.com> Cc: "Umesh RAINA" <umesh.raina@se.com>, "Ramakanth Kumathe" <ramakanth.kumathe@se.com> Sent: Tue, 29 Aug 2023 at 19:00 Subject: Immediate technician visit, automation not working: Mr. Manav Dhawan, Ambala Dear Team, Wiser home automation is not working at customer site. According to customer all relays stopped working. The lights of his house is unable to operate with switch and mobile. Kindly consider this as a special emergency case and arrange an immediate technician visit. The details of customer and copy of bill is attached below. 1. Customer Name : Mr. Manav Dhawan 2. Customer Address : House no - 91, Model Town , ambala city, 134003 3. Installation Type : Done 4. Product : A) Wiser Home Automation Relay 4 channel : 05 No Gateway: 01 5. Contact Number : +91 89299 99998 6. Site Status: Automation Not working Note: Please intimate us before visit to the site. Regards Pardeep kumar Schneider Electric Sr. Sales Executive Mohali M: 8360361651 Sent from Yahoo Mail on Android | 2023-09-15 | 2023-09-16 16:17 | No | Warranty | MANAV MANAV | 91 no Model Town , | Ambala | 134003 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Karnail Singh Sharma Electric Chandigarh | Sharma Electric works(1003) | checked the relay found working ok. Email : id not provided by the customer. | Repair |  | 8- Service Completed | 2023-09-16 16:22 |  |  | 55 | INR | 55 | ENM HOME DISTRIBUTION
WO-11267730 | 104066029 | 2023-09-16 15:28 | 2023-09-17 |  | 2023-09-16 10:13 | IH14000100 | IH14000100 | IH14000100 |  | Dear Sir/Madam, My 4 channel relay is malfunctioning. Pls get it fixed asap. Thanks Shipra Jain 7011335645 ---------- Forwarded message --------- From: Shipra Jain <jain.shipra1975@gmail.com> Date: Mon, 13 Feb, 2023, 9:45 pm Subject: Re: Smart door bell not working [ ref:_00DA0abSm._5008V1YDj6K:ref ] To: Schneider Electric Customer Care <customercare.in@schneider-electric.com> On Mon, 13 Feb, 2023, 7:09 pm Schneider Electric Customer Care, <customercare.in@schneider-electric.com> wrote: Dear Team, Greetings from Schneider Electric! Please share the invoice copy for warrant validation along with the model ref or few images to identify the model from our end. Regards, Abhijit Sarkar Customer Care Centre ¦ Schneider Electric India ¦ Toll Free: 18001030011 / 18004254272 / 18004194272 ¦ Email:Customercare.in@schneider-electric.com ¦ Site: www.schneider-electric.com " Still need help? Try Chat ( https://www.se.com/in/en/ ) with Us" Schneider Electric India ¦ Global Specialist In Energy Management --------------- Original Message --------------- From: [jain.shipra1975@gmail.com] Sent: 13/2/2023 2:47 pm To: customercare.in@schneider-electric.com Subject: Smart door bell not working [External email: Use caution with links and attachments] Dear Sir / Madam, I hv purchased your smart door bell in September 2022 . My door bell is not working since yesterday. Pls send someone to get it fixed. My registered number is 7011335645. IH14000100 Thanks & Regards Mrs Shipra Jain House No. 15 B Chattarpur Mini farms Chattarpur, New Delhi 110074 No Attachments linked to the email ref:_00DA0abSm._5008V1YDj6K:ref | 2023-09-16 | 2023-09-17 09:30 | No | Warranty | Shipra Jain | House No. 15 B Chattarpur Mini farms Chattarpur | Delhi | 110074 | Delhi | India FS ED&I CSP North Team Seamtek International Pvt. Ltd. GHAZIABAD | Satish Raika Seamtek International Pvt. Ltd. GHAZIABAD | Seamtek International Pvt. Ltd. | Following Wiser Components has been repaired: 4 channel relay: 1 qty. | Repair |  | 8- Service Completed | 2023-09-18 12:49 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11268837 | 104076886 | 2023-09-16 11:52 | 2023-09-16 |  | 2023-09-16 10:58 | A9N3P63C | A9N3P63C | A9N3P63C |  | Product : A9N3P63C MCB Sr No. D2304 DOM Jan 2023 Warranty Status : YES Knob Free / Loose Unable to switch ON Paras Hospital Plot number 324, DAL GATE SRINAGAR, Jammu and Kashmir. Pin 190001 Mr Sanjeev 7888560423 Sanjeevjk@rediffmail.com | 2023-09-16 | 2023-09-16 14:52 | No | Warranty | PARAS HOSPITAL | Plot number 324, DAL GATE | SRINAGAR | 190001 | Jammu and Kashmir | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Ram Ashish Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the MCB found Knob Free / Loose Unable to switch ON and MCCB found phase missing. Hence faulty replaced. A9N3P63C - 1 Nos. LV525302 - 1 Nos. email : sanjeevjk.2023@rediffmail.com | Repair |  | 8- Service Completed | 2023-09-16 22:48 |  |  | 7 | INR | 7 | ENM HOME DISTRIBUTION
WO-11269357 | 104076962 | 2023-09-16 12:00 | 2023-09-16 |  | 2023-09-16 11:28 | A9KR11463 | A9KR11463 | A9KR11463 |  | Product : A9KR11463 RCCB Sr No. DD2022W23-6-1 Yes With in Warranty Problem : Dolly Free / Not getting ON Automation & Control Unit -II ( Panal Manufacturing ) Industrial Area ,SIDCUL Pantnagar, 263153 Udham Singh Nagar, Uttarakhand. purchase@classicautomation.in Mr.Ganesh Kumar 7351008393 | 2023-09-16 | 2023-09-16 15:42 | No | Warranty | Automation & Control pvt ltd. | Unit -II ( Panal Manufacturing ) Industrial Area ,SIDCUL Pantnagar null | Udham Singh Nagar | 263153 | Uttarakhand | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the RCCB found dolly free and MCCB found phase missing. Hence faulty replaced. A9N16258 - 1 Nos. LV516302 - 1 Nos. email : purchase@classicautomation.in | Repair |  | 8- Service Completed | 2023-09-16 22:46 |  |  | 5 | INR | 5 | ENM HOME DISTRIBUTION
WO-11269393 | 104076847 | 2023-09-16 16:13 | 2023-09-16 |  | 2023-09-16 12:58 | UNS61SW1M_WE | UNS61SW1M_WE | UNS61SW1M_WE |  | Hi, PFA, complaint registration details for a newly installed site for Unica switch Please send a technician to this site as soon as possible. Thanks & Regards, MJ Marketing 33/480, AM Building, Railway Station Road, Near Keloth Juma Masjid, Keloth, Payyanur - 670307 PH : 04985 209896, 9188 209896 Email : contact@mjmarketing.in "We know you have many choices in doing business and we THANK YOU for choosing us!" | 2023-09-16 | 2023-09-19 15:56 | No | Warranty | Ramachandran A T | Ayodhya Ramapuram Pazayangadi (p o), Near Ramapuram Vayanashala | Kannur | 670303 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found unica switchs action missing and struck issue unica 1way 3nos uns162sw2m 1nos uns6bpl2m 1nos replaced switchs working fine | Repair |  | 9- Service Validated | 2023-09-19 16:01 |  |  | 110 | INR | 110 | ENM HOME DISTRIBUTION
WO-11084151 | 103047609 | 2023-08-07 12:14 | 2023-08-07 |  | 2023-08-07 10:43 | MTN6215-5910 | MTN6215-5910 | MTN6215-5910 |  | DOP: 7/3/2023 MTN6215-5910 P: Showing error :- 0420 34 basement north avenue road punjabi bagh delhi -110026 9643446042 , 7210031684. | 2023-08-07 | 2023-09-28 16:09 | No | Warranty | In charge In charge | 34 basement north avenue road punjabi bagh | Delhi | 110026 | Delhi | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the Multi-touch pro KNX found physical ok. Give the input supply in the KNX showing 0420 Error. We replace the faulty Multi-touch pro with new. | Repair |  | 8- Service Completed | 2023-09-28 18:03 |  |  | 32 | INR | 32 | ENM HOME DISTRIBUTION
WO-11269440 | 104077179 | 2023-09-16 16:11 | 2023-09-16 |  | 2023-09-16 14:13 | E8331BPL1_DG | E8331BPL1_DG | E8331BPL1_DG |  | Dear team, Kindly arrange the site visit and solve the issue as soon as possible. 1 Name of Customer SHAHID MASH 2 Site Address KULIRATHARI ELETTIL, ELETTIL (PO) ELETTIL-PARAPPANPOYIL ROAD, ELETTIL KOZHIKODE - 673572 3 Name of Contact Person at Site SHAHID MASH 4 Contact Phone / Mob. No: 9447753481 5 Defective Product Details E8331BPL1_DG : 1 PCS 6 Nature of Defect Not working 7 Shutdown availability if applicable Yes 8 Warranty Status Under Warranty 9 Commissioned / Installed date Before Three Months 10 Serial No: or DOM of the Product 11 Name & Phone No: of Person Registering the Complaint LAN Marketing 8075581561 | 2023-09-16 | 2023-09-18 16:08 | No | Warranty | SHAHID MASH | KULIRATHARI ELETTIL, ELETTIL (PO) ELETTIL-PARAPPANPOYIL ROAD, ELETTIL | KOZHIKODE | 673572 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found avator bell switch some time working issue, checked that switch no issue observed bell switch working fine | Repair |  | 9- Service Validated | 2023-09-18 16:14 |  |  | 40 | INR | 40 | ENM HOME DISTRIBUTION
WO-11269476 | 104077128 | 2023-09-18 11:02 | 2023-09-16 |  | 2023-09-16 15:13 | E8334L2_WE_G8 | E8334L2_WE_G8 | E8334L2_WE_G8 |  | Dear team, Kindly arrange the site visit and solve the issue as soon as possible. -- Name of customer Ayisha Rayeez address Maraazi House Karthikapalli, Orkkatteri, Vadakara Kozhikode 673542 Contact person Ayisha Rayeez 8943816682 E8334L2_WE_G8 INVOICE DATE 24 JAN 2022 Thanks & RegardsLAN MARKETING 12/16 M-S Opp.Juma Masjid Areekode-Kondotty Road Chemrakkattur Pin-673639 Customer Care: 8304903103 | 2023-09-16 | 2023-09-20 15:12 | No | Warranty | Ayisha Rayeez | Maraazi House Karthikapalli, Orkkatteri, Vadakara | Kozhikode | 673542 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Rejilesh APSMarketingCompany Calicut | APS Marketing Company | visited this site found AvatarOn, 4 switches sparking issue, switchs clean done , working fine | Repair |  | 9- Service Validated | 2023-09-20 15:24 |  |  | 40 | INR | 40 | ENM HOME DISTRIBUTION
WO-11269500 | 104077566 | 2023-09-18 11:08 | 2023-09-16 | MCB Tripping issue | 2023-09-16 15:43 | A9N4P40C | A9N4P40C | A9N4P40C |  | Fwd: Faulty MCB A9N4P40C Nusiance tripping issue Pranav Mhetre, Procurement Specialist, Aditya Green Energy Private Limited, Block No. 1, Kapil Plaza, Near Udyog Bhavan, Signal Camp, Latur, Maharashtra - 413512 Mobile :- +91 7875882226 | 2023-09-16 | 2023-09-18 13:19 | No | Warranty | Aditya Green Energy Pvt. Ltd. Latur | Kapil Plaza, Near Udyog Bhavan, Signal Camp, Latur | Latur | 413512 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Sachin Jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the MCB Tripping issue. MCb is get tripped after 5 minutes. then we take trail . customer already new MCB fitted in system. So Problem observed in MCb. MCb needs to be replaced. So Required material : A9N4P40C- 01 nos | Repair |  | 9- Service Validated | 2023-09-18 16:52 | =S= Consig Fill up 226064550 |  | 300 | INR | 300 | ENM HOME DISTRIBUTION
WO-11269508 | 104077474 | 2023-09-16 18:43 | 2023-09-16 |  | 2023-09-16 15:58 | A9KF71263 | A9KF71263 | A9KF71263 |  | Dear sir / madam, We have purchased 63A DP MCB (A9KF71263) - 1No (SCREW TIGHTING PROBLEM) from M/s. Maiyar Techno Systems. Wide their invoice no: 4267 dated 13.09.2023. We are facing Problem with Brand new Mcb. We request you to send your service person to rectify/replace at the earliest to our Factory located in below address. Kindly do the needful at the earliest. Note:- Attached Invoice Copy & Mcb Images FYR. ?Invoice Date 13 09 2023 Address :- Rampo controls # 19-20, "Ram's Techno Tower" Rajagopalanagar Main Road, 7th Main, Opp: Nagalingeshwara Temple, Between Rajagopalanagar Police Station & Peenya II stage Bus stand, Bangalore-560058 phone: +91 7899411592 phone: 080 - 28360993 web: www.rampocontrols.com With Regards, B.Naveen Kumar RampoControls. +91 7899411592. 080 28360993. | 2023-09-16 | 2023-09-22 14:33 | No | Warranty | Rampo controls | # 19-20, "Ram's Techno Tower" Rajagopalanagar Main Road,7th Main, Opp: Nagalingeshwara Temple, Near Rajagopalanagar Police Station, Bangalore - | Bangalore | 560058 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | MANOJ GANESAN SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported mcb, the problem found was screw not tightening issue. So we had arranged for the replacement. | Repair |  | 9- Service Validated | 2023-09-22 14:39 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11269525 | 104077379 | 2023-09-16 17:05 | 2023-09-16 | Switch not operating | 2023-09-16 16:33 | X1001WH_N | X1001WH_N | X1001WH_N |  | Dear Sir, Pl issue complaint no. 1. Name of Customer: dinesh kulkarni 2. Site Address: - I 1202, greens Society 3. Name of contact person at site :- dinesh kulkarni 4. Contact Phone / Mob. No: - 8879159003 5. Defective product details:-X 1001 WH 6. Product Make:- Opale 7. Nature of Defect:switch not working 8. Shutdown availability if applicable :nil 9. Serial No: or DOM of - 10. Dealer Name /OA no. /Invoice Details: - 10yrs Warranty 11. Commissioned / Installed date:- NIL 12. Name & phone No: of person registering the complaint: Mr. dinesh kulkarni Get Outlook for Android | 2023-09-16 | 2023-09-18 11:14 | No | Warranty | Dinesh Kulkarni | Building I, 1202, greens Society, Dange Chowk, PCMCBuilding I, 1202, greens Society, Dange Chowk, PCMC | Pune | 411057 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Kunal jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the switch found that the Switch is not working it's found broken from inside the board . so this problem is not repairable.So switch Needs to be replaced, Required Material : X1001WH - 06 nos. we arranged the material from our stock and replaced it. | Repair |  | 9- Service Validated | 2023-09-18 15:49 | =S= Consig Fill up 226053356 |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11269558 | 104077731 | 2023-09-18 13:03 | 2023-09-16 |  | 2023-09-16 17:43 | E8315_6_DG | E8315_6_DG | E8315_6_DG |  | Dear Team Pls find the attached invoice copy for reference. Invoice number 11 05 2023 Atul Pandey ¦ Shree Krishna Sec Auto Pvt. Ltd. ¦ New Delhi Mobile: +91-74080-62123 Phone: +91-11-45578643/44 Telefax ¦ Email: accounts@shreekrishnacorp.com ¦ Site: www.shreekrishnacorp.com ¦ *** Please consider the environment before printing this e-mail *** On Saturday, September 16, 2023 at 04:37:53 PM GMT+5:30, Mail2Case India <customercare.in@schneider-electric.com> wrote: Hello sir. We have received a complain regarding E8315_6_DG . we would like to inform You that the serial number f the product is missing, For filing the complain we would be requiring either the serial number of the product or the invoice copy of the product. we request you to please provide the above details. Thank You Regards Ankur Singh --------------- Original Message --------------- From: [accounts@shreekrishnacorp.com] Sent: 16/9/2023 4:01 pm To: customercare.in@schneider-electric.com Subject: complain Register (Switch Socket) Dear Team Pls complain register regarding of E8315_6_DG Site Address Mr Rakesh Address- 140 Rajdhani Enclave New Delhi - 110034 Cont Per - Mr Vipin - 8800703594 Atul Pandey ¦ Shree Krishna Sec Auto Pvt. Ltd. ¦ New Delhi Mobile: +91-74080-62123 Phone: +91-11-45578643/44 Telefax ¦ Email: accounts@shreekrishnacorp.com ¦ Site: www.shreekrishnacorp.com ¦ *** Please consider the environment before printing this e-mail *** No Attachments linked to the email thread::17z9dB04e5WFP5yyH4qODj4:: | 2023-09-16 | 2023-09-23 17:28 | No | Warranty | Vipin Vipin | 140 Rajdhani Enclave | New Delhi | 110034 | Delhi | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the sockets and found sockets switch have dolly free issue. We replace the faulty sockets with new. | Repair |  | 8- Service Completed | 2023-09-23 17:32 |  |  | 34 | INR | 34 | ENM HOME DISTRIBUTION
WO-11269594 | 104076942 | 2023-09-17 00:39 | 2023-09-16 |  | 2023-09-16 18:23 | UNS616SK2M_GY | UNS616SK2M_GY | UNS616SK2M_GY |  | Dear Sir, Please find the attachment and do the needful. Name of Customer VENUGOPAL Site Address RAJEEVAM MUTHUKULAM P O KAYAMKULAM 690506 Alappuzha Name of contact person at site VENUGOPAL Contact Phone / Mob. No: 9446837404, '9526082492 Defective product details SCHNEIDER UNICAPURE 6/16AMP SOCKET(UNS616SK2M_GY) 2 nos SCHNEIDER UNICAPURE 1WAY SWITCH(UNS61SW1M_GY) 2 nos Nature of Defect not working Shutdown availability if applicable Distributor Name,Invoice # & Date hhys inframart Serial No: or DOM of the product Name & phone No: of person registering the complaint Joseph ouseph 9526082492 Invoice Date : 01 JUN 2023 Regards, Joseph ouseph | 2023-09-16 | 2023-09-23 12:44 | No | Warranty | VENUGOPAL JI | RAJEEVAM MUTHUKULAM P O KAYAMKULAM | Alappuzha | 690506 | Kerala | India FS South2 ED&I CSP PrinterPeople Cochin | Renjith PR PrinterPeople Cochin | PRINTER PEOPLE-COCHIN | UNS61SW1M_GY- 2 nos fault.. replacement send to customer location for onsite | Repair |  | 8- Service Completed | 2023-09-23 12:46 |  |  | 1 | INR | 1 | ENM HOME DISTRIBUTION
WO-11276726 | 104084014 | 2023-09-18 13:04 | 2023-09-18 |  | 2023-09-18 11:13 | UNS61SW1M_WE | UNS61SW1M_WE | UNS61SW1M_WE |  | Name of Customer Fasil ck Site Address Ck house Edakkara Malappuram dt , pin : 679331 Kerala. Name of contact person at site Fasil ck Contact Phone / Mob. No: 9446159141 Defective product details Unica pure switches Nature of Defect Switches complaint Shutdown availability if applicable yes Warranty status Under Warranty Commissioned / Installed date 6 months Serial No: or DOM of the product Name & phone No: of person registering the complaint Muhammed Ali - 8606739993 | 2023-09-18 | 2023-09-20 14:20 | No | Warranty | Fasil CK | Ck house Edakkara | Malappuram | 679331 |  | India FS South2 ED&I CSP APSMarketingCompany Calicut | PRAMEESH P.S APSMarketingCompany Calicut | APS Marketing Company | visited this site found unica 5st fan regulator speed variation issue UNS5STFAN replaced 1nos problem solved | Repair |  | 9- Service Validated | 2023-09-20 14:23 |  |  | 75 | INR | 75 | ENM HOME DISTRIBUTION
WO-11276772 | 104084521 | 2023-09-18 14:15 | 2023-09-18 |  | 2023-09-18 11:43 | A9N16256 | A9N16256 | A9N16256 |  | RCCB 40 MPR NOT WORKING Model number : A9N16256 Serial Number : DD2023W25-2-1 3606480498558 Shalimar Iridium Vibhuthikand Gomtinagar Near by Indra Gandhi Prathistan Gate 2 Lucknow 226010 Uttar Pradesh India 919335706818 | 2023-09-18 | 2023-09-23 15:09 | No | Warranty | Reliance Digital | Shalimar Iridium Vibhuthikand Gomtinagar Near by Indra Gandhi Prathistan Gate 2 | Lucknow | 226010 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Abhishek Patel Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found RCCB having dolly free issue so we replaced. | Repair |  | 8- Service Completed | 2023-09-23 15:28 |  |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-11276864 | 104086303 | 2023-09-19 14:48 | 2023-09-18 |  | 2023-09-18 12:43 | A9N1P63C | A9N1P63C | A9N1P63C |  | Updated contact number: 9571703015 Model number : A9N1P63C Serial number : 3606480497469 Invoice Date : january 2023 | 2023-09-18 | 2023-09-19 14:49 | No | Warranty | Krishna Electricals | Shop no. 1, Gali no. 4A, Krishna Colony Opp. sec 25, | Faridabad | 121004 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mcb found dolly free, Hence faulty replaced. A9N1P63C - 1 nos email : id not provided by customer. | Repair |  | 8- Service Completed | 2023-09-19 16:37 |  |  | 45 | INR | 45 | ENM HOME DISTRIBUTION
WO-11276907 | 104085526 | 2023-09-19 17:17 | 2023-09-18 |  | 2023-09-18 13:13 | A9N2P25C | A9N2P25C | A9N2P25C |  | Dear Sir, We have supplied Acti-9 MCB at following address : Wahi & Sons ( Mr.Ved - Mobile Number - 9891462280) D-5 , Pushpanjali Forms Bijwason New Delhi - 110061 Nature of Complaint : 25A DP MCB - A9N2P25C - 1 Pcs not working. Invoice attached for your Ref. Invoice date 18 July 2023 Thanks & Regards Pardeep sachdeva Mobile No : 0-9899806665 Shubham Electricals & Consultants Shop No 166, Vayapar Sadan, Opposite Groovie Hotel, MG Road Gurgaon-122001. Ph- 0124- 4015075 | 2023-09-18 | 2023-09-19 17:20 | No | Warranty | Wahi & Sons | D-5 , Pushpanjali Forms Bijwason null | New Delhi | 110061 | Delhi | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mcb found phase missing, Hence faulty replaced. A9N2P25C - 1 nos Email : id not provided by customer. | Repair |  | 8- Service Completed | 2023-09-20 11:04 |  |  | 20 | INR | 20 | ENM HOME DISTRIBUTION
WO-11295720 | 104211902 | 2023-09-22 15:30 | 2023-09-22 | Switches not working | 2023-09-22 14:43 | IN8401_16 | IN8401_16 | IN8401_16 |  | Dear Sir, Pl issue complaint no. 1. Name of Customer: Vishwas Chaudhari 2. Site Address: - flat no- 1102 Aishwaryam Comfort, Chinchwad - Akurdi Link Rd, opposite Yuvraj Motors, Maharashtra 411035 3. Name of contact person at site :- Vishwas Chaudhari 4. Contact Phone / Mob. No: - 95117 57305 5. Defective product details:-IN8401 6. Product Make:- Zencelo 7. Nature of Defect: Switch not working 8. Shutdown availability if applicable :nil 9. Serial No: or DOM of - 22012L 10. Dealer Name /OA no. /Invoice Details: - In warranty 11. Commissioned / Installed date:- NIL 12. Name & phone No: of person registering the complaint: Mr.Vishwas Chaudhari-95117 57305 Invoice Date : 22 november 2022 Radhika Cables and switch gear | 2023-09-22 | 2023-09-22 16:04 | No | Warranty | Vishwas Chaudhari | flat no- 1102 Aishwaryam Comfort, Chinchwad - Akurdi Link Rd | Pimpri-Chinchwad | 411035 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Kunal jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the Switches not working. it;s found stuck not changing contact. switches stuck again & again. this problem is not repairable. So Switches needs to be replaced. Required Material : IN8401- 01 nos | Repair |  | 9- Service Validated | 2023-09-22 16:18 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11295765 | 104211756 | 2023-09-22 17:06 | 2023-09-22 |  | 2023-09-22 14:57 | MTN6725-0004 | MTN6725-0004 | MTN6725-0004 |  | RE: Issues in Dali Gateway [ thread::cU5v332YcOet594BUsx-6T4:: ] Approved by Marketing 1 Company Name & Complete Address with pin code - Where product is installed 729A, DLF Camellias, Phase -5 Gurgaon , Haryana 2 Contact Person at Site : Name & Mobile No. Harshit - 8218612352 Alternate Mobile No : Nariender - 7807652063 3 Contact Person at Site - Email Address** harshit.sharma@iiiot-infotech.com 4 Product Issue Type (Please select from drop down of column C-9) Software/communication Issue 5 Are you ready to troubleshoot the issue remotely ? Yes/NO. If Yes, Our technical support engineer will call back to troubleshoot the issue remotely. No 6 Defective Product Model/Part No (Pls refer FAQ sheet ) MTN6725-0004 7 Nature of Defect* - Defects Video and Photographs Last seen were not recovered when power was failed 8 Shutdown availability if applicable 9 Photograph of product where Serial No/Batch Code or Date of Manufacturing printed - Please refer FAQ sheet to find the Batch code details on the products Please send soft compies along with this check list. 10 Proof Of Purchase - Pease attach SE*** Authorised Partner Invoice soft copy along with this check list Please send soft compies along with this check list. 11 Name & phone No: of person registering the Service Request Suraj Gaur - 9990739248 | 2023-09-22 | 2023-09-26 18:22 | No | Warranty | IIIOT-Infotech | 729A, DLF Camellias, Phase -5 | Gurgaon | 122002 | Haryana | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the gateway and found gateway have communication issue. We handover new gate way. | Repair |  | 8- Service Completed | 2023-09-26 18:31 |  |  | 54 | INR | 54 | ENM HOME DISTRIBUTION
WO-11277170 | 104088540 | 2023-09-19 16:09 | 2023-09-18 |  | 2023-09-18 14:58 | A9N4P63C | A9N4P63C | A9N4P63C |  | Dear sir A product schneider ie mcb is free.. Pls send for replacement. Thanking you Haryana electricals 1d 13 bp nit fbd M-9810225303 | 2023-09-18 | 2023-09-19 16:13 | No | Warranty | Haryana Electricals | 1B 13 BP NIT Faridabad Near 12 Chowk 121001 | FARIDABAD | 121001 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mcb found dolly free, Hence faulty replaced. A9N4P63C - 1 nos Email : id not provided by cusotmer. | Repair |  | 8- Service Completed | 2023-09-19 17:27 |  |  | 45 | INR | 45 | ENM HOME DISTRIBUTION
WO-11295848 | 104214431 | 2023-09-22 15:34 | 2023-09-22 | switch not working | 2023-09-22 15:28 | IN8444_16_BZ | IN8444_16_BZ | IN8444_16_BZ |  | Switch not working for E-704 Aishwaryam Comfort Gold 1. Name of Customer: I Sayyed 2. Site Address: - flat no- 704Aishwaryam Comfort Gold, Chinchwad - Akurdi Link Rd, opposite Yuvraj Motors, Maharashtra 411035 3. Name of contact person at site :- I Sayyed 4. Contact Phone / Mob. No: - 77994 09095 5. Defective product details:-IN8401,IN8444/16 6. Product Make:- Zencelo 7. Nature of Defect: Switch not working 8. Shutdown availability if applicable :nil 9. Serial No: or DOM of - 21475L 10. Dealer Name /OA no. /Invoice Details: - In warranty 11. Commissioned / Installed date:- NIL 12. Name & phone No: of person registering the complaint: Mr.I Sayyed -77994 09095 Thanks, I Sayyed 7799409095 | 2023-09-22 | 2023-09-22 16:23 | No | Warranty | I Sayyed | flat no- 704 Aishwaryam Comfort Gold, Chinchwad - Akurdi Link Rd, opposite Yuvraj Motors, | Pune | 411035 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Kunal jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the Switches not working. it;s found stuck not changing contact. switches stuck again & again. this problem is not repairable. So Switches needs to be replaced. Required Material : IN8444/16- 01 nos | Repair |  | 9- Service Validated | 2023-09-22 16:32 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11277221 | 104085156 | 2023-09-19 16:24 | 2023-09-18 |  | 2023-09-18 15:23 | E8331D32N_DG_G8 | E8331D32N_DG_G8 | E8331D32N_DG_G8 |  | p.p1 margin: 0.0px 0.0px 0.0px 0.0px; font: 17.0px '.AppleSystemUIFont' span.s1 font-family: 'UICTFontTextStyleBody'; font-weight: normal; font-style: normal; font-size: 17.00px Dear team, My name is Shahid Akhtar and currently I am TSE in Chandigarh team. Past few days I got a complaint from my customer Mr. Rohit in Avatar 32A DP. The detais of the customer is - 1. The model reference no. of the product is E8331D32N_DG_G8 2. The name of the customer is Mr. Rohit. 3. Contact no. of the customer is 9896068751 / 9050225741 4. Address of the customer is Harish #127, Model Town, Ambala city, Pincode - 134103 Invoice number : 564 Invoice Date : 03/11/2022 I have attached all the documents related to this mail. Please find the documents attached to this mail. Please do the needful asap. Thank You & Best Regards, Shahid Akhtar (TSE, Schneider Electric India) | 2023-09-18 | 2023-09-23 15:34 | No | Warranty | Rohit Rohit | #127, Model Town | Ambala | 134103 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the grey avatar switch found not getting on/ off due to inside terminal is melted. Might be due to loose termination. Hence faulty replaced. E8331D32N_DG_G8 - 1 Nos. email : id not provided by the customer. | Repair |  | 8- Service Completed | 2023-09-23 15:36 |  |  | 55 | INR | 55 | ENM HOME DISTRIBUTION
WO-11295850 | 104212749 | 2023-09-22 17:15 | 2023-09-22 |  | 2023-09-22 15:28 | A9N16258 | A9N16258 | A9N16258 |  | Hello sir\mam. please find the attached file of invoice and details.1. Model number of the product Model No Serial No 1. A9N16258 237130411491 2. A9N16258 237130540407 3. A9N16258 237130411661 4. A9N16258 237131118459 5. A9N16258 237131118487 6. A9N16258 237130540440 7. A9N16258 237124129108 8. A9N16258 237124128965 9. A9N16258 237124128975 10. A9N16258 237131118551 11. A9N16258 237124128946 12. A9N16259 238123178185 13. A9N16258 2371305403692. Serial no of the product3. Invoice Details4. Complete site address with pin-code : 301, 3rd Floor, 1/18-B, Dream Land Building, Asaf Ali Road, Near SBI Bank, New Delhi 1100025. Contact person"s name and contact details : Arjun Singh , M: 9650128739.6. Email ID: mechatronicsasia@gmail.com Virus-free.www.avast.com On Thu, Sep 21, 2023 at 5:04?PM Mail2Case India <customercare.in@schneider-electric.com> wrote: Hello Sir/Mam.Greetings of the day.We have received your complain request , We would like to tell you that the details which you have sheared with us is not sufficient for filing the complain .So we request you that please share the mentioned details:1. Model number of the product2. Serial number of the product3. Invoice Details4. Complete site address with pin-code5. Contact person"s name and contact details6. Email IDThank YouRegards Ankur SinghSchneider ElectricRegards,Ankur SinghCustomer Care Centre ¦ Schneider Electric India ¦ Toll Free: 18001030011 / 18004254272 / 18004194272 ¦ Email:Customercare.in@schneider-electric.com ¦ Site: www.schneider-electric.com--------------- Original Message ---------------From: [mechatronicsasia@gmail.com]Sent: 21/9/2023 3:39 pmTo: customercare.in@schneider-electric.comSubject: RCCB repairing under warranty,DearSir, We have purchased Schneider RCCB from your vendors near about thirteen RCCB is not working and it is under warranty ,we attached photos of RCCB, please solve our problem ASAP, Thanks With thanks & Regard Arjun singh Mob. +91-9650128739, Office - 011-41050634 Mechatronics Asia 301, 3rd Floor,1/18-B,Dream Land Building Near SBI Bank, Asaf Ali Road, New Delhi-110002 Authorize Channel Partner for: Virus-free.www.avast.com Following attachments are linked to this email:1.WhatsApp Image 2023-09-21 at 3.37.46 PM.jpegthread::6loFEce3dkiz164ysu_9ZT4:: -- With thanks & Regard Pawan Kumar Saraswat Mob. +91-8447405356, Office - 011-41050634 Mechatronics Asia 301, 3rd Floor,1/18-B,Dream Land Building Near SBI Bank, Asaf Ali Road, New Delhi-110002 Authorize Channel Partner for: | 2023-09-22 | 2023-09-28 16:23 | No | Warranty | Arjun Singh | 301, 3rd Floor, 1/18-B, Dream Land Building, Asaf Ali Road | New Delhi | 110002 | Delhi | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the RCCB and found RCCB have dolly stay some time and some time not stay. We replace the faulty 3 RCCB with new. Some RCCB is burnt and terminal have spark so we reject the replacement. | Repair |  | 8- Service Completed | 2023-09-28 17:59 |  |  | 27 | INR | 27 | ENM HOME DISTRIBUTION
WO-11277299 | 104092883 | 2023-09-19 17:04 | 2023-09-18 |  | 2023-09-18 15:58 | A9N1P25C | A9N1P25C | A9N1P25C |  | 1pc MCB not working Model number A9n1p25c Serial number : D2146 Invoice date 19 june 2023 B34/680 Chandan Nagar, Ludhiana 141001 Vaneet Dhand 9779541396 | 2023-09-18 | 2023-09-19 17:06 | No | Warranty | Vaneet Dhand | B34/680 Chandan Naga | Ludhiana | 141001 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | checked the mcb found phase missing. Hence faulty, replaced. A9N1P25C - 1 Nos. Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-20 17:36 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11295939 | 104215095 | 2023-09-22 16:49 | 2023-09-22 |  | 2023-09-22 16:14 | IH14000100 | IH14000100 | IH14000100 |  | Hello team, Please look forward for this customer complaint regarding wiser gateway as they are facing problem to connect with internet . Please do the needful as soon as possible Here is the customer details Name :- Advaitha associates Number:- 9341221335 Address :- No 70,80 feet road, Banashankari 6th stage 3rd block, Bangalore -560062 Thank you Regards SHWETA Manager sales wiser Home & Distribution DivisionSchneider Electric M 7042314880MS TEAMS shweta2@se.comE MAIL shweta2@se.comCustomer Support Contact Us Schneider Electric India Pvt Limited3, 1, Millers Rd, Vasanth NagarBengaluru560051India Internal | 2023-09-22 | 2023-09-25 11:44 | No | Warranty | ADVAITHA ASSOCIATES | NO 76 80 FEET ROAD, BANASHANKARI 6TH STAGE 3RD BLOCK | Bangalore | 560062 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Mohammad Riyaz_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the reported wiser automation gateway, problem was gateway not operating in the customer mobile.so we resetted the gateway and installed , checked the operations found working ok. The same shown to the customer. There is no issue now. | Repair |  | 9- Service Validated | 2023-09-25 11:49 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11277334 | 104092174 | 2023-09-29 14:25 | 2023-09-18 |  | 2023-09-18 16:26 | IH101ZWIFI | IH101ZWIFI | IH101ZWIFI |  | New installation of wiser Home Automation: Mr. Ashish Arora mohali ear Team, Please install wiser home automation at customer home. The details of customer and copy of bill is attached below 1. Customer Name : Mr. Ashish Arora 2. Customer Address : # 123, phase 2, Mohali 3. Installation Type : NEW 4. Product : Wiser Home Automation A) Automation Gateway : 01 B) 4 channel Relay : 08 C) curtain Relay : 04 5. Contact Number : +91 9216123123 (owner) Ritesh mishra(manager): +91 77101 01029 | 2023-09-18 | 2023-09-29 14:27 | No | Commercial Action - Sales | Ashish Arora | #123 Phase 2 | Mohali | 160002 | Punjab | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Ram Ashish Sharma Electric Chandigarh | Sharma Electric works(1003) | Installation sone. >4 channel Relay ( IH14000100) : 07 > curtain Relay : 04 >Automation Gateway (IH101ZWIFI) : 01 email : id not provided by the customer. | Commissioning & Installation | Start-up | 8- Service Completed | 2023-09-29 15:37 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11295972 | 104215711 | 2023-09-23 15:13 | 2023-09-22 |  | 2023-09-22 16:25 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Re: Installation of Smart Door Bell Kindly Install Wiser on urgent basis on below address Name- Hari shankar Sharma Address- 176A Shree ram Vihar Agra Road Jamdoli Jaipur 302031 Mobile no.- 8764003774 Invoice attached for your reference. | 2023-09-22 | 2023-09-23 15:15 | No | Commercial Action - Sales | Hari Sharma | 176A Shree ram Vihar Agra Road Jamdoli | Jaipur | 302031 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Sunny Sharma Sharma Electric Jaipur | Sharma Electric Works | Checked the vdp found working ok. Email : id not provided by customer . | Commissioning & Installation | Start-up | 8- Service Completed | 2023-09-23 15:20 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11277339 | 104091715 | 2023-09-19 14:40 | 2023-09-18 |  | 2023-09-18 16:28 | IN8401_16 | IN8401_16 | IN8401_16 |  | Dear Sir, Our customer is using Schneider zen celo switches and these switches are not working properly and creating operational issues. Material detail below. Pl Find Attached Invoices Copy 1. IN8401 (BZ) Total Switches 15 Nos. Kindly depute the service engineer at below address to resolve the issue. Address. DR. GURVINDER KAUR HOME NO. 711, PRATAP NAGAR DADABARI KOTA - 324009 (RAJ.) Contact Person. Mr.Mahendra Pal Singh ( 94144-30590 ) Invoice Date: 24-12-22 Invoice Number 4733 -- Thanks with regards, ARUN VIJAY 99280-17715 Power Controls Email:sales@powercontrolskota.com Web:http://www.powercontrolskota.com ¦ Address: F-236(A), Road No.5, Indraprastha Industrial Area, Kota,(rajasthan) India Pincode: 324005 P Before Printing Think About Environmental Responsibility! | 2023-09-18 | 2023-09-19 14:42 | No | Warranty | Mahendra Pal Singh | HOME NO. 711, PRATAP NAGAR DADABARI | KOTA | 324009 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | checked the switches found play problem . hence faulty, replaced. IN8401 - 3 Nos. IN8402 - 1 Nos. Email : id not provided by the customer. | Repair |  | 8- Service Completed | 2023-09-19 16:56 |  |  | 250 | INR | 250 | ENM HOME DISTRIBUTION
WO-11296035 | 104213333 | 2023-09-23 10:02 | 2023-09-22 |  | 2023-09-22 16:53 | MTN627814 | MTN627814 | MTN627814 |  | Company Name & Complete Address with pin code - Where product is installed FUTURE AUTOMATION SOLUTIONS First Floor, Nirman house, Opposite Dharmadev Developers, Beside Navrang pauva and food zone, Shyamal Cross Road, Shyamal-Prahladnagar Road, Satellite, Ahmedabad-380015 2 Contact Person at Site : Name & Mobile No. Saurav Dhanopiya - +91 9712927430 Alternate Mobile No : 3 Contact Person at Site - Email Address** logistics.fas2022@gmail.com 4 Defective Product Model/Part No (Pls refer FAQ sheet ) 1. MTN627814 (4 Nos) 2. E84751MS3B_WE ( 1 nos ) 5 Nature of Defect* - Defects Video and Photographs 1.HANG ISSUE 2. Not working 6 Shutdown availability if applicable 7 POP - SE Authorised Partner Invoice soft copy REXEL INDIA PRIVATE LIMITED - 2022/CIHR05169 8 Photograph of product where Serial No/Batch Code or Date of Manufacturing printed - Please refer FAQ sheet Attached 9 Name & phone No: of person registering the complaint Saurav - +91 97129 58014 | 2023-09-22 | 2023-09-25 15:25 | No | Warranty | Future Automation Solutions | Second Floor, Hani House | Ahmedabad | 380015 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Mistri Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physically ok. E84751MS3W13F SR NO : 2209 obsreved sensor not working. so we give the supply but sensor not geting on. so may be its a internal problem so free replacement. MTN62814 SR NO : 2221 observed problem and key switching problem 4 nos so free replacemnet. | Repair |  | 9- Service Validated | 2023-09-25 15:26 | =S= Consig Fill up 226031718 |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11277405 | 104093156 | 2023-09-18 17:51 | 2023-09-18 |  | 2023-09-18 17:13 | UNS61SW1M_WE | UNS61SW1M_WE | UNS61SW1M_WE |  | Dear team, Kindly arrange the site visit and solve the issue as soon as possible. 1 Name of Customer NAVAS CHOLA 2 Site Address CHOLA MANZIL UGRAPURAM PO KARIPARAMB MALAPPURAM - 673639 3 Name of Contact Person at Site NAVAS CHOLA 4 Contact Phone / Mob. No: 9846703546 5 Defective Product Details UNS61SW1M_WE : 3 PCS UNS62SW1M_WE : 2 PCS UNSSKTLT2M_WE : 1 PCS 6 Nature of Defect Not working 7 Shutdown availability if applicable Yes 8 Warranty Status Under Warranty 9 Commissioned / Installed date Before Three Months 10 Serial No: or DOM of the Product 11 Name & Phone No: of Person Registering the Complaint LAN Marketing 9946185592 -- Thanks & RegardsLAN MARKETING 12/16 M-S Opp.Juma Masjid Areekode-Kondotty Road Chemrakkattur Pin-673639 Customer Care: 8304903103 | 2023-09-18 | 2023-09-19 16:44 | No | Warranty | NAVAS CHOLA | NAVAS CHOLA CHOLA MANZIL UGRAPURAM PO KARIPARAMB MALAPPURAM | Malappuram | 673639 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found unica 32dp switchs struck issue, dp switch clean done, its working fine | Repair |  | 9- Service Validated | 2023-09-19 16:47 |  |  | 45 | INR | 45 | ENM HOME DISTRIBUTION
WO-11296181 | 104218789 | 2023-09-26 10:52 | 2023-09-22 | NA | 2023-09-22 17:59 | UNS21USB1P1M_GY_N | UNS21USB1P1M_GY_N | UNS21USB1P1M_GY_N |  | Unica Pura UNS21USB1P1M_WEUSB Invoice date 24/september /2022 Designer Electrical Make money partment flat number 2B, VIP Bazar 1806 Luskar hut road, tegore park kOlkata 700039 8961011238 Rohit agarwal | 2023-09-22 | 2023-09-26 14:45 | No | Warranty | Rohit agarwal | Make money partment flat number 2B, VIP Bazar 1806 Luskar hut road, tegore park | kOlkata | 700039 | West Bengal | India FS ED&I CSP East Team B.D Electroservices Kolkata | KOUSHIK MONDAL_B.D Electroservices Kolkata | B.D Electroservices(500017330) | On received of ZVO material will delivered to customer. | Repair |  | 8- Service Completed | 2023-09-26 17:52 |  |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-11277414 | 104093068 | 2023-09-18 17:31 | 2023-09-18 |  | 2023-09-18 17:21 | A9KF71416 | A9KF71416 | A9KF71416 |  | Re: WO-11213633 from Schneider Electric Main Installed Product Name : A9KF71416 Main IP Serial Number : Work Order Reason:1] A9KF71416 - 01 SR.NO. DD2023-W20-2-8 REASON : HARDWARE PROBLEM 2] LC1E3210N5 - 01 SR.NO. 1023185 REASON : HARDWARE PROBLEM CUSTOMER NAME : Trimurti Electric Corporation 5, Shayam Chamber, Nr.Telephone Exchange, Veraval (Shapar) RAJKOT. - 360024 MO. 7600025375 | 2023-09-18 | 2023-09-19 09:47 | No | Warranty | Trimurti Electric Corporation | 5,Shyam Shopping Center,Opp.Rajdhani Cinema Veraval(Shapar) Rajkot | Rajkot | 360001 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | RAHUL PARMAR JKS Rajkot | JKS Engineering Co. | Check mcb on/off found ok.check mcb 1st poleopen found 1nos mcb replacement.check contactor on/off working ok.contactor coil workinf ok check contactor t3 thared not working change thared in rts matariyal contactor found ok | Repair |  | 9- Service Validated | 2023-09-19 09:52 | =S= Consig Fill up 226064591 |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11296192 | 104217812 | 2023-09-23 10:48 | 2023-09-22 |  | 2023-09-22 18:04 | UNS61SW1M_WE | UNS61SW1M_WE | UNS61SW1M_WE |  | COMPLAINT ANVAR KM KAKKATTIL ANVAR KM KANDIYIL HOUSE AROOR (PO), THEEKUNI KAKKATTIL (VIA), KAKKATTIL KOZHIKODE - 673507 ANVAR KM 9061792212 UNS61SW1M_WE : 3 PCS UNS32DP2M_WE : 1 PCS Not working Yes Under Warranty Before Three Months LAN Marketing 8075581561 | 2023-09-22 | 2023-09-25 15:28 | No | Warranty | ANVAR KM | KANDIYIL HOUSE AROOR (PO), THEEKUNI KAKKATTIL (VIA), KAKKATTIL | KOZHIKODE | 673507 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Rejilesh APSMarketingCompany Calicut | APS Marketing Company | visited this site found unica one way switch contact issue UNS61SW1M replaced problem solved | Repair |  | 9- Service Validated | 2023-09-25 15:28 |  |  | 60 | INR | 60 | ENM HOME DISTRIBUTION
WO-11277424 | 104092332 | 2023-09-18 17:47 | 2023-09-18 | As per sr. no. product in warranty raise ZVO for replacement | 2023-09-18 17:28 | A9N2P10D | A9N2P10D | A9N2P10D |  | Dear Sir/Madam Please Provide Complain number has per Attached Deta Checklist for Complaint Registration 1 Name of Customer M/S SUKHARAM ELECTRIC CORPORATION 2 Site Address 34, ROAD NO-6, NEW INDUSTRIAL ESTATE, B/H OF ALIDHRA, TV COMPOUND, UDHNA UDHYOGNAGAR, UDHNA, SURAT - 394210 Contact Phone / Mob. No: 9638725071 3 Name of contact person at site MR. Kiran Prajapati Sukharam 5 Defective product details A9N2P10D - QTY - 02 6 Product Make SCHNEIDER- MCB 7 Nature of Defect NOT WORKING PROPERLY (one pole no continuity in MCB and Output Voltage not shown) 8 Shutdown availability if applicable 9 Warranty status UNDER WARRANTY 10 Commissioned / Installed date 11 Serial No: or DOM of the product BILL NO - : 5941/23-24 DATE - 14-09-2023 12 Name & phone No: of person registering the complaint JOHNSON- 8780431402 13 NOTE Note : Point Nos: 1 to 9 are compulsory JOHNSON..Mob No:8780431402 EPABX No: 0261-2432308, 2420774 / 7383732308 / 9737326676 Hi-Tech Marketing NOTE: our new address is Hi-Tech Marketing"HI-TECH House"SHOP NO: 209, SNS INTERIO, E-Block,Bhatar-Althan Road,Surat-395007E mail:- hitech.surat@gmail.com www.hitechmarketing.co.in Location: https://www.google.com/maps/place/21%C2%B009'36.9%22N+72%C2%B048'41.0%22E/@21.1602815,72.8117754,20z Ashok K. Gandhi - 09376932308 - Kamal N. Parikh - 09376920774 - Hemen K. Gandhi - 09374726676 - Akash H Gandhi - 09173063086 | 2023-09-18 | 2023-09-19 14:36 | No | Warranty | M/S SUKHARAM ELECTRIC CORPORATION | 34, ROAD NO-6, NEW INDUSTRIAL ESTATE, B/H OF ALIDHRA, TV COMPOUND, UDHNA UDHYOGNAGAR, UDHNA null | SURAT | 394210 | Gujarat | India FS ED&I CSP West Team VARDHAMAN ELECTROSOFT Vadodara | MAHENDRA SINGH VARDHAMAN ELECTROSOFT Vadodara | VARDHAMAN ELECTROSOFT | During the site visit we found that customer having issue. Not getting output voltage of MCB. When I checked MCB physically ok . pole to pole continuity ok but the output voltage is not equal to the input voltage . | Repair |  | 9- Service Validated | 2023-09-22 15:04 |  |  | 40 | INR | 40 | ENM HOME DISTRIBUTION
WO-11296213 | 104217396 | 2023-09-23 16:02 | 2023-09-22 |  | 2023-09-22 18:14 | E8334L1_WE_G8 | E8334L1_WE_G8 | E8334L1_WE_G8 |  | Dear Team, hope everyone is doing well, a few weeks ago we billed a customer, the product is an avatar on. After some days of installation he feels switches are not working properly. He's expecting fabulous service from us, I kindly request a technical guy to exchange the defective switches from the customer site. We have mentioned the customer details manually, also we have attached an invoice copy for your reference. Billed to :- Laxmi infra buildcon pvt limited Customer name - Jagmohan Contact no.- 9810962447 Site Address- B - 43, south city - 2, gurugram | 2023-09-22 | 2023-09-27 11:37 | No | Warranty | Jagmohan Jagmohan | B - 43, south city - 2 | Gurugram | 122018 | Haryana | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the sockets and found sockets have output issue and dolly free issue. We replace the faulty sockets with new. | Repair |  | 8- Service Completed | 2023-09-27 14:42 |  |  | 1 | INR | 1 | ENM HOME DISTRIBUTION
WO-11277425 | 104092566 | 2023-09-20 10:04 | 2023-09-18 |  | 2023-09-18 17:28 | E8331EKT_DG | E8331EKT_DG | E8331EKT_DG |  | Dear team, Pls register complaint of E8331_6_DG 5 pcs Detail of customer Lalit Mehta H/no 105,Alpha City Fatehabad 125050 Haryana 9315877777 17/4/2023: Invoice Date Thanks & Regards, SANJAY KUMAR Manager-Sales Home and Distribution DivisionSchneider Electric http://www.facebook.com/SchneiderElectric Landline: +91 7087045622 Mobile: +91 9802600986 Email: sanjay.kumar1@se.com CC 18001030011/ 18004254272 2nd Floor, SCO 23,Sector 32,Chandigarh Road Ludhiana - 141010INDIA Download mySchneider app 24/7 support. Mobile catalog. Access to expert help. *Please consider the environment before printing this e-mail Internal | 2023-09-18 | 2023-09-23 18:00 | No | Warranty | Lalit Mehta | H/no 105,Alpha City | Fatehabad | 125050 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Rakesh Kumar Sharma Electric Chandigarh | Sharma Electric works(1003) | checked the sockets found not giving output and fan regulator found speed variation issue. Hence faulty, replaced. E8315_16_DG - 3 Nos. E8331FR350_DG_G8 - 1 Nos. Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-23 18:05 |  |  | 250 | INR | 250 | ENM HOME DISTRIBUTION
WO-11296252 | 104217228 | 2023-09-23 15:13 | 2023-09-22 |  | 2023-09-22 18:28 | E3031H1_EBGS | E3031H1_EBGS | E3031H1_EBGS |  | THE ABOVE 2 TWO ITEMS ARE GIVEN PROBLEM PLEASE DO THE NEEDFUL TO SOLVE IT. INSTALLATION ADDRESS - MR. S R GOENKA. 6, ALIPORE PARK ROAD, KOLKATA - 700027. CONTACT PERSON SK. ASIF 9903396967., COPY OF THE ATTACHED FOR YOUR REFERENCE! Invoive Details; Designer Electricals 27/July/2023 Delected Product: E3031H1EBGS 1G 1W C-METRO GREY E3031FRGS FAN REGULATOR THE ABOVE 2 TWO ITEMS ARE GIVEN PROBLEM PLEASE DO THE NEEDFUL TO SOLVE IT. INSTALLATION ADDRESS - MR. S R GOENKA. 6, ALIPORE PARK ROAD, KOLKATA - 700027. CONTACT PERSON SK. ASIF 9903396967., COPY OF THE ATTACHED FOR YOUR REFERENCE! | 2023-09-22 | 2023-09-27 15:12 | No | Warranty | SK ASIF | 6, ALIPORE PARK ROAD, | KOLKATA | 700027 | West Bengal | India FS ED&I CSP East Team SREYAM SERVICES BHATPARA | AMIT BHATTACHARYA_SREYAM SERVICES BHATPARA | Sreyam Services(8513) | FOUND SWITCH REPLACED BY NEW ONE AND DEFFECTIVE MATERIAL IS COLLECTED. | Repair |  | 8- Service Completed | 2023-09-29 10:21 | E3031H1EBGS not mapped properly with BFS =S= Free Order 226080723 has been saved |  | 22 | INR | 22 | ENM HOME DISTRIBUTION
WO-11280117 | 104113332 | 2023-09-19 14:24 | 2023-09-19 |  | 2023-09-19 11:28 | UNS32DP2M_WE | UNS32DP2M_WE | UNS32DP2M_WE |  | Dear Team, Hope this email finds you well, I would like to bring in your notice that, we have billed to a valuable customer, He has found 2 item of his list, is missing the internal screws of a DP switch unica pure white(UNS32DP2M_WE) AND one item in opale is been defective, customer has paid 100% advance payment for this order, also he's having very less time to change the defective switches & reinstall the fresh switches, so as distributor we have replaced the defective product to the customer, Now, the defective switches are kept in our schneider galaxy, experience point schneider, at dlf city court, first floor 111. Here, we have mentioned the switches is to be replaced from us, UNS32DP2M_WE - 1 nos. X1002WH - 1 nos. Here we have also attached an invoice copy for your reference. BILLING DETAIL Customer name - Soumya Roy SITE ADDRESS - B171 PINNACLE SECTOR-43, DLF PHASE-5, GURUGRAM CONTACT - 9899378212 Receiving address - First floor 111, dlf city court, schneider experience point, near sikanderpur Contact no.- 9910038074 Name - Dhal chand Invoice No. 23-24/00464 Dated 16-Sep-23 Thanks & Regards Somnath Mukherjee experience point schneider | 2023-09-19 | 2023-09-21 17:03 | No | Warranty | Dhal Chand | "office no 111. First floor Dlf city Court. Sikanderpur | Gurugram | 122002 | Haryana | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the switch and found switch have screw missing and output issue. We replace the faulty switch with new. Mail Id. rrahulwadhwa@gmail.com | Repair |  | 8- Service Completed | 2023-09-21 17:52 |  |  | 1 | INR | 1 | ENM HOME DISTRIBUTION
WO-11296563 | 104214408 | 2023-09-23 11:15 | 2023-09-22 | DB Lock Missing & problem | 2023-09-22 18:44 | A9KETND06 | A9KETND06 | A9KETND06 |  | Warning: Email body is too large and was truncated at 32 000 characters. Information may have been lost. Dear Sir / Madam, Pl attend. Checklist for Complaint Registration Doc. Ref :- SE/CCC/001 1 Company Name & Complete Address with pin code - Where product is installed PRIDE WORLD CITY NEAR D.Y.PATIL COLLEGE CHARHOLI BUDRUK PUNE -412105 2 Contact Person at Site : Name & Mobile No. VINAYAK PATIL 9011880099 SANJAY KHANDALE - 7410093117 Alternate Mobile No : 3 Contact Person at Site - Email Address** sonali@srentp.com 4 Defective Product Model/Part No (Pls refer FAQ sheet ) A9KETND06 5 Nature of Defect* - Defects Video and Photographs 40 NOS DB LOCK NOT PROPER WORKING 6 Shutdown availability if applicable 7 POP - SE Authorised Partner Invoice soft copy Invoice # 9008630235 A9KETND06-118 PCE 8 Photograph of product where Serial No/Batch Code or Date of Manufacturing printed - Please refer FAQ sheet 9 Name & phone No: of person registering the complaint Sonali 9022060934 | 2023-09-22 | 2023-09-25 15:58 | No | Warranty | Pride World City | Nr DY Patil College , Dhanuri , | Pune | 412105 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Sachin Jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the DB - 40 nos it's Lock Missing & problem. checked on/off operation not found ok. we found POP on that. then we clean it properly and on/ off operation found ok. then we found another DB found lock missing. this problem found customer mishandling so we reject the warranty of product. | Repair |  | 9- Service Validated | 2023-09-25 16:04 |  |  | 40 | INR | 40 | ENM HOME DISTRIBUTION
WO-11280287 | 104116108 | 2023-09-19 16:48 | 2023-09-19 |  | 2023-09-19 12:27 | CSS54E_WE | CSS54E_WE | CSS54E_WE |  | Re: Faulty Schneider PIR Sensor under warranty period [ thread::paJP4gvmeKutIy9rTDIaUD4:: ] I have purchased a few Schneider PIR Sensor on 18th July. And immediately after installation I am unable to obtain the desired time duration. Even while switching it to 2 minutes, My sensor keep on working for 15-20 minutes. I had raised complaint to the seller, but seems he didn?t respond adequately. Kindly arrange a swift check and provide me a solution for 2 sensor(s). Regards, Pratik Nag P.S Please find my details below My address: 158, Navjeevan Appartment, Dwarka Sector 1A New Delhi 110045 Phone: 7042121211 Inv attached | 2023-09-19 | 2023-09-25 14:33 | No | Warranty | Pratik Nag | 158, Navjeevan Appartment, Dwarka Sector 1A | Delhi | 110045 | Delhi | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the sensor and found sensor have timing issue. As per serial number sensor not cover under warranty, But customer provide the invoice details. We replace the faulty sensor with new. Mail Id. pratik.nag@me.com | Repair |  | 8- Service Completed | 2023-09-25 17:55 |  |  | 42 | INR | 42 | ENM HOME DISTRIBUTION
WO-11296655 | 104216147 | 2023-09-23 11:17 | 2023-09-22 | MCB Tripping Issue | 2023-09-22 18:58 | A9N4P40C | A9N4P40C | A9N4P40C |  | Dear Sir, Please find the given details of faulty MCB. Description Serial No Qty Fault A9N4P40C 940145-3/ 3 606480 497865/ DD-2022-W30-2-8 1 Auto Tripping Issue (While Connected to supply and also when not Connected to supply) A9N4P40C 940145-8/3 606480 497865/ DD-2022-W30-2-8 1 Auto Tripping Issue (While Connected to supply and also when not Connected to supply) Requesting you to please replace the same. Regards, Pranav Mhetre, Procurement Specialist, Aditya Green Energy Private Limited, Block No. 1, Kapil Plaza, Near Udyog Bhavan, Signal Camp, Latur, Maharashtra - 413512 Mobile :- +91 7875882226 Telephone :- +91 2382 253 700 Email :- pranav@adityagreenenergy.com Website :- www.adityagreenenergy.com On Sat, Sep 16, 2023 at 9:47?AM sanjay kothale <skothale.sktraders@gmail.com> wrote: Dear Team Pl. Look in the matter ---------- Forwarded message ---------From: SK Traders <info@sktradersaurangabad.com>Date: Sat, Sep 16, 2023 at 9:26?AMSubject: Fwd: Faulty MCBTo: Sanjay <skothale.sktraders@gmail.com> fyi ---------- Forwarded message ---------From: Pranav Mhetre <purchase@adityagreenenergy.com>Date: Fri, Sep 15, 2023 at 5:50?PMSubject: Faulty MCBTo: SK Traders <info@sktradersaurangabad.com>, S.K.TRADERS <sales.sktraders@gmail.com>Cc: Jayesh Bajaj <jayesh@adityagreenenergy.com> Dear Sir, Please find the attached details and Photos of faulty MCB. Description Serial No Qty Fault A9N4P40C 94045-3/3 606480 497865 1 Auto Tripping Issue ( While Connected to supply And also when not Connected to supply ) Requesting you to please replace the same. Regards, Pranav Mhetre, Procurement Specialist, Aditya Green Energy Private Limited, Block No. 1, Kapil Plaza, Near Udyog Bhavan, Signal Camp, Latur, Maharashtra - 413512 Mobile :- +91 7875882226 Telephone :- +91 2382 253 700 Email :- pranav@adityagreenenergy.com Website :- www.adityagreenenergy.com -- Regards, Kothale S.S S.K.Traders 9373169403 | 2023-09-22 | 2023-09-25 10:28 | No | Warranty | Aditya Green Energy Pvt. Ltd. Latur | Kapil Plaza, Near Udyog Bhavan, Signal Camp, Latur | Latur | 413512 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Samadhan S_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the MCB Tripping Issue. MCB on/off operation not found ok. it's found dolly free due to internal mechanism issue. so problem observed in MCB's. It's needs to be replaced/ Required Material : A9N4P40C - 02 nos | Repair |  | 9- Service Validated | 2023-09-25 15:41 | =S= Consig Fill up 226075235 |  | 300 | INR | 300 | ENM HOME DISTRIBUTION
WO-11280293 | 104115640 | 2023-09-20 12:09 | 2023-09-19 |  | 2023-09-19 12:29 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Name of Client: Mr. Sudhir Kumar ji Address:H.No. 11,G- Block,Rajindra Estate,Moga- 142001 E- Mail : sudhir201@gmail.com M.No. : 9915420002, 93681-40001 Invoice No. : 7803 Date of Invoice: 29/9/2022 Product Reference No. : 1H100WFVDP Quantity: 1pc Bill copy attached below. Kindly provide him service asap . Thanks & Regards, Rahul Sharma | 2023-09-19 | 2023-09-20 12:21 | No | Warranty | Sudhir Kumar | H.No. 11 G- Block Rajindra Estate Moga | Moga | 142001 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | checked the vdp found configuration issue. set right the same, now vdp working properly. Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-20 12:26 |  |  | 75 | INR | 75 | ENM HOME DISTRIBUTION
WO-11301080 | 104229398 | 2023-09-23 11:53 | 2023-09-23 |  | 2023-09-23 11:02 | A9N1P20C | A9N1P20C | A9N1P20C |  | MCB complaint Product :A9N1P20C, 20Amps AC MCB Sr No.D 2149 DOM DEC 2021 Not getting ON / Dolly Free Please replace | 2023-09-23 | 2023-09-23 16:24 | No | Warranty | Sai Enterprises | 32, Near clock tower, Gangapur | Bhilwara | 311801 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | Checked the mcb found dolly free and MT found not getting on due to mechanism issue, Hence faulty replaced. A9N1P20C - 1 nos LV432641 - 1 nos Email : | Repair |  | 8- Service Completed | 2023-09-23 16:27 |  |  | 305 | INR | 305 | ENM HOME DISTRIBUTION
WO-11301120 | 104229342 | 2023-09-23 17:02 | 2023-09-23 |  | 2023-09-23 12:13 | MTN684032 | MTN684032 | MTN684032 |  | Dear Team Please find the attached complaint and depute the engineer for the same. Name of Customer MR.LOKESHWAR P Site Address NO.F-0001, STERLING GARDENS KEMPAPURA HEBBALA BENGALURU-560024 Name of contact person at site KRISHNA PRASAD M Contact Phone / Mob. No: 9900030357 Defective product details MTN684032-KNX POWER SUPPLY Nature of Defect THIS CONTROLLER IS NOT POWERING ON Shutdown availability if applicable YES Warranty status UNDER WARRENTY Commissioned / Installed date 21 May 2023 Name & phone No: of person registering the complaint MR; KRISHNA PRASAD M, M/S TECHMECH ENGG CELL NO-9900030357 Invoice Date GST/0810/23-24 DT: 10 MAY 2023 --------------------------------------------------------------------------- Thanks & Regards, Krishna Prasad M Techmech Engineers BANGALORE ¦ CHENNAI ¦ MYSORE No.30/B6 ¦ 3rd Main Road ¦ Industrial Estate ¦ Rajajinagar ¦ Bangalore- 560 010 Phone : 080 ? 23300858 ¦ Fax: 080 - 23300155 ¦ Mob: +91-9900030357 Web: www.techmechengineers.com ¦ e-Mail ID: sales@techmechengineers.com | 2023-09-23 | 2023-09-25 16:00 | No | Warranty | KRISHNA PRASAD | NO.F-0001, STERLING GARDENS KEMPAPURA HEBBALA | BENGALURU | 560024 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Mohammad Riyaz_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | i had visited the site and checked the customer reported knx power supply, the problem found was the controller not getting power On due to internal issue, so we had arranged for the replacement directly to Techmech engineers. | Repair |  | 9- Service Validated | 2023-09-25 20:11 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11280446 | 104115896 | 2023-09-19 16:30 | 2023-09-19 |  | 2023-09-19 13:28 | P1101_DG | P1101_DG | P1101_DG |  | Hi, PFA, complaint registration details for a newly installed site for Livya Switches. Please send a technician to this site as soon as possible. Name of Customer Jagadeesh AP Site Address Puthiyapurayil, pakayad,Dharmadam, near Maniyath school. (p o)pakayad pincode - 670661 Kannur Name of contact person at site Jagadeesh AP Contact Phone / Mob. No: 9847633906 Defective product details LIVIA 16A 1WAY SWITCH "P1101_DG" Nature of Defect Customer is facing issues with LIVIA 16a 1way switch with indicator Shutdown availability if applicable Warranty status Under Warranty Commissioned / Installed date One month Serial No: or DOM of the product Name & Phone No: of person registering the complaint Mohammed Jebrood- 9743182896 Thanks & Regards, MJ Marketing 33/480, AM Building, Railway Station Road, Near Keloth Juma Masjid, Keloth, Payyanur - 670307 PH : 04985 209896, 9188 209896 Email : contact@mjmarketing.in "We know you have many choices in doing business and we THANK YOU for choosing us!" | 2023-09-19 | 2023-09-21 21:23 | No | Warranty | Jagadeesh AP | Puthiyapurayil, pakayad,Dharmadam, (p o)pakayad | KANNUR | 670661 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found livia switchs dolly crack and some switchs not working P1001 10NOS P1181 1NOS replaced problem solved | Repair |  | 9- Service Validated | 2023-09-21 21:30 |  |  | 80 | INR | 80 | ENM HOME DISTRIBUTION
WO-11301144 | 104229229 | 2023-09-25 12:26 | 2023-09-23 | Switch not working | 2023-09-23 12:43 | IN8401_16 | IN8401_16 | IN8401_16 |  | Dear Sir, Pl issue complaint no. 1. Name of Customer: Soumen Ghosal 2. Site Address: - flat no- 1101 Aishwaryam Comfort, Chinchwad - Akurdi Link Rd, opposite Yuvraj Motors, Maharashtra 411035 3. Name of contact person at site :- Soumen Ghosal 4. Contact Phone / Mob. No: - 90070 05036 5. Defective product details:-IN8401 6. Product Make:- Zencelo 7. Nature of Defect: Switch not working 8. Shutdown availability if applicable :nil 9. Serial No: or DOM of - 21516L 10. Dealer Name /OA no. /Invoice Details: - In warranty 11. Commissioned / Installed date:- NIL 12. Name & phone No: of person registering the complaint: Mr.Soumen Ghosal Regards, Soumen Ghosal | 2023-09-23 | 2023-09-25 16:08 | No | Warranty | Soumen Ghosal | Flat no- 1101 Aishwaryam Comfort, Chinchwad - Akurdi Link Rd | Pimpri-Chinchwad | 411035 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Kunal jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the Switches not working. it;s found stuck not changing contact. switches stuck again & again. this problem is not repairable. So Switches needs to be replaced. Required Material : IN8401- 01 nos, IN8444/16 - 03 nos | Repair |  | 9- Service Validated | 2023-09-26 10:08 | =S= Consig Fill up 226081594 |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11280712 | 104120461 | 2023-09-20 12:06 | 2023-09-19 |  | 2023-09-19 14:42 | A9N3P32C | A9N3P32C | A9N3P32C |  | Please register complaint of PART NO. ? A9N3P32C , QTY ? 1 nos Please register complaint of PART NO. ? A9N3P32C , QTY ? 1 nos, INVOICE NO. AA0630008052 (9008448199 ) DTD. Feb 25, 2023 Site Address :- Rudra Lift & Control G- 20, Ground Floor Property no. 222, Sector ? 7, Rohini, New Delhi ? 110085. Contact No. :- 8882679970 (Mr. Surendra) Problem :- ONE SCREW FREE (Images are attach) Please register complaint and resolve on priority. Please confirm. Regards! SHIVVIR A RASTOGI CABOT ELECTRONICS PVT LTD 149 PATPARGANJ IND. AREA DELHI-110092 Mob:9910396031/9810033915/9910396032/8130232971 Email:- Sales@cabotgroups.com | 2023-09-19 | 2023-09-26 15:08 | No | Warranty | Rudra Lift & Control | G- 20, Ground Floor Property no. 222, Sector ? 7, Rohini, null | Delhi | 110085 | Delhi | India FS ED&I CSP North Team Sharma Electric Works Delhi | Pradeep Sharma_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mcb found phase screw free, Hence faulty replaced. A9N3P32C - 1 nos Email : id not provided by customer . | Repair |  | 8- Service Completed | 2023-09-26 15:10 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11301202 | 104229749 | 2023-09-23 15:02 | 2023-09-23 |  | 2023-09-23 14:13 | A9KF71463BQ | A9KF71463BQ | A9KF71463BQ |  | Dear Team, Inv. copy attached herewith. Checklist for Complaint Registration Doc. Ref :- SE/CCC/22-23/353 1 Company Name & Complete Address with pin code - Where product is installed BRISK ELECTRONICS PVT. LTD. 2 SIDE ADRESS PLOT NO. 512/1, PHASE-4, NR. RAMOL POLICE CHOWKI, VATVA GIDC, AHMEDABAD-382445 3 Contact Person at Site: Name & Mobile No. SHAILESH MAKWANA - 9924227896 4 Altemate Mobile No. : BHAVIK SHAH -85111 48901 5 Contact Person at Site - Email Address**. 6 Defective Product Model/Part No (Pls refer FAQ sheet ) A9KF71463BQ = TRIPPING PROBLEM INV. : 107716 6-a Defective Product Model/Part No (Pls refer FAQ sheet ) A9KR11263 = ON/OFF PROBLEM INV. : 107716 6-b Defective Product Model/Part No (Pls refer FAQ sheet ) METSEEM6436HCL10NC = 02 NO. INV. : 15089 6-c Defective Product Model/Part No (Pls refer FAQ sheet ) A9KF71310BQ = TRIPPING PROBLEM INV. : 109418 6-d Defective Product Model/Part No (Pls refer FAQ sheet ) A9KF71320BQ = TRIPPING PROBLEM INV. : 109418 6-e Defective Product Model/Part No (Pls refer FAQ sheet ) ABL2REM24045K = 03 NO. NOT WORKING INV. : 106158 6-f Defective Product Model/Part No (Pls refer FAQ sheet ) 7 Nature of Defect* - Defects Video and Photographs 8 Shutdown availability if applicable 9 POP - SE Authorised Partner Invoice soft copy INV. : 107716,15089,106158 10 Photograph of product where Serial No/Batch Code or Date of Manufacturing printed - Please refer FAQ sheet 11 Name & phone No: of person registering the complaint SHAILESH MAKWANA - 9924227896 Points 1,2,3,4,5 & (7or8) are mandatory. * Kindly share defect symptoms instead of "Not working", Please share the link of large files(product photoes or videoes) ** End user will receive a survey asking feedback on service POP - Proof of Purchase Please fill above details and send this sheet to customer care, Customer care contact link is give below https://www.se.com/in/en/work/support/contacts.jsp Please mention Complaint as key word and Product Name in email subject line e.g for Masterpact NW ACB complaint - Complaint for Masterpact NW Our web site :- https://www.se.com/in/en/ | 2023-09-23 | 2023-09-27 12:09 | No | Warranty | Brisk Electronics Pvt. Ltd.(3136) | Plot No. 512/1, Phase 4, Near Ramol Police Chowki, GIDC Vatva, | Ahmedabad | 382445 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Ritesh Prajapati_Anik Engineering Ahmedabad | Anik Engineering (554) | Check the above product A9KR11263 SR NO : D2023 W1051 dolly free. A9KF71463 SR NO : DD2241 dolly free. A9KF71310 SR NO : D2304 tested ok. A9KF71320 SR NO : D1710 tested ok. A9KF71320 - D1710 tested ok. ABL2REM24045K 8A2022W164161B00 - 8A2022 W16416B00688100206 all 3 Nos power supply are tested ok. METSEEM6436H SR NO : 540410034924 DOM 26032 FW V01.03.00 HW : A1 C1 :1.0 no display problem . METSEEM6436H SR NO : 540410005024 dom 180418 fw v01.03.00 HW A1 CL 1.0 no display problem. meter invoice no 107716. | Repair |  | 9- Service Validated | 2023-09-27 12:09 | =S= Consig Fill up 226086342 |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11280786 | 104120755 | 2023-09-21 17:37 | 2023-09-22 |  | 2023-09-19 15:11 | IH101ZWIFI | IH101ZWIFI | IH101ZWIFI |  | Wiser Installation Required Kindly arrange the installation at the below address asap. Product is available at the address. Invoice attached. Customer Name ? Rohit Dua Contact No ? 8588007709 Address ? House no- 205/206 Sec-06 pkt B-3 Rohini New Delhi 110085. IH101ZWIFI ---2pcs IH100WFVDP----- 1pc IH14000100--- 16 pcs IH101ZW2IR--- 6pc | 2023-09-19 | 2023-09-22 22:30 | No | Commercial Action - Sales | Rohit Dua | House no- 205/206 Sec-06 pkt B-3 Rohini | Delhi | 110085 | Delhi | India FS ED&I CSP North Team Seamtek International Pvt. Ltd. GHAZIABAD | Satish Raika Seamtek International Pvt. Ltd. GHAZIABAD | Seamtek International Pvt. Ltd. | *The client has refused us to do work today, as the material was not ready. *The client has given us the time to do the work today. And we reached the site on time. *When we reached the site, the client was not there. | Commissioning & Installation | Start-up | 8- Service Completed | 2023-09-22 14:30 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11301227 | 104230038 | 2023-09-23 17:04 | 2023-09-23 |  | 2023-09-23 15:13 | A9N26947 | A9N26947 | A9N26947 |  | Hi, I am Akash, from KFC project team. This shunt trip coil has been bought by our KFC project sub vendor for our renovation project in KFC at Phoenix Market City Food Court store at Bangalore. His mobile phone is damaged, so we are doing the follow up for him. Our vendor name Jaganaath and his mobile phone number is +91 9620246121 I request you to take immediate action in this shunt trip coil issue. Regards, Akash +91 6383870982 Get Outlook for Android From: Schneider Electric Customer Care <customercare.in@schneider-electric.com> Sent: Saturday, September 23, 2023 2:05:54 PM To: Akash P <akash.p@dil-rjcorp.com> Subject: [External] RE: Shunt trip coil not in working condition - Phoenix market City Bangalore [ thread::CCHlnpQldeC0fSu1XC4yej4:: ] Caution: This email originated from outside of the organization. Do not click links or open attachments unless you recognize the sender and know the content is safe. Hi Akash, Greetings from Schneider!! Please share the contact person name & number on site along with end user mail id. Regards, Abhijit Sarkar Customer Care Centre ¦ Schneider Electric India ¦ Toll Free: 18001030011 / 18004254272 / 18004194272 ¦ Email:Customercare.in@schneider-electric.com ¦ Site: www.schneider-electric.com " Still need help? Try Chat ( https://www.se.com/in/en/ ) with Us" Invoice Detail Rishabh Cable Co, Bangalore 13-09-2023 --------------- Original Message --------------- From: [akash.p@dil-rjcorp.com] Sent: 22/9/2023 9:47 pm To: customercare.in@schneider-electric.com Subject: Shunt trip coil not in working condition - Phoenix market City Bangalore Dear sir, I have raised a complaint that a shunt trip coil which I have bought is not working. I have attached the invoice bill of the shunt trip coil and the photos of shunt trip coil. Please refer the attached photos. Request you to look into this issue as early as possible. This KFC store is located in Phoenix Market City Bangalore Address of the store is mentioned below, KFC Food Court Store, Phoenix Market City, Whitefield Main Road, Mahadevapura, Bengaluru, Karnataka 560048 Regards, Akash | 2023-09-23 | 2023-09-28 15:40 | No | Warranty | KFC Food Court | KFC Food Court Store, Phoenix Market City, Whitefield Main Road, Mahadevapura null | Bengaluru, | 560048 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Mohammad Riyaz_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported shunt trip- found not actuating internal mechanism dislocated. So we had arranged for the new replacement to the customer. | Repair |  | 8- Service Completed | 2023-09-28 17:02 |  |  | 12 | INR | 12 | ENM HOME DISTRIBUTION
WO-11280834 | 104122499 | 2023-09-22 11:05 | 2023-09-19 |  | 2023-09-19 15:30 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | VDP --installation request vdp installation IH100WFVDP---installation request Inv attached | 2023-09-19 | 2023-09-22 18:14 | No | Commercial Action - Sales | Pawan Ji | House no 5 Azad takies | Bisalpur | 262201 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Abhishek Patel Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Installation has been done, VDP working fine. | Commissioning & Installation | Start-up | 8- Service Completed | 2023-09-22 18:16 |  |  | 270 | INR | 270 | ENM HOME DISTRIBUTION
WO-11301233 | 104230016 | 2023-09-25 10:12 | 2023-09-23 | MCb Dolly Free | 2023-09-23 15:28 | A9N3P50C | A9N3P50C | A9N3P50C |  | Dear Sir, Complaint received from the COTMAC ELECTRONICS PVT. LTD. Saying that MCB A9N3P50C- 1 Qty has an issue dolly not working. SO.NO-300812443 Site address- COTMAC ELECTRONICS PVT. LTD. J-449,MIDC,Bhosari,PUNE-411026 Contact person- Mr.Shahjahan Shaikh.(8308802907/7447480991) Please find the attached our Invoice. Invoice Details ; Simply Electrifying Pvt Ltd Date ; 12 september 2023 NAumber: 43831 Thanks & Regards, Mohini Bali 8805008503 A B Controls / Simply Electrifying Pvt. Ltd. 201 Varsha Avenue, 104 Anand Park Aundh, Pune 411007 Tel : +91- 20- 25890010 / 25890030 Tollfree : +91 - 1800 233 4333 Please do visit us at www.simply-electrifying.com | 2023-09-23 | 2023-09-25 12:05 | No | Warranty | COTMAC ELECTRONICS PVT. LTD. | COTMAC ELECTRONICS PVT. LTD. J-449,MIDC,Bhosari null | Pune | 411026 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Sachin Jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the MCb Dolly Free. it's not getting ON. so we removed side sticker and we found some dust on sticker so we clean it. and then taken on/off operation it's working found ok. | Repair |  | 9- Service Validated | 2023-09-25 12:10 |  |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11280877 | 104118772 | 2023-09-20 12:49 | 2023-09-19 |  | 2023-09-19 15:54 | A9N4P63C | A9N4P63C | A9N4P63C |  | MCB-Complaint i want to replace these products this products are not working properly (MCB 4POLE 63AMP ACTI 9 ) 2 pc from: OM ELECTRICS WORKS Name- Om Parkash Dang M. 7837426747 9815409842 ADDRESS #458/2/A NEW KIDWAI NAGAR ST.2 NEAR DD JAIN COLLEGE LUDHIANA 141008 PLS RESOLVE MY ISSUE | 2023-09-19 | 2023-09-23 14:07 | No | Warranty | Om Electric Works | Nwekidwai nagar House no. 45/2/A Street no. 2 near Devki devi jain collage | Ludhiana | 141008 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the mcb found dolly free. Hence faulty replaced. A9N4P63C - 2 Nos. email : omelectricworks04@gmail.com | Repair |  | 8- Service Completed | 2023-09-23 14:09 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11301252 | 104229913 | 2023-09-27 13:17 | 2023-09-23 |  | 2023-09-23 16:13 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Request for Installation-- Smart Door Bell Kindly arrange to install VDP for below customer, bill attached for your reference. Customer Name- Mr .Bhatia Product: Smart Door Bell Address: 51, Lajpat Nagar, Jalandhar-144001 Contact No: : 9815662222 Regards, RAGENI SHARMA | 2023-09-23 | 2023-09-27 13:18 | No | Commercial Action - Sales | Bhatia Bhatia | 51, Lajpat Nagar, | Jalandhar | 144001 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | WIFI not available at site. email : id not provided by the customer. | Commissioning & Installation | Start-up | 8- Service Completed | 2023-09-27 13:22 |  |  | 65 | INR | 65 | ENM HOME DISTRIBUTION
WO-11280891 | 104123266 | 2023-09-19 17:00 | 2023-09-19 |  | 2023-09-19 15:58 | MTN6185-6034 | MTN6185-6034 | MTN6185-6034 |  | MTN6185-6034 My Device MTN6185-6034 indiactors are not glowing Digital Technologies Address is A96, Sector 72, Noida - 201301. Nearest Metro Noida Sector-52 Invoice No. 2022/CIHR02529 Dt 26/09/2022 Shirish Srivastava 7827033331 digital-technologies@outlook.com | 2023-09-19 | 2023-09-23 17:35 | No | Warranty | Digital Technologies | G 46,Sector 41 | Noida | 201303 | Uttar Pradesh | India FS ED&I CSP North Team Saffron Automation Delhi | Deepak Pal_Saffron Automation Delhi | Saffron Automation(18001) | Check the KNX push button pro and found push button have indicator glowing issue. We replace the faulty KNX push button with new. Mail Id. digital-technologies@outlook.com | Repair |  | 8- Service Completed | 2023-09-23 18:11 |  |  | 38 | INR | 38 | ENM HOME DISTRIBUTION
WO-11304276 | 104235814 | 2023-09-25 10:38 | 2023-09-25 |  | 2023-09-25 10:28 | A9N3P63C | A9N3P63C | A9N3P63C |  | Product: : A9N3P63C MCB 3Pole MCB 63 amps Sr No: D 2312 March 2023 Not Getting ON / OFF Knob Loose Gaurav Associates NHPC Township, Chamera-I Power Station Khairi BANIKHET, Himachal Pradesh. 176303 Mr Jatin Sharma 8360194147 Mail Id : jatsharma1@rediffmail.com | 2023-09-25 | 2023-09-25 11:14 | No | Warranty | Gaurav Assiciates | NHPC Township, Chamera-I Power Station Khairi near Banikhet Himachal Pardesh | chamba | 176303 | Himachal Pradesh | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Karnail Singh Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the mcb found knob free and checked the contactor found not getting on, Hence faulty replaced. A9N3P63C - 1 nos LC1D95M7 - 1 nos Email : jatsharma1@rediffmail.com | Repair |  | 8- Service Completed | 2023-09-25 12:36 |  |  | 330 | INR | 330 | ENM HOME DISTRIBUTION
WO-11280927 | 104123435 | 2023-09-19 19:57 | 2023-09-19 |  | 2023-09-19 16:17 | IH14000100 | IH14000100 | IH14000100 |  | Wiser installation K. Rajasekhar We need installation tomorrow at 3pm K. Rajasekhar 8007365462 or 9740303333 Villa no 62 prestige ozone hagadur nexus Whitefield 560066 Sl. No. Description Quantity 1 2 3 4 Relay - IH14000100 IR blasters - H101ZW2IR Doorbell- IH100WFVDP Fan controller-IH1200010F 2 2 1 1 | 2023-09-19 | 2023-09-20 15:10 | No | Warranty | K. Rajasekhar | Villa no 62 prestige ozone hagadur nexus Whitefield | Bangalore | 560066 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | C Gunasekaran_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | We had visited the site and installed customer purchase wiser relay and checked working ok . | Repair |  | 9- Service Validated | 2023-09-20 22:12 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11304305 | 104235917 | 2023-09-25 12:43 | 2023-09-25 |  | 2023-09-25 10:46 | P1132_N | P1132_N | P1132_N |  | SWITCH COMPLAINT KHALID K K ZAFAR,ANIYARAM SOUTH,PERIGATOOR,KANNUR DIST.PIN;670675 KANNUR MOB;9447517749,807514101 KHALID K K MOB;9447517749,807514101 P1132,P1181 Not working,Breakage. YES YES 21.02.22 P1132 -2 NOS,P1181-4NOS SIJU A K,9037648636 | 2023-09-25 | 2023-09-26 11:31 | No | Warranty | KHALID K K | ZAFAR, ANIYARAM SOUTH,PERIGATOOR | KANNUR | 670675 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found livia 32dp switch & 16ah switch indicator not working P1132 1NOS P1181 2NOS replaced problem solved | Repair |  | 8- Service Completed | 2023-09-26 11:34 |  |  | 70 | INR | 70 | ENM HOME DISTRIBUTION
WO-11281163 | 104127243 | 2023-09-21 12:13 | 2023-09-19 |  | 2023-09-19 18:13 | A9N4P63C | A9N4P63C | A9N4P63C |  | Model Number: A9N4P63C Serial Number :3606480740756 DD2021W23-2-8 Invoive date : year 2023 Shop no 2, Ashok Mohalla, Bhooton Wali, Nangloi Delhi 110041 Delhi India 9811702273 Stish Jindal | 2023-09-19 | 2023-09-21 13:11 | No | Warranty | Laxmi Electricals | Shop no 2, Ashok Mohalla, Bhooton Wali, Nangloi | Delhi | 110041 | Delhi | India FS ED&I CSP North Team Sharma Electric Works Delhi | Pradeep Sharma_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mcb found working ok. Email : id not provided by customer. | Repair |  | 8- Service Completed | 2023-09-21 13:19 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11304471 | 104230580 | 2023-09-25 14:24 | 2023-09-25 |  | 2023-09-25 11:44 | LSS100100 | LSS100100 | LSS100100 |  | Dear Team Pls find the attached invoice copy for regarding complaint of Logic Controller (LSS100100) kindly register the complain. Invoice Details: Shree Krishna Corporation Date : 05/08/2023 No: 68/July/2023-24 Site Address Max Estates 128 Pvt Ltd Address- Nirman Sadan Gate No 1 TS-02 Sector 128 Link Road Noida U.P 201304 Cont Per - Mr Dinesh - 97184 23351 Atul Pandey ¦ Shree Krishna Corporation. ¦ New Delhi Mobile: +91-74080-62123 Phone: +91-11-45578643/44 Telefax ¦ Email: accounts@shreekrishnacorp.com ¦ Site: www.shreekrishnacorp.com ¦ *** Please consider the environment before printing this e-mail *** | 2023-09-25 | 2023-09-26 11:49 | No | Warranty | Dinesh Dinesh J | Nirman Sadan Gate No 1 TS-02 Sector 128 Link Road | Noida | 201304 | Uttar Pradesh | India FS ED&I CSP North Team Saffron Automation Delhi | Deepak Pal_Saffron Automation Delhi | Saffron Automation(18001) | Check the logic controller and found after input supply module is power up. After programming the controller not gave output. Si its faulty. We replace the faulty controller with new. | Repair |  | 8- Service Completed | 2023-09-27 11:51 |  |  | 24 | INR | 24 | ENM HOME DISTRIBUTION
WO-11283255 | 104143266 | 2023-09-20 15:21 | 2023-09-20 |  | 2023-09-20 09:24 | IH101ZWIFI | IH101ZWIFI | IH101ZWIFI |  | Wiser installation Phase 4 for HT Please Raise the Wiser Installation for Hindustan Times Phase 4 Automation Gateway IH101ZWIFI - Qty---1 4 Channel Automation Relay-IH14000100 - Qty---5 | 2023-09-20 | 2023-09-20 21:47 | No | Commercial Action - Sales | ANANT UPADHAYIA | Shashi Park Rd, Mayur Vihar | Delhi | 110091 | Delhi | India FS ED&I CSP North Team Seamtek International Pvt. Ltd. GHAZIABAD | Satish Raika Seamtek International Pvt. Ltd. GHAZIABAD | Seamtek International Pvt. Ltd. | following wiser components has been installed gateway: 1 qty 4 ch. relay :5 qty | Commissioning & Installation | Start-up | 8- Service Completed | 2023-09-22 16:49 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11304866 | 104241020 | 2023-09-26 16:02 | 2023-09-25 |  | 2023-09-25 13:59 | X1001WH_N | X1001WH_N | X1001WH_N |  | OPel 6 mpr Invoice Power control Invoice Date : August 2022 Kamlesh Chaurasiya 9352600455 A-18 BHAMASHAH MANDI/Anaj mandi , Kota 324005 | 2023-09-25 | 2023-09-26 16:05 | No | Warranty | Kamlesh Chaurasiya | A-18 BHAMASHAH MANDI/Anaj mandi | Kota | 324005 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | Checked the switches found side break. Hence faulty replaced. X1001WH - 5 Nos. email : id not provided by the customer. | Repair |  | 8- Service Completed | 2023-09-27 12:30 |  |  | 250 | INR | 250 | ENM HOME DISTRIBUTION
WO-11283262 | 104143344 | 2023-09-20 15:25 | 2023-09-21 |  | 2023-09-20 09:31 | IH101ZWIFI | IH101ZWIFI | IH101ZWIFI |  | Wiser installation Phase 4 for HT Please Raise the Wiser Installation for Hindustan Times Phase 4 Automation Gateway IH101ZWIFI - Qty---1 4 Channel Automation Relay-IH14000100 - Qty---5 | 2023-09-20 | 2023-09-22 01:14 | No | Commercial Action - Sales | PRADEEP KUMAR | Shashi Park Rd, Mayur Vihar | Delhi | 110091 | Delhi | India FS ED&I CSP North Team Seamtek International Pvt. Ltd. GHAZIABAD | Satish Raika Seamtek International Pvt. Ltd. GHAZIABAD | Seamtek International Pvt. Ltd. | following wiser components has been installed gateway: 1 qty 4 ch. relay :5 qty | Commissioning & Installation | Start-up | 8- Service Completed | 2023-09-22 17:15 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11304899 | 104238195 | 2023-09-26 14:16 | 2023-08-26 |  | 2023-09-25 14:07 | IH101ZWIFI | IH101ZWIFI | IH101ZWIFI |  | RE: Installation call login [ thread::VLh1KEh8fAqZbuk0s8oosz4:: ] IH101ZWIFI 1 IH14000100 1 IH100WFVDP 1 Pls create work order for Wiser installation for below add details. invoice attached. Flat No-6132,Maple Parx Laureate,Sec-108 Block A. Noida-201304 UP Contact Person-Mr. Abhijeet 8288933222 | 2023-09-25 | 2023-09-27 02:27 | No | Commercial Action - Sales | Abhijeet Abhijeet | Flat No-6132,Maple Parx Laureate,Sec-108 Block A. | Noida | 201304 | Uttar Pradesh | India FS ED&I CSP North Team Seamtek International Pvt. Ltd. GHAZIABAD | Satish Raika Seamtek International Pvt. Ltd. GHAZIABAD | Seamtek International Pvt. Ltd. | Following wiser component has been installed: Gateway : 1 4 channel relay : 1 Smart doorbell : 1 | Commissioning & Installation | Start-up | 8- Service Completed | 2023-09-28 14:34 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11283271 | 104143426 | 2023-09-20 15:31 | 2023-09-21 |  | 2023-09-20 09:37 | IH101ZWIFI | IH101ZWIFI | IH101ZWIFI |  | Wiser installation Phase 4 for HT Please Raise the Wiser Installation for Hindustan Times Phase 4 Automation Gateway IH101ZWIFI - Qty---1 4 Channel Automation Relay-IH14000100 - Qty---5 | 2023-09-20 | 2023-09-22 05:07 | No | Commercial Action - Sales | SUNITA PETER | Shashi Park Rd, Mayur Vihar | Delhi | 110091 | Delhi | India FS ED&I CSP North Team Seamtek International Pvt. Ltd. GHAZIABAD | Satish Raika Seamtek International Pvt. Ltd. GHAZIABAD | Seamtek International Pvt. Ltd. | following wiser components has been installed gateway: 1 qty 4 ch. relay :5 qty | Commissioning & Installation | Start-up | 8- Service Completed | 2023-09-22 17:08 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11304917 | 104237782 | 2023-09-25 15:39 | 2023-09-25 |  | 2023-09-25 14:13 | E8331BPL1_DG | E8331BPL1_DG | E8331BPL1_DG |  | Dear team, Kindly arrange the site visit and solve the issue as soon as possible. 1 Name of Customer SHAHID MASH 2 Site Address KULIRATHARI ELETTIL, ELETTIL (PO) ELETTIL-PARAPPANPOYIL ROAD, ELETTIL KOZHIKODE - 673572 3 Name of Contact Person at Site SHAHID MASH 4 Contact Phone / Mob. No: 9447753481 5 Defective Product Details E8331BPL1_DG : 1 PCS 6 Nature of Defect Not working 7 Shutdown availability if applicable Yes 8 Warranty Status Under Warranty 9 Commissioned / Installed date Before Three Months 10 Serial No: or DOM of the Product 11 Name & Phone No: of Person Registering the Complaint LAN Marketing 8075581561 -- Thanks & RegardsLAN MARKETING 12/16 M-S Opp.Juma Masjid Areekode-Kondotty Road Chemrakkattur Pin-673639 Customer Care: 8304903103 | 2023-09-25 | 2023-09-28 16:43 | No | Warranty | SHAHID MASH | KULIRATHARI ELETTIL, ELETTIL (PO) ELETTIL-PARAPPANPOYIL ROAD, ELETTIL | KOZHIKODE | 673572 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Rejilesh APSMarketingCompany Calicut | APS Marketing Company | visit this customer place AvatarOn, push button for doorbell sometime not working E8331BPL1_DG_G8 replaced problem solved | Repair |  | 8- Service Completed | 2023-09-28 16:53 |  |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11283276 | 104143487 | 2023-09-20 15:35 | 2023-09-21 |  | 2023-09-20 09:42 | IH101ZWIFI | IH101ZWIFI | IH101ZWIFI |  | Wiser installation Phase 4 for HT Please Raise the Wiser Installation for Hindustan Times Phase 4 Automation Gateway IH101ZWIFI - Qty---1 4 Channel Automation Relay-IH14000100 - Qty---5 | 2023-09-20 | 2023-09-22 03:52 | No | Commercial Action - Sales | SURENDRA PRTAP SINGH | Shashi Park Rd, Mayur Vihar | Delhi | 110091 | Delhi | India FS ED&I CSP North Team Seamtek International Pvt. Ltd. GHAZIABAD | Satish Raika Seamtek International Pvt. Ltd. GHAZIABAD | Seamtek International Pvt. Ltd. | following wiser components has been installed gateway: 1 qty 4 ch. relay :5 qty | Commissioning & Installation | Start-up | 8- Service Completed | 2023-09-22 16:53 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11304937 | 104238397 | 2023-09-26 17:39 | 2023-09-25 |  | 2023-09-25 14:21 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Fw: Complaint of Smart Door bell- Mr. Gagandeep Singh, sector 38, Chandigarh Dear Team, The smart door bell installed at customer site is not working properly. Please arrange a technician visit at the site ASAP. The details of customer are as follows: Product Name: WISER Smart Door Bell Qty: 1 No Name: Mr. Gagandeep Singh Installation Address: House Number 3533, Sector 37-D, Chandigarh Pincode:160037 Mobile No. 9464250106, 8360361651 Installation : Done (Not working) Broadband with wifi Available: Yes Regards Pardeep kumar Schneider Electric Mohali M: 8360361651 | 2023-09-25 | 2023-09-26 17:40 | No | Warranty | Gagandeep Singh | House Number 3533, Sector 37-D | Chandigarh | 160036 | Chandigarh | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Vinod Kumar_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the vdp found not working properly due to WIFI wrong issue. Hence fault door bell is health ok. WIFI Signal - 10% dbm - 85dbm up load speed - 4.0 mbp5 Down load speed - 1.0 mbp5 email : id not provided by the customer. | Repair |  | 8- Service Completed | 2023-09-26 17:50 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11283287 | 104143538 | 2023-09-20 15:10 | 2023-09-20 |  | 2023-09-20 09:49 | IH101ZWIFI | IH101ZWIFI | IH101ZWIFI |  | Wiser installation Phase 4 for HT Please Raise the Wiser Installation for Hindustan Times Phase 4 Automation Gateway IH101ZWIFI - Qty---1 4 Channel Automation Relay-IH14000100 - Qty---5 | 2023-09-20 | 2023-09-21 00:59 | No | Commercial Action - Sales | UMA DEVI | Shashi Park Rd, Mayur Vihar | Delhi | 110091 | Delhi | India FS ED&I CSP North Team Seamtek International Pvt. Ltd. GHAZIABAD | Satish Raika Seamtek International Pvt. Ltd. GHAZIABAD | Seamtek International Pvt. Ltd. | following wiser components has been installed gateway: 1 qty 4 ch. relay :5 qty | Commissioning & Installation | Start-up | 8- Service Completed | 2023-09-22 17:01 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11305010 | 104241485 | 2023-09-26 10:45 | 2023-09-25 |  | 2023-09-25 14:44 | A9N4P63C | A9N4P63C | A9N4P63C |  | Dear sir , model -A9N4P63C serial no. - d2224 problem - dolly free site name - shalimar maryied address- 21/ 23 railway colony near jhansi railway station jhansi up . Pin code - 284003 contact person - shubhankar sawant site incharge contact no . - 8896721663 Kindly proceed with this complaint as soon as possible. | 2023-09-25 | 2023-09-26 13:50 | No | Warranty | Shalimar Maryied | 21/ 23 railway colony near jhansi railway station | Jhansi | 284003 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Aman Khare_Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found it's having site voltage issue, MCB working fine . | Repair |  | 8- Service Completed | 2023-09-26 13:52 |  |  | 428 | INR | 428 | ENM HOME DISTRIBUTION
WO-11283292 | 104143626 | 2023-09-20 15:17 | 2023-09-20 |  | 2023-09-20 09:57 | IH101ZWIFI | IH101ZWIFI | IH101ZWIFI |  | Wiser installation Phase 4 for HT Please Raise the Wiser Installation for Hindustan Times Phase 4 Automation Gateway IH101ZWIFI - Qty---1 4 Channel Automation Relay-IH14000100 - Qty---5 | 2023-09-20 | 2023-09-21 03:30 | No | Commercial Action - Sales | SANJAY JANGRA | Shashi Park Rd, Mayur Vihar | Delhi | 110091 | Delhi | India FS ED&I CSP North Team Seamtek International Pvt. Ltd. GHAZIABAD | Satish Raika Seamtek International Pvt. Ltd. GHAZIABAD | Seamtek International Pvt. Ltd. | following wiser components has been installed gateway: 1 qty 4 ch. relay :5 qty | Commissioning & Installation | Start-up | 8- Service Completed | 2023-09-22 15:32 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11305019 | 104243093 | 2023-09-25 15:35 | 2023-09-25 |  | 2023-09-25 14:44 | A9N16258 | A9N16258 | A9N16258 |  | RCCB 16 AUGUST 2023 Ashoka electronics Invoice number : GJ-128736783-2324 BO7SVVXNDF A9N16258 Address: Varayil House, AZCHAVATTAM, MANKAVU KOZHIKODE 673007 NishaL L 985371283 | 2023-09-25 | 2023-09-28 15:14 | No | Warranty | NishaL NishaL | Varayil House, AZCHAVATTAM, MANKAVU | KOZHIKODE | 673007 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Rejilesh APSMarketingCompany Calicut | APS Marketing Company | visited this site found Acti 9 xID residual circuit breaker - 63 A 4pole test button not working A9N16258 replaced problem solved | Repair |  | 8- Service Completed | 2023-09-28 15:17 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11284955 | 104144173 | 2023-09-20 16:10 | 2023-09-20 |  | 2023-09-20 11:13 | CSC316RP-GY-EX | CSC316RP-GY-EX | CSC316RP-GY-EX |  | Warning: Email body is too large and was truncated at 32 000 characters. Information may have been lost. Dear Team, Request you to register a complaint based on the details provided. SITE CONTACT DETAILS Suresh A Senior Manager I ¦ M&E ? REE, Sobha Limited Sobha Gardenia, Kanniamman Kovil Street, Vengaivasal, Chennai ? 600126. Mobile: +91 9788859273 Email: suresh.a@sobha.com Best Regards, Ganeshkumar S 9500086392 Get Outlook for Android Internal Internal From: praveen.c@sobha.com <praveen.c@sobha.com> Sent: Wednesday, September 20, 2023 10:32:46 AM To: Ganeshkumar Ganeshkumar <Ganeshkumar.S@se.com>; 'VINOD N R' <vinodnr@techmechelectrify.com>; 'Sakshi Rao' <sakshirao@techmechelectrify.com>; chennaisales@techmechelectrify.com <chennaisales@techmechelectrify.com>; SM APA Customercare IN <Customercare.IN@schneider-electric.com> Cc: 'Binu P S(SM-Purchase)' <binu.s@sobha.com>; 'Srinivasan R (SM - Cont)' <ramaswamy.srinivasan@sobha.com>; 'gardenia.electrical' <gardenia.electrical@sobha.com>; 'VinodKumar N (VP-M&E)' <vinodkumar.n@sobha.com>; suresh.a@sobha.com <suresh.a@sobha.com> Subject: REPEATED ISSUE-----Damages in weather proof socket - CSO316RP & CSC316--SOBHA GARDENIA [External email: Use caution with links and attachments] Dear Concerned, Please find the attached mail from the site and please provide the rectification process to close the issue asap SITE CONTACT DETAILS Suresh A Senior Manager I ¦ M&E ? REE, Sobha Limited Sobha Gardenia, Kanniamman Kovil Street, Vengaivasal, Chennai ? 600126. Mobile: +91 9788859273 Email: suresh.a@sobha.com Praveen C Assistant Manager¦ Procurement Sobha Limited Polyhose Towers, 5th Floor, SPIC Annex, #88,Mount Road, Guindy, Chennai ? 600 032 Tel: 044-22350115/16 ¦ Mobile: 9384063666 Email: praveen.c@sobha.com www.sobha.com From: praveen.c@sobha.com <praveen.c@sobha.com> Sent: Tuesday, September 19, 2023 10:25 AM To: 'Ganeshkumar Ganeshkumar' <Ganeshkumar.S@se.com>; 'VINOD N R' <vinodnr@techmechelectrify.com>; 'Sakshi Rao' <sakshirao@techmechelectrify.com>; 'chennaisales@techmechelectrify.com' <chennaisales@techmechelectrify.com> Cc: 'Binu P S(SM-Purchase)' <binu.s@sobha.com>; 'Srinivasan R (SM - Cont)' <ramaswamy.srinivasan@sobha.com>; 'gardenia.electrical' <gardenia.electrical@sobha.com>; 'VinodKumar N (VP-M&E)' <vinodkumar.n@sobha.com>; 'suresh.a@sobha.com' <suresh.a@sobha.com> Subject: REPEATED ISSUE-----Damages in weather proof socket - CSO316RP & CSC316--SOBHA GARDENIA Awaiting response Praveen C Assistant Manager¦ Procurement Sobha Limited Polyhose Towers, 5th Floor, SPIC Annex, #88,Mount Road, Guindy, Chennai ? 600 032 Tel: 044-22350115/16 ¦ Mobile: 9384063666 Email: praveen.c@sobha.com www.sobha.com CSC316RP-GY-EX Invoice Date 24/August/2022 Invoice Number : TE/1354/22-23 From: praveen.c@sobha.com <praveen.c@sobha.com> Sent: Thursday, September 14, 2023 5:24 PM To: 'Ganeshkumar Ganeshkumar' <Ganeshkumar.S@se.com>; 'VINOD N R' <vinodnr@techmechelectrify.com>; 'Sakshi Rao' <sakshirao@techmechelectrify.com>; 'chennaisales@techmechelectrify.com' <chennaisales@techmechelectrify.com> Cc: 'Binu P S(SM-Purchase)' <binu.s@sobha.com>; 'Srinivasan R (SM - Cont)' <ramaswamy.srinivasan@sobha.com>; 'gardenia.electrical' <gardenia.electrical@sobha.com>; 'VinodKumar N (VP-M&E)' <vinodkumar.n@sobha.com>; 'suresh.a@sobha.com' <suresh.a@sobha.com> Subject: REPEATED ISSUE-----Damages in weather proof socket - CSO316RP & CSC316--SOBHA GARDENIA Dear Sir, Please find the attached mail from the site and please provide the rectification process to close the issue asap Praveen C Assistant Manager¦ Procurement Sobha Limited Polyhose Towers, 5th Floor, SPIC Annex, #88,Mount Road, Guindy, Chennai ? 600 032 Tel: 044-22350115/16 ¦ Mobile: 9384063666 Email: praveen.c@sobha.com www.sobha.com | 2023-09-20 | 2023-09-22 18:55 | No | Warranty | Sobha Limited | Kanniamman Kovil Street, Vengaivasal null | Chennai | 600126 | Tamil Nadu | India FS South2 ED&I CSP UpservePowerSystems Chennai | HARI PRASATH UpservePowerSystems Chennai | Upserve Power Systems | CSO316RP-GY-EX - 15 nos replacement is given. | Repair |  | 9- Service Validated | 2023-09-22 19:37 | CSO316RP-GY-EX this is booked CSC316RP-GY-EX this is IN blocked |  | 19 | INR | 19 | ENM HOME DISTRIBUTION
WO-11305106 | 104240471 | 2023-09-25 17:24 | 2023-09-25 |  | 2023-09-25 14:58 | MTN6725-0004 | MTN6725-0004 | MTN6725-0004 |  | DEAR SIR, Please send your engineer at following address:- NAME- MR RISHI JALAN ADDRESS-ARUN CHAMBER P-38 INDIA EXCHANGE PLACE 2ND FLOOR KOLKATA-700001 CONTACT PERSON-BHIM CHOUDHARY NUMBER-9831329880 PROBLEM- MTN6725-0004 DALI 2 CHANNEL GATEWAY-1NOS PRODUCT-NOTWORKING STATUS-WARRANTY Warm Regards, Khushboo Begani Designer Electricals P-38 India Exchange Place 2nd Floor Kolkata-700001 (M)9831041229 (O)033-22376001/71341468 Experience Studio Soluintel Pvt Ltd 10a,Kapalitola Lane,Room 3D, 3rd Floor,Kolkata - 700012 http://www.soluintel.com (O)033-40069244 P Please don't print this Email unless you really need to - this will preserve trees on planet earth | 2023-09-25 | 2023-09-27 15:04 | No | Warranty | DESIGNER ELECTRICALS | P-38 INDIA EXCHANGE PLACE 2ND FLOOR KOLKATA- | Kolkata | 700001 | West Bengal | India FS ED&I CSP East Team SREYAM SERVICES BHATPARA | AMIT BHATTACHARYA_SREYAM SERVICES BHATPARA | Sreyam Services(8513) | AFTER SITE VISIT FOUND KNX DALI GATEWAY CHECK AND COLLECTED, NEW MATERIAL DIRECT ORDER BY CUSTOMER SITE. | Repair |  | 8- Service Completed | 2023-09-27 15:07 |  |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-11285183 | 104147049 | 2023-09-20 13:58 | 2023-09-20 | Validated By Prashant | 2023-09-20 12:44 | IN8401_N | IN8401_N | IN8401_N |  | Zencelo 1 switcheches IN8401_N Invice date : 2 september 2023 801 e wingh ABT appartment Rnai city marg M 400097 Neha poddar. | 2023-09-20 | 2023-09-21 13:42 | No | Warranty | Neha Poddar | 801, ABT Apartment, A wing, Ranisati Marg, Malad | Mumbai | 400097 | Maharashtra | India FS ED&I CSP West Team S K SERVICES Mumbai | Ganesh Tati_S K SERVICES Mumbai | S.K. Services (10237) | We Visited the site Product Ref No:-IN8486/32-2Nos Serial No:-23146,23353 We check the material 32A DP switch is properly Not Operating. One Switch We solve And another one is replace. | Repair |  | 9- Service Validated | 2023-09-21 13:45 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11305197 | 104240093 | 2023-09-25 15:48 | 2023-09-25 |  | 2023-09-25 15:13 | SAE-UE-MS-CSBWE | SAE-UE-MS-CSBWE | SAE-UE-MS-CSBWE |  | Dear Team, Please find the below mail. Please login a new complaint. We attend the site. -------- Original Message -------- Subject:Re: WO-11289950 from Schneider ElectricDate:21.9.2023 17:40From:SAFFRON AUTOMATION <support@saffronautomation.com>To:Schneider-Electric <vibhuti.arora@se.com>Cc:Anand Rai <Anand.Rai@se.com>, ashu kumar <ashukumar@saffronautomation.com> Dear Mam, We contact to customer (Mr. Mohit / Mob. 9720145179), his provided the schedule for site visit on Saturday. Please cancel the subject complaint, After attend the site we re-login the complaint. On 21.9.2023 11:28, Schneider-Electric wrote: Hello, WO-11289950 has been assigned to Saffron Automation(18001). Work Order Type: Repair Work Order Sub Type: Customer Name: Mohit Mohit Customer Location: Mohit Mohit - SITE Contact Name: Mohit Mohit Case : 104174446 Schneider Planner: Vibhuti Arora Main Installed Product Name : SAE-UE-MS-CSBWE Main IP Serial Number : Work Order Reason:RE: FW: Pernod Ricard !! Sensor issue [ thread::dqD522UMdBqJBsBTyvgMsz4:: ]Exact model reference of faulty sensors along with qty .-Model no is SAE-UE-MS-CSAWE-2nos2. Serial number or invoice copy of authorize distributor to validate the warranty -Our invoice number HSV-2324-0919 is attached herewith.3. Complete site address containing (Plot No/Shop No/Street No/Landmark and Postal code ) -Site address is Pernod Ricard,12th Floor,Tower-B,DLF Cyber Park,Sector 20,Gurgaon.Contact person is Mr Mohit-Mob no 9720145179 Thank You -- ? ? Thanks & Regards Saffron Automation Address: B23 2ND FLOOR PATPARGANJ INDUSTRIAL AREA DELHI-110092 Phone: +91 9599294666 ¦ Mobile: +91 9599294664 Email: support@saffronautomation.com ¦ Web: www.saffronautomation.com ¦ Product Ranges: AC Drive ¦ PLC ¦ HMI Display ¦ AC Servo System ¦ UPS ¦ Sensors ¦ Temp. Controller ¦ Power Supply ¦ Encoder ¦ Customised Control,Power,VFD/PLC Panels ¦ Electronic Components ¦ LV Switch-gear Please don't print this e-mail unless you really need to..... -- ? ? Thanks & Regards Saffron Automation Address: B23 2ND FLOOR PATPARGANJ INDUSTRIAL AREA DELHI-110092 Phone: +91 9599294666 ¦ Mobile: +91 9599294664 Email: support@saffronautomation.com ¦ Web: www.saffronautomation.com ¦ Product Ranges: AC Drive ¦ PLC ¦ HMI Display ¦ AC Servo System ¦ UPS ¦ Sensors ¦ Temp. Controller ¦ Power Supply ¦ Encoder ¦ Customised Control,Power,VFD/PLC Panels ¦ Electronic Components ¦ LV Switch-gear Please don't print this e-mail unless you really need to..... | 2023-09-25 | 2023-09-25 17:41 | No | Warranty | Mohit Mohit | Pernod Ricard,12th Floor,Tower-B,DLF Cyber Park,Sector 20, | Gurgaon | 122016 | Haryana | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the sensor and found sensor have connection and programming issue. We suggest to customer please check the connection and programming. We check the sensor and sensor working ok. | Repair |  | 8- Service Completed | 2023-09-25 17:44 |  |  | 1 | INR | 1 | ENM HOME DISTRIBUTION
WO-11285584 | 104146282 | 2023-09-20 17:38 | 2023-09-20 |  | 2023-09-20 14:43 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Hi Team, Please Raise the Wiser Smart Door Bell repair WO for below Customer.. Jayanthi prem No 405, Sankalp Central Park Jawa Main Rd, Medar Block, Yadavagiri, Mysuru, Karnataka 570020 9945415386 IH100WFVDP ? 1 Qty SD028213330476 Smart Door bell unable to reset or connect to WiFi Warm Regards Ramakanth Kumathe Lighting Controls Home and DistributionSchneider Electric M +91 80073 65462E ramakanth.kumathe@se.com Bearys Global Research Traingle 63/3B, Whitefield Ashram Road Govigere Village, Bidarahalli Hobli Bangalore - 560067 India Now Raise Wiser Installation or troublshoot through chat https://www.se.com/in/en/work/support/customer-care/contact-schneider-electric.jsp *Please consider the environment before printing this e-mail Internal From: AUTOMETA <autometa.in@gmail.com> Sent: Wednesday, September 20, 2023 11:39 AM To: SM APA India Info <indiainfo@se.com> Cc: Ramakanth Kumathe <Ramakanth.Kumathe@se.com> Subject: Replacement of faulty device [External email: Use caution with links and attachments] Dear Team, We have received a faulty device from Clinets place after installation.Client is facing communication issues with the device.So after consulting with Mr Ramakanth we have sent the device for replacement to local service partner.Request you to do the needful. Regard Falak Store Incharge Autometa | 2023-09-20 | 2023-09-28 14:08 | No | Warranty | Jayanthi Prem | No 405, Sankalp Central Park, Jawa Main Rd, Medar Block, Yadavagiri | Mysore | 570020 | Karnataka | India FS South1 ED&I CSP AlternatePowerSupplies Mysore | A.R.Bhanu Prakash AlternatePowerSupplies Mysore | Alternate Power Supplies | Door bell was dead, Replaced the doorbell | Repair |  | 9- Service Validated | 2023-09-28 13:08 |  |  | 1 | INR | 1 | ENM HOME DISTRIBUTION
WO-11305249 | 104244798 | 2023-09-25 16:16 | 2023-09-25 | Switch not working | 2023-09-25 15:23 | X1001WH_N | X1001WH_N | X1001WH_N |  | opale switch complaint Opale ---2 pcs 10 years warranty Sushil Kalawatia---9987007535 Greens Flat# F904 Building maple Aditya Birla Hospital Marg, Opp Pudumjee Paper Mill, Thergaon, Pimpri-Chinchwad pune 411033 | 2023-09-25 | 2023-09-26 12:00 | No | Warranty | Sushil Kalawatia | Greens Flat# F904 Building maple Aditya Birla Hospital Marg, Opp Pudumjee Paper Mill, Thergaon, Pimpri-Chinchwad | pune | 411033 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Sachin Jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the switch found that the Switch is not working it's found broken from inside the board . so this problem is not repairable.So switch Needs to be replaced, Required Material : X1001WH - 03 nos. we arranged the material from our stock and replaced it. | Repair |  | 9- Service Validated | 2023-09-26 15:46 | =S= Consig Fill up 226079565 |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11285939 | 104154180 | 2023-09-20 17:51 | 2023-09-20 | NA | 2023-09-20 16:13 | E8334L1_DG_G5 | E8334L1_DG_G5 | E8334L1_DG_G5 |  | AVATAR 5 mpr switches E8334L1_DG_G5 EA315 Laduram Tusewal Invoi 10/8/23 Ritu Kanori 9903884949 12/3 Baliganj Park Road, PS esemtrada Kolkata wb 700019 | 2023-09-20 | 2023-09-21 15:45 | No | Warranty | Ritu Kanori | 12/3 Baliganj Park Road, PS esemtrada | Kolkata | 700019 | West Bengal | India FS ED&I CSP East Team B.D Electroservices Kolkata | RAHUL RAY_B.D Electroservices Kolkata | B.D Electroservices(500017330) | Visited site and we found there is a no issue found. Material is Ok. | Repair |  | 9- Service Validated | 2023-09-21 17:10 |  |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-11099962 | 103173994 | 2023-09-11 17:04 | 2023-08-10 |  | 2023-08-10 15:09 | X1001WH | X1001WH | X1001WH |  | Approved by Yuvaraj for site inspection only. Kindly ask engineer to share the images of faulty switches and detailed report along with batch code. Re: Sobha Forest View Aparts, Kanakapura Road - Electrical Fittings Issue [ thread::sO55Ivbvf-KUUW9G-EY7fD4:: ] | 2023-08-10 | 2023-09-13 09:43 | No | Warranty | Vyju Krishnan | # 3/1, JP Techno Park, Millers Road, Vasanth Nagar, Bangalore | Bengaluru | 560062 |  | India FS ED&I CSP South Team PSK Power Controls Bangalore | Chethan SC P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | Inspected and found below mentioned 1)Ref:X1001WH S/N:21032L = 3 No'S 2)Ref:X1002WH S/N:21404L = 1 No Switches Switches was not working and after switches replaced and fixed tested working found ok Hence we have replaced new good warranty replacement from our PKS stock | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-13 09:44 |  |  | 17 | INR | 17 | ENM HOME DISTRIBUTION
WO-11305447 | 104245610 | 2023-09-27 15:35 | 2023-09-25 |  | 2023-09-25 16:13 | UNS61SW1M_WE | UNS61SW1M_WE | UNS61SW1M_WE |  | Dear team, Pls register complaint of UNICA_PURE UNS61SW1M_WE Akash Chawla House number 206-207 near Chautala house Ram colony Barnala Road Sirsa 125055 Haryana 8053000300 Invoice detail Arihant Electric Company Date : 11 SEPT 2023 Thanks & Regards, SANJAY KUMAR Manager-Sales Home and Distribution DivisionSchneider Electric http://www.facebook.com/SchneiderElectric Landline: +91 7087045622 Mobile: +91 9802600986 Email: sanjay.kumar1@se.com CC 18001030011/ 18004254272 2nd Floor, SCO 23,Sector 32,Chandigarh Road Ludhiana - 141010INDIA Download mySchneider app 24/7 support. Mobile catalog. Access to expert help. *Please consider the environment before printing this e-mail Internal | 2023-09-25 | 2023-09-27 15:40 | No | Warranty | Akash Chawla | House number 206-207 near Chautala house Ram colony Barnala Road | Sirsa | 125055 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Ram Ashish Sharma Electric Chandigarh | Sharma Electric works(1003) | checked the switches found play problem. hence faulty, replaced. UNS61SW1M_WE - 8 Nos. UNS161SWL1M_WE - 2 Nos. UNS62SW1M_WE - 3 Nos. UNS4STFAN1N_WE - 1 Nos. Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-27 17:38 |  |  | 3 | INR | 3 | ENM HOME DISTRIBUTION
WO-11285971 | 104149628 | 2023-09-20 17:32 | 2023-09-20 |  | 2023-09-20 16:28 | SAE-UE-MS-CDBWE | SAE-UE-MS-CDBWE | SAE-UE-MS-CDBWE |  | Dear Team,Please reissue the case no. Earlier it was cancelled .---------- Forwarded message ---------From: Complaints SEW Date: Mon, Sep 18, 2023 at 10:37?AMSubject: Case : 104082873 dt. 18.9.23To: Complaints SEW , SharmaElectric Cc: Ramkaran Yadav , Mukesh Kumar, Rajan SinghDear Sir,Mr. Manish NoolchandaniPlot no 221 , gyan marg , tilak nagar JaipurMr. Manish Noolchandani9829000090Product : SAE-UE-MS-CDBWEnot working--*WITH REGARDS-*Sarabjit SinghSHARMA ELECTRIC WORKS I CHANDIGARH I ADMIN. AUTH. SERVICE & SPARESDEALER : CROMPTON GREAVES & SCHNEIDER ELECTRIC INDIA*Tele FAX 0172-4629871E MAIL : complaints@sharmaelectricworks.com *Address : PLOT NO. 279, GF, INDUSTRIAL AREA,**PHASE-II, CHANDIGARH-160002 , Website : www.sharmaelectricworks.com**** Please consider the environment before printing this e-mail-- *WITH REGARDS-*Sarabjit SinghSHARMA ELECTRIC WORKS I CHANDIGARH I ADMIN. AUTH. SERVICE & SPARESDEALER : CROMPTON GREAVES & SCHNEIDER ELECTRIC INDIA*Tele FAX 0172-4629871E MAIL : complaints@sharmaelectricworks.com *Address : PLOT NO. 279, GF, INDUSTRIAL AREA,**PHASE-II, CHANDIGARH-160002 , Website : www.sharmaelectricworks.com**** Please consider the environment before printing this e-mail | 2023-09-20 | 2023-09-20 17:36 | No | Warranty | Manish Noolchandani | plot no 221 , gyan marg , tilak nagar | Jaipur | 302004 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | Checked the sensor found working ok. Email : id not provided by customer. | Repair |  | 8- Service Completed | 2023-09-20 17:40 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11305496 | 104242418 | 2023-09-26 11:40 | 2023-09-25 | NA | 2023-09-25 16:43 | UNS5STFAN2M_WE | UNS5STFAN2M_WE | UNS5STFAN2M_WE |  | Dear Sir, Please visit the site client are chasing for defective material MR PRADEEP GATTANI-9432227970 Warm Regards, Khushboo Begani Designer Electricals P-38 India Exchange Place 2nd Floor Kolkata-700001 (M)9831041229 (O)033-22376001/71341468 Experience Studio Soluintel Pvt Ltd 10a,Kapalitola Lane,Room 3D, 3rd Floor,Kolkata - 700012 http://www.soluintel.com (O)033-40069244 P Please don't print this Email unless you really need to - this will preserve trees on planet earth On Saturday, 1 July, 2023 at 10:58:13 am IST, designer electricals <designer_electricals@yahoo.in> wrote: DEAR SIR, Please send your engineer at following address:- NAME- MR PRADEEP GATTANI ADDRESS- SUNRISE HIGHTS 134 A BELEGHATA MAIN ROAD 21st floor Flat 2101 KOLKATA -700015 CONTACT PERSON- MR PRADEEP GATTANI NUMBER- 9432227970 PROBLEM- UNS5STFAN2M_WE 2M REGULATOR-2nos (multipal problem) PRODUCT-NOTWORKING STATUS-WARRANTY Invoice Detail Designer Electricals Kolkata Date : 25 April 2023 Warm Regards, Khushboo Begani Designer Electricals P-38 India Exchange Place 2nd Floor Kolkata-700001 (M)9831041229 (O)033-22376001/71341468 Experience Studio Soluintel Pvt Ltd 10a,Kapalitola Lane,Room 3D, 3rd Floor,Kolkata - 700012 http://www.soluintel.com (O)033-40069244 P Please don't print this Email unless you really need to - this will preserve trees on planet earth | 2023-09-25 | 2023-09-26 14:15 | No | Warranty | PRADEEP GATTANI | SUNRISE HIGHTS 134 A BELEGHATA MAIN ROAD 21st FLOOR FLAT 2101 | KOLKATA | 700015 | West Bengal | India FS ED&I CSP East Team B.D Electroservices Kolkata | KOUSHIK MONDAL_B.D Electroservices Kolkata | B.D Electroservices(500017330) | On received of ZVO material will delivered to customer. | Repair |  | 8- Service Completed | 2023-09-26 17:41 |  |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-11305497 | 104245519 | 2023-09-27 15:08 | 2023-09-25 |  | 2023-09-25 16:43 | E8315C_6_WE | E8315C_6_WE | E8315C_6_WE |  | Dear team, Pls register complaint of Avtar On Invoice Details: Arihant Electric Company 16 sep 2023 Detail of Customer TARSEM GROVER 190 B BLOCK Sirsa 125055 Haryana 9416359710 Thanks & Regards, SANJAY KUMAR Manager-Sales Home and Distribution DivisionSchneider Electric http://www.facebook.com/SchneiderElectric Landline: +91 7087045622 Mobile: +91 9802600986 Email: sanjay.kumar1@se.com CC 18001030011/ 18004254272 2nd Floor, SCO 23,Sector 32,Chandigarh Road Ludhiana - 141010INDIA Download mySchneider app 24/7 support. Mobile catalog. Access to expert help. *Please consider the environment before printing this e-mail Internal | 2023-09-25 | 2023-09-27 15:09 | No | Warranty | TARSEM GROVER | 190 B BLOCK | Sirsa | 125055 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Rakesh Kumar Sharma Electric Chandigarh | Sharma Electric works(1003) | checked the bell push button found play problem. hence faulty, replaced. E8331BPL1_DG_G8 - 2 Nos. Email: id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-27 17:43 |  |  | 3 | INR | 3 | ENM HOME DISTRIBUTION
WO-11286250 | 104157616 | 2023-09-20 18:50 | 2023-09-20 |  | 2023-09-20 18:13 | A9KF71232BQS | A9KF71232BQS | A9KF71232BQS |  | A9KF71232BQ Prakash electrical 17 september 2023 Pawan Kumar 7868038937 HNRKR Complex, Kodigehalli Main Road, KR Puram Bangalore 560036 | 2023-09-20 | 2023-09-27 10:30 | No | Warranty | Pawan Kumar | HNRKR Complex, Kodigehalli Main Road, KR Puram | Bengaluru | 560036 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | MANOJ GANESAN SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported mcb found on/off knob broken, in the box itself.on goodwill basis we had arranged for the replacement. | Repair |  | 8- Service Completed | 2023-09-27 11:51 |  |  | 12 | INR | 12 | ENM HOME DISTRIBUTION
WO-11290094 | 104176203 | 2023-09-21 17:26 | 2023-09-21 |  | 2023-09-21 12:13 | UNS161SW1M_GY | UNS161SW1M_GY | UNS161SW1M_GY |  | Invoice Details: 30 t march 2023 Hari Om lighting Chandni cHolk delhi 2309 UNICA GRAY COLOUR SOCKET SWITCH 4 SWITCHES ARE NOT WORKING Address C401 -Rohini Hights Sector 29, 110042 NEW DELHI Abhishek Sharma 9910747576. | 2023-09-21 | 2023-09-27 13:02 | No | Warranty | Abhishek Sharma | C401 -Rohini Hights Sector 29 | NEW DELHI | 110042 | Delhi | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the switches and found switches have dolly free issue. We replace the faulty switches with new. | Repair |  | 8- Service Completed | 2023-09-27 14:52 |  |  | 1 | INR | 1 | ENM HOME DISTRIBUTION
WO-11290261 | 104177705 | 2023-09-21 14:09 | 2023-09-21 | Hence this switch has need to be replaced.(4) Product details - X1181WH - 01Nos . | 2023-09-21 13:14 | X1181WH_N | X1181WH_N | X1181WH_N |  | Invoice Details : 4th november 2022 POS-P02938/22-23 Distributor: Radhika Cables and switch gares Model number / OPEL SWITCH 16 APR ONE WAY Flat Number B-1102, Malpani Greens Society, Waked Pune, 411057 MH Opposite Waked Food court Himanshu Kochar 9763372276. | 2023-09-21 | 2023-09-21 17:00 | No | Warranty | himanshu kochar | B-1102 Malpani Greens Society Kaspate vasti wakad opp Euro School | Pune | 411057 | Maharashtra | India FS ED&I CSP West Team Alliance Controls Pvt Ltd Pune | Shmabhu Bone_Alliance Controls Pvt. Ltd | Alliance Controls Pvt. Ltd. (7966) | 1)We visited at site discuss with customer & check the faulty switch after proper shutdown main supply.(2) Check faulty switch is broken doulby of switch . (3) Hence this switch has need to be replaced.(4) Product details - X1181WH - 01Nos . | Repair |  | 9- Service Validated | 2023-09-22 10:28 |  |  | 13 | INR | 13 | ENM HOME DISTRIBUTION
WO-11290272 | 104178583 | 2023-09-22 11:16 | 2023-09-21 |  | 2023-09-21 13:14 | UNS5STFAN2M_WE | UNS5STFAN2M_WE | UNS5STFAN2M_WE |  | UNICA WHITE COLOUR 5MPR UNS5STFAN2M_WE Sri Krihna Electricals Invoice Date: August Address; 16B/4E, Sunltana tanners compoud Asarfabad Knpur 208010 Chout 8467950158 | 2023-09-21 | 2023-09-23 14:48 | No | Warranty | Chotu Chotu | 16B/4E, Sunltana tanners compoud Asarfabad | Knpur | 208010 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Aman Khare_Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found fan regulator having speed variation issue so we replaced. | Repair |  | 8- Service Completed | 2023-09-23 14:54 |  |  | 115 | INR | 115 | ENM HOME DISTRIBUTION
WO-11290516 | 104181531 | 2023-09-22 13:06 | 2023-09-21 |  | 2023-09-21 14:59 | EZ9F71463 | EZ9F71463 | EZ9F71463 |  | 63 Apr 4pol EZ9F71463 3606480737442 19 January 2023 Hippo Stores Haryana Saevhit Bildwell Pvt Ltd. WA 29, Shakarpur Near Gurudwara , East Delhi 110092 singlasuresh22@gmail.com Suresh Singla 9873295396 | 2023-09-21 | 2023-09-22 13:08 | No | Warranty | Saevhit Bildwell Pvt Ltd | WA 29, Shakarpur Near Gurudwara , East Delhi null | Delhi | 110092 | Delhi | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the Rccb found working ok. Email : id not provided by customer. | Repair |  | 8- Service Completed | 2023-09-22 17:24 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11290603 | 104178794 | 2023-09-21 17:54 | 2023-09-21 | As per sr. no. product in warranty raise ZVO. | 2023-09-21 15:43 | IN84SFR_N | IN84SFR_N | IN84SFR_N |  | Checklist for the Registration of Service Request Sr. No Particulars Doc. Ref :- SE/CCC/002/V0.1 1 M/S. JSD RETAIL At & post village - Buhari, Ta-valod, DIST-Tapi, Pin- 394630, gujarat 2 Contact Person at Site : Name & Mobile No. PRATIK D SHAH- 9825339456 Alternate Mobile No : 3 Contact Person at Site - Email Address** 4 Product Issue Type (Please select from drop down of column C-9) 5 Are you ready to troubleshoot the issue remotely ? Yes/NO. If Yes, Our technical support engineer will call back to troubleshoot the issue remotely. 6 Defective Product Model/Part No (Pls refer FAQ sheet ) IN84SFR WH = 1 NO. 7 Nature of Defect* - Defects Video and Photographs 8 Shutdown availability if applicable YES 9 Photograph of product where Serial No/Batch Code or Date of Manufacturing printed - Please refer FAQ sheet to find the Batch code details on the products 10 Proof Of Purchase - Pease attach SE*** Authorised Partner Invoice soft copy along with this check list SR NO . 22381L , INVOICE DATE : 23-08-2022, TAX INVOICE: 58 11 Name & phone No: of person registering the Service Request PURVI SHAH- 9909252666 All fields are mandatory. Free of cost service visit subjected to warranty policy of the product and contract between Schneider Electric and buying party . Warranty will be check either by serial no/Batch code/DOM printed on the product or date of invoice of our authorised partner /Schneider Electric direct invoice or Contract . Warranty policy may be change product to product or contract with the customer.* Kindly share defect symptoms instead of "Not working", Please share the link of large files(product photoes or videoes) ** End user will receive a survey asking feedback on service SE*** - Schneider Electric Please fill above details and send this sheet to customer care, Customer care contact link is give below https://www.se.com/in/en/work/support/customer-care/contact-schneider-electric.jsp Please mention Service Request as key word and Product Name in email subject line e.g for Masterpact NW ACB Service Request - Service Request for Masterpact NW Our web site :- https:+C16+A2:C22+A1:C22 | 2023-09-21 | 2023-09-22 17:11 | No | Warranty | JSD RETAIL | At & post village - Buhari, Ta-valod null | Tapi | 394630 | Gujarat | India FS ED&I CSP West Team VARDHAMAN ELECTROSOFT Vadodara | MAHENDRA SINGH VARDHAMAN ELECTROSOFT Vadodara | VARDHAMAN ELECTROSOFT | We visited the site and checked the regulater and found that regulater is physically ok but not working. | Repair |  | 9- Service Validated | 2023-09-26 17:16 | =S= Consig Fill up 226072624 |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11290694 | 104184890 | 2023-09-22 10:01 | 2023-09-21 |  | 2023-09-21 16:28 | A9N2P63C | A9N2P63C | A9N2P63C |  | FW: REGARDING DEFECTIVE MCB Kindly register the complaint for E9 MCB. Invoice copy and customer details mentioned for your kind ref. Mohit Sharma Deputy Manager (Indirect Purchase) Mob. : 9717503008 Okaya Power Private Limited Baddi | 2023-09-21 | 2023-09-28 13:08 | No | Warranty | Okaya Fujikawa Power Pvt Ltd | Village Handa Kundi Nalagarh Road Bagwania | Baddi | 174101 | Himachal Pradesh | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Vinod Kumar_Sharma Electric Chandigarh | Sharma Electric works(1003) | checked the mcb found tripping issue. hence mcb received for testing purpose.Hence faulty replaced. A9N61539 - 2 Nos. email : id not provided by the customer. | Repair |  | 8- Service Completed | 2023-09-28 13:15 |  |  | 55 | INR | 55 | ENM HOME DISTRIBUTION
WO-11290763 | 104185265 | 2023-09-22 14:44 | 2023-09-21 |  | 2023-09-21 16:58 | A9N2P63C | A9N2P63C | A9N2P63C |  | MCB 2pol A9n2p63c 13/SEPTEMBER /2023 SB electricticals Shop number 1 ,Chuhan Market Street number 5 Mamura sector 66 noida Sanjay Parajapat 9818543412 | 2023-09-21 | 2023-09-22 14:46 | No | Warranty | Sanjay Parajapat | Shop number 1 ,Chuhan Market Street number 5 Mamura sector 66 | Noida | 201307 | Uttar Pradesh | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mcb found dolly free after reset and repairing , Mcb found working ok. Resolved by repair. Email : id not provided by customer . | Repair |  | 8- Service Completed | 2023-09-22 14:50 |  |  | 65 | INR | 65 | ENM HOME DISTRIBUTION
WO-11290812 | 104182511 | 2023-09-23 12:11 | 2023-09-21 |  | 2023-09-21 17:29 | A9KF71420 | A9KF71420 | A9KF71420 | 3606480740701 | Dear sir, Herewith attached photo for your reference , We are try to TURN ON and it was not holding. We need replacement. Thanks & Regards, 3606480740701 a9kf7 QC-RCL Karthik .S 8220265999 Ragavendra controls Pvt. Ltd., Vellanaipatti, Coimbatore ? 641 048, Tamil Nadu, India. E.MAIL :qc@rclindia.in | 2023-09-21 | 2023-09-27 17:00 | No | Warranty | RAGAVENDRA CONTROLS PRIVATE LIMITED | Site Address 6855\1A MOLAPALAYAM ROAD VELLANAIPATTI POST | COIMBATORE | 641048 | Tamil Nadu | India FS ED&I CSP South Team Power Pro Engineering Services Coimbatore | KV ARUNKUMAR_POWER PRO ENGINEERIG SERVICES COIMBATORE | Powerpro Engineering Services | WE HAVE VISITED THE SITE AND INSPETCED WE FOUND MCP ON& OFF DOLLY FREE DUE TO THIS INTERNAL ISSUE WE HAVE COLLECTED THE DETAILS FOR FURTHER ACTION AND ARRAGING FOR FREE REPALCEMENT FOR THIS AND COLLECTED THE DEFECTIVE | Repair |  | 8- Service Completed | 2023-09-27 17:01 |  |  | 21 | INR | 21 | ENM HOME DISTRIBUTION
WO-11290905 | 104187785 | 2023-09-23 11:42 | 2023-09-21 |  | 2023-09-21 18:06 | A9N3P63C | A9N3P63C | A9N3P63C |  | Complaints --MCB 63 amp 3 pole--2 pcs --MCB D2312 Fault:- Dolly free | 2023-09-21 | 2023-09-23 17:37 | No | Warranty | Jai Jagdamba Electrical | Village Kabdi , Nr Govt School, , | Panipat | 132103 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Karnail Singh Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the MCB found dolly free. Hence faulty replaced.. A9N3P63C - 2 Nos. email : rishimuni499@gmail.com | Repair |  | 8- Service Completed | 2023-09-23 17:40 |  |  | 165 | INR | 165 | ENM HOME DISTRIBUTION
WO-11290948 | 104188161 | 2023-09-22 11:42 | 2023-09-21 | Part order request validated by Chandrakant Panchal Sir | 2023-09-21 18:24 | CPX32DP2M_WE | CPX32DP2M_WE | CPX32DP2M_WE |  | Clipsal switch complaint 32 AMP DP - clipsal ---2 pcs invoice sep 2022 139 saket nagar manish puri auto stand Indore 452018 Akshay 7974987260 | 2023-09-21 | 2023-09-23 17:49 | No | Warranty | Akshay Akshay | 139 saket nagar manish puri auto stand | Indore | 452018 | Madhya Pradesh | India FS ED&I CSP West Team ABR Technical Service Indore | Mayank Patidar_ABR Technical Services Indore | ABR Technical Services (9574) | Visited site as per customer and checked following switches 1.) 20383L(CPX32DP2M_GY) 2.) 20383L(CPX32DP2M_GY) Checked switches and found stuck as per DOM Switches out of warranty. Customer provide invoice dated 03/09/2023 of livia switch .Customer purchased both livia and clipsal switches. Benefits of doubt and customer satisfaction we recommend to replace 2 Nos. switches. we request to customer please provide correct invoice next time. Note-Defective collected from site. | Repair |  | 9- Service Validated | 2023-09-23 17:51 | =S= Consig Fill up 226078940 |  | 10 | INR | 10 | ENM HOME DISTRIBUTION
WO-11295121 | 104205827 | 2023-09-22 11:27 | 2023-09-22 |  | 2023-09-22 10:54 | A9N2P16C | A9N2P16C | A9N2P16C |  | MCB Complaint Product : MCB A9N2P16C 16 Amps , 2 Pole MCB Sr No. D2225 DOM June 2022 Yes In warranty Problem : Not giving Output Phase Miss | 2023-09-22 | 2023-09-22 11:29 | No | Warranty | AK Engineering | Plot No-J 1145, Nr Relaxo Chownk, Bhiwadi, | Alwar | 301019 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mcb found phase missing, Hence faulty replaced. A9N2P16C - 1 nos Email : id not provided by customer. | Repair |  | 8- Service Completed | 2023-09-22 13:45 |  |  | 175 | INR | 175 | ENM HOME DISTRIBUTION
WO-11295345 | 104207470 | 2023-09-22 15:21 | 2023-09-22 |  | 2023-09-22 12:28 | E8315_16_DG | E8315_16_DG | E8315_16_DG |  | Name of Customer Ajithkumar U Site Address Avani House, Elamanamkunnu Road, Kottooli (PO) ,c Calicut - 673016 Calicut Name of contact person at site Ajithkumar U Contact Phone / Mob. No: 9947504595 Defective product details E8315_16_DG, E8315_6_DG , E8331D20N_DG_G8 Nature of Defect Not Working Shutdown availability if applicable Warranty status Inv.no. 222301324 dt 15-08-2022 Commissioned / Installed date Serial No: or DOM of the product Name & phone No: of person registering the complaint Invoice Details : Prime Syndicate, Calicut Date : 15/August/2022 ___________________________________________________________________________ Kamlesh Patel ¦ Prime Syndicate ¦ Calicut ¦ India ¦ Phone: +0495 2724258 ¦ Mobile: +91 9495942520 Email: primesyndicate.calicut@gmail.com ¦ primesyndicate@yahoo.com ¦ 17/1661,Pavamani Road, Calicut *** Please consider the environment before printing this e-mail | 2023-09-22 | 2023-09-27 16:24 | No | Warranty | Ajithkumar U | Avani House, Elamanamkunnu Road, Kottooli (PO) | Calicut | 673016 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Rejilesh APSMarketingCompany Calicut | APS Marketing Company | visited this site found AvatarOn, switched socket, 3P, 6 A, action missing E8315_6_DG - replaced problem solved | Repair |  | 8- Service Completed | 2023-09-27 16:27 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11295585 | 104209078 | 2023-09-22 15:25 | 2023-09-22 |  | 2023-09-22 14:03 | A9N1P25C | A9N1P25C | A9N1P25C |  | Fwd: Case : 104085277 dt. 18.9.23 Dear Sir, Mr. Mahinder RGAVP 3rd floor Udyog bhawan Jaipur Mr. Mahinder 7240157924 Product : A9N1P25C NOT WORKING -- *WITH REGARDS-* Sarabjit Singh SHARMA ELECTRIC WORKS I CHANDIGARH I ADMIN. AUTH. SERVICE & SPARES DEALER : CROMPT | 2023-09-22 | 2023-09-22 15:29 | No | Warranty | Mahinder Mahinder | RGAVP 3rd floog Udyog bhawan | Jaipur | 302005 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Sunny Sharma Sharma Electric Jaipur | Sharma Electric Works | Checked the mcb found working ok. Email : id not provided by customer. | Repair |  | 8- Service Completed | 2023-09-22 15:35 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-10544104 | 99587795 | 2023-03-24 16:24 | 2023-03-22 |  | 2023-03-22 16:08 | ATV930D45N4 | ATV930D45N4 | ATV930D45N4 | 4023500 JM201900829 | Failure of Drive Altivar 930, ATV930D45N4 Dear sir, This is to inform you that we have been facing frequent Drive failures for the newly commissioned LRWP Exit RT line. Today (28/11/22) reported one more drive failed. In this drive also the R& Y phase fuse was blown & Thyristor is short. since the commissioning out of 20 installed Drives, 8 Drives failed to date. With this failure trend, it's very difficult for us to run the production and keep Spares. Details: R & Y phase incoming side fuse Blown, checked the thyristor with multimeter Showing R Phase short. Product Details: Altivar 930, ATV930D45N4 Rating: 45KW-60 HP v 2.2 IE21 SL no-4023500JM201900829 We are still waiting for the solution for the same, as it's very regretful to say we are not getting support from M/s Schinder. It requested to kindly expedite the matter with Schneider and provide us with a concrete solution. @ Picture is attached for your reference. -- Best Regards, Kundan Kumar Rail Mill (Automation ¦¦ Electrical) Jindal Steel & Power Limited Kharasia Road, Raigarh (CG) Pin 496001 M +91 9109137498 E: kundan.kumar@jindalsteel.com | 2023-03-22 | 2023-08-08 10:41 | No | Warranty | JINDAL STEEL & POWER LTD | KHARSIA ROAD, PATRAPALI null | Raigarh | 496001 | chhattisgarh | India FS ED&I CSP East Team SOMDEV & COMPANY RAIPUR | SOUMYA BEHERA_SOMDEV & COMPANY RAIPUR | Somdev & Company | material ordered directly to customer site | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-15 10:42 |  |  | 0 | INR | 0 | Industrial Automation Ops
WO-11140474 | 103377079 | 2023-08-19 12:59 | 2023-08-19 |  | 2023-08-19 11:37 | MTN6215-5910 | MTN6215-5910 | MTN6215-5910 |  | DOP: 17/6/2023 MTN6215-5910-KNX MULTI TOUCH PRO P: THE UNIT DISPLAY SHOWS ERROR ON THE SCREEN WHEN POWERING ON AND AFTER DOWNLOADING THE PROGRAM. Johnson & Smith Co Unit 1 B 48 3rd Stage Peenya Industrial Estate Peenya Bangalore Bangalore Karnataka 560058 MR.KRISHNA PRASAD M 9900030357 | 2023-08-19 | 2023-09-25 16:56 | No | Warranty | Johnson & Smith Co | Unit 1 B 48 3rd Stage Peenya Industrial Estate Peenya null | Bangalore | 560058 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Nagaraja G_P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | Inspected found 1)Ref:MTN6215-5910 S/N:2023 = 1 No KNX multitouch pro display error issue. Hence we will give the above mentioned KNX Multitouch pro warranty replacement ASAP. | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-25 16:57 |  |  | 13 | INR | 13 | ENM HOME DISTRIBUTION
WO-11145198 | 103407135 | 2023-08-21 15:59 | 2023-08-21 |  | 2023-08-21 12:35 | IN8401_16_SP | IN8401_16_SP | IN8401_16_SP |  | Address Edakkalapurath (ho) varikkoli (po) kallachi,nadapuram Kozhikode 673506 Kerala India | 2023-08-21 | 2023-09-26 21:24 | No | Warranty | anwar ep | Edakkalapurath (ho) varikkoli (po) kallachi,nadapuram | Kozhikode | 673506 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Rejilesh APSMarketingCompany Calicut | APS Marketing Company | pramod sir arranged replacement material , we got the material, but customer available on next week. so close this case | Repair |  | 8- Service Completed | 2023-09-26 21:26 |  |  | 65 | INR | 65 | ENM HOME DISTRIBUTION
WO-11145415 | 103407544 | 2023-08-21 17:43 | 2023-08-21 |  | 2023-08-21 13:48 | E8331L1LED_WG_C1 | E8331L1LED_WG_C1 | E8331L1LED_WG_C1 |  | DOP: 1/8/2023 AvataOn E8331L1LED_WG_C1 P: Not Working Mohammed Javed New Number 2 old 33 Deivasigamani ( next to music academy) ROYAPETTAH CHENNAI 600014 Mohammed Javed 8056305159 | 2023-08-21 | 2023-09-09 19:03 | No | Warranty | Mohammed Javed Mohammed Javed | New Number 2 old 33 Deivasigamani ( next to music academy) ROYAPETTAH | Chennai | 600014 | Tamil Nadu | India FS South2 ED&I CSP UpservePowerSystems Chennai | HARI PRASATH UpservePowerSystems Chennai | Upserve Power Systems | We received socket also same issues. We educated the customer to use only international standard two pin plug in round two pin socket. | Repair |  | 9- Service Validated | 2023-09-09 19:23 |  |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-11150259 | 103444664 | 2023-08-22 17:56 | 2023-08-24 | Validated By Prashant | 2023-08-22 14:29 | IN8401_16_SP | IN8401_16_SP | IN8401_16_SP |  | DOP: 10 days old Zencelo Switches Qty: 10 P: Not Working Kindly check invoice at site | 2023-08-22 | 2023-09-04 19:30 | No | Warranty | Vishal Electrical | 102 starapurwala billing ,opt shiv shagar hotel,shpo no 3 ,grand floor west , mumbai 36 | Mumbai | 400011 | Maharashtra | India FS ED&I CSP West Team S K SERVICES Mumbai | Ganesh Tati_S K SERVICES Mumbai | S.K. Services (10237) | We Visited Site 6A 1 Way Switches is Properly Not Operating So Stuck issue and Lock Broken 32A DP Switches is Properly Not Operating So Stuck issue and Lock Broken 32A DP Switch is Not Operating So On/Off Operating Lock Broken | Repair |  | 9- Service Validated | 2023-09-04 20:30 | =S= Consig Fill up 225998074 |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11150399 | 103446701 | 2023-08-22 15:54 | 2023-08-22 |  | 2023-08-22 15:29 | EZ9EPS63SN | EZ9EPS63SN | EZ9EPS63SN |  | DOP: 12/10/2022 ez9eps63sn P: Not Working Mathew Joseph Ezhakth ethans Moonnalam Buypass road (behind Hyundai) Adoor Ph -7511113200 | 2023-08-22 | 2023-09-01 12:55 | No | Warranty | Mathew Joseph Mathew Joseph | Ezhakth ethans Moonnalam Buypass road (behind Hyundai) Adoor null | Pathanamthitta | 679335 | Kerala | India FS South2 ED&I CSP PrinterPeople Cochin | Renjith PR PrinterPeople Cochin | PRINTER PEOPLE-COCHIN | indicator purchased and replaced.. | Repair |  | 9- Service Validated | 2023-09-01 13:06 |  |  | 155 | INR | 155 | ENM HOME DISTRIBUTION
WO-11157510 | 103492439 | 2023-09-11 07:05 | 2023-08-24 |  | 2023-08-24 10:17 | IH14000100 | IH14000100 | IH14000100 |  | DOP: 23/8/2023 IH14000100 4 Channel Automation Relay IH101ZWIFI Automation Gateway Qty: 5 P: Installation Badrinath 779 1st floor 9th A main off 100 feet road Indiranagar 1st stage Bangalore-560038 Badrinath 9448312528 | 2023-08-24 | 2023-09-11 18:00 | No | Commercial Action - Sales | C & G Associates | 1st floor, No.779, 9th A Main Off 100 feet road Indiranagar 1st Stage | Bangalore | 560038 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Mohammad Riyaz_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | As per customer request we had visited and installed wiser 4channel relay -3nos, automation gateway - 1nos and checked thru Alexa, app and manually found working ok. The same shown to the customer. IH101ZWIFI-1 nos IH14000100- 3nos. | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-11 21:22 |  |  | 20 | INR | 20 | ENM HOME DISTRIBUTION
WO-11158305 | 103513953 | 2023-08-26 15:14 | 2023-08-24 |  | 2023-08-24 11:58 | IN8401_N | IN8401_N | IN8401_N |  | Zencelo Eco park 15 days back Mr. Ajit Singh ?hotel Jon by the park , d 65 a madhav singh raod banipark Jaipur 302016 Rajasthan Ind | 2023-08-24 | 2023-09-02 18:00 | No | Warranty | Ajit Singh | hotel Jon by the park , d 65 a madhav singh raod banipark | Jaipur | 302016 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Sunny Sharma Sharma Electric Jaipur | Sharma Electric Works | Checked the switch found not working, Hence faulty replaced. IN8401/16 - 2 nos Email :chiefeng.jpr@jonthepark.com | Repair |  | 9- Service Validated | 2023-09-04 15:04 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11158363 | 103514627 | 2023-08-24 15:25 | 2023-08-24 |  | 2023-08-24 12:18 | A9N3P63C | A9N3P63C | A9N3P63C |  | MCB of 63 amps 3 pole - pole open Socket is not working also JCB Power Products India Private Limited 23/7, Mathura Road, Ballabgarh 121004 Haryana Indi Mr. ABHISHEK KUMAR 7530847781 | 2023-08-24 | 2023-09-23 16:45 | No | Warranty | JCB Power Products India Private Limited | 23/7, Mathura Road, | Ballabgarh | 121004 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked mcb found phase missing, and switch found not giving output,Hence faulty replaced A9N3P63C - 1 nos PKF16F735 - 1 nos Email : id not provided by customer | Repair |  | 8- Service Completed | 2023-09-23 16:47 | 225984168 ZFRE BOOKED. |  | 45 | INR | 45 | ENM HOME DISTRIBUTION
WO-11158904 | 103519310 | 2023-08-25 11:49 | 2023-08-24 |  | 2023-08-24 16:25 | P1001_DG | P1001_DG | P1001_DG |  | DOP: 7/10/2022 P1001 : 10 PCS P1002 : 6 PCS P: Switch is Crack issue SALEEM EHIRAKKARI KUMMANKODE KALLACHI (PO) NADAPURAM KOZHIKODE - 673506 SALEEM EHIRAKKARI 7034680580, 9048052378 | 2023-08-24 | 2023-09-04 15:42 | No | Warranty | SALEEM SALEEM |  | Kozhikode | 673506 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found livia one way & two switchs dolly cracked P1001 60NOS P1002 20NOS replaced | Repair |  | 9- Service Validated | 2023-09-05 15:45 |  |  | 65 | INR | 65 | ENM HOME DISTRIBUTION
WO-11159019 | 103521233 | 2023-08-25 10:53 | 2023-08-25 |  | 2023-08-24 17:11 |  |  |  |  | DOP: 9/4/2022 A9R12491 Qty:1 P: Not Working BRIGHTSPORTS CENTER Vadacode P.O, Kangarappady, Kochi, Kakkanad, Kerala 682021 Behind Kanagarapady Town hall Ph: 9847099948 | 2023-08-24 | 2023-09-01 17:18 | No | Warranty | BRIGHTSPORTS CENTER | Vadacode P.O, Kangarappady, Kochi, | Ernakulam | 682021 | Kerala | India FS ED&I CSP South Team Geartech Electric Cochin | Vineesh M_Geartech Electric Cochin | Geartech Electric ASC for Schneider Electric | Inspected the RCCB and found the problem with nuisance tripping. To solve this need to replace the RCCB with a new one. | Repair |  | 9- Service Validated | 2023-09-01 19:20 |  |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-11163042 | 103553004 | 2023-08-28 14:00 | 2023-08-25 |  | 2023-08-25 15:24 | IN8486/32>SZ-PP | IN8486/32>SZ-PP | IN8486/32>SZ-PP |  | IN8486/ 32bz 3 158/159, Lalganga Shoping Mall, GE Road, Near Telephone Exchange Raipur 492001 Chhattisgarh India | 2023-08-25 | 2023-09-04 12:00 | No | Warranty | Yash Marketing | 158/159, Lalganga Shoping Mall, GE Road, Near Telephone Exchange | Raipur | 492001 | chhattisgarh | India FS ED&I CSP East Team SOMDEV & COMPANY RAIPUR | SOUMYA BEHERA_SOMDEV & COMPANY RAIPUR | Somdev & Company | the switches defective so we replace the same. | Repair |  | 9- Service Validated | 2023-09-04 13:00 |  |  | 12 | INR | 12 | ENM HOME DISTRIBUTION
WO-11167309 | 103570129 | 2023-08-27 15:51 | 2023-08-26 | We have done the Doorbell installation as per the customer requirements. System is working ok. | 2023-08-26 14:43 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | DOP: 3/8/2023 IH100WFVDP Smart Doorbell Qty:1 P: Installation MV Venu madhavarao NGOS Colony Narasaropet-522601 9440800377 | 2023-08-26 | 2023-08-31 11:31 | No | Commercial Action - Sales | KVN Radhika | NGOs colony, opp Govt hospital | Narasaraopeta | 522601 | Andhra Pradesh | India FS ED&I CSP South Team ENERPRO ENGINEERING SOLUTIONS Vijayawada | SK SIRAJUDDIN_ENERPRO ENGINEERING SOLUTIONS VIJAYAWADA | Enerpro Engineering Solutions - 500012682 | DOORBELL INSTALLATIOIN SUPPORT | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-01 11:39 |  |  | 67 | INR | 67 | ENM HOME DISTRIBUTION
WO-11172583 | 103585883 | 2023-08-30 11:49 | 2023-08-28 |  | 2023-08-28 11:16 | P1001_6_DG_N | P1001_6_DG_N | P1001_6_DG_N |  | DOP: 2 months Livia Switches: 15 , isolator-1 P: Not Working Kindly check invoice at site | 2023-08-28 | 2023-09-04 16:24 | No | Warranty | Riyan Riyan | Kagzi Colony Sanganer Near by Jama Masid | Jaipur | 302029 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | Checked the switch found jam issue, Hence faulty replaced P1001 - 8 nos Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-05 11:27 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11172981 | 103588032 | 2023-08-31 12:58 | 2023-08-28 |  | 2023-08-28 14:16 | UNS616SK2M_WE | UNS616SK2M_WE | UNS616SK2M_WE |  | DOP: 19/5/2022 UNS616SK2M_WE P: Not Working SIYAZ VP VALIYA PEEDIYAKKAL POONGODE POST MALAPPURAM-KERALA PIN: 679327 SIYAZ VP 9745580380 | 2023-08-28 | 2023-09-01 21:14 | No | Warranty | SIYAZ SIYAZ |  | Malappuram | 679327 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Rejilesh APSMarketingCompany Calicut | APS Marketing Company | visited this site found unica switchs struck issue unica 1way replaced 1nos problem solved | Repair |  | 9- Service Validated | 2023-09-01 21:28 |  |  | 70 | INR | 70 | ENM HOME DISTRIBUTION
WO-11172985 | 103591705 | 2023-08-28 16:28 | 2023-08-28 |  | 2023-08-28 14:17 | A9N3P32C | A9N3P32C | A9N3P32C |  | 32 amps 3 pole - on off issue 63 amps 4 pole - on off issue supply 2 month to customer - Shri Ganesh electrical faridabad sector 84 , adore legend Faridabad 121001 Haryana Mr. Ved Prakash ?Click to dial 7906007741 | 2023-08-28 | 2023-09-02 16:56 | No | Warranty | Ved Prakash | sector 84 , adore legend | Faridabad | 121001 | Haryana | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the MCB and found 3 Pole MCB have 1 phase missing issue and 4 Pole MCB have tripping after 15 minute. So MCB is faulty. We replace the faulty MCB with new. | Repair |  | 9- Service Validated | 2023-09-02 17:00 |  |  | 42 | INR | 42 | ENM HOME DISTRIBUTION
WO-11173075 | 103588840 | 2023-08-28 15:39 | 2023-08-28 |  | 2023-08-28 14:48 | A9N16201 | A9N16201 | A9N16201 |  | Dear - Sir Please mentioned project address Prestige Botanique First Cross, Rastriya Vidyalaya Rd, Upparahalli, Mavalli, Bengaluru, Karnataka 560004 9945410918 | 2023-08-28 | 2023-09-01 14:57 | No | Warranty | Prestige Botanique | First Cross, Rastriya Vidyalaya Rd, Upparahalli, Mavalli | Bangalore | 560004 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Nagaraja G_P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | Inspected and found below mentioned 1)Ref: A9KR11225 S/N:2021 = 1 No, RCCB test push button not working properly. Hence we will give same new warranty replacement ASAP. | Repair |  | 9- Service Validated | 2023-09-01 14:58 |  |  | 11 | INR | 11 | ENM HOME DISTRIBUTION
WO-11173316 | 103592547 | 2023-08-31 14:38 | 2023-08-28 |  | 2023-08-28 17:10 | EZ9R55463 | EZ9R55463 | EZ9R55463 |  | DOP: 19/9/2022 EZ9R55463 Qty : 1 PCS P: Not working ABDUL HAMEED MUNDA PALAM, KONDOTTY CHERUVAYOOR(PO) MALAPPURAM - 673645 ABDUL HAMEED 9745526174 | 2023-08-28 | 2023-08-31 13:59 | No | Warranty | ABDULHAMEED ABDUL | MUNDA PALAM KONDOTTY, EDAVANNAPARA | Malappuram | 673638 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found Easy9 Residual Current Circuit Breaker - 4P - 63A - 100mA test button not working EZ9R55463 replaced problem solved | Repair |  | 9- Service Validated | 2023-09-01 14:04 |  |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11176983 | 103601062 | 2023-08-29 11:14 | 2023-08-29 | As per telephonic discussion with mr.dattatray kute sir this product is need to be replaced. | 2023-08-29 09:46 | E5058NL_WE | E5058NL_WE | E5058NL_WE |  | E5058NL,WE -Not Working Qty- 1 which is not working at site . Kindly arrange to check the material at site.following details attached. Invoice No. Date Consignee Amt Qty 2021/CIHR00272 21-04-2022 Rexel India 136804.43 /- 1 Site Address 1st Floor , Flat no.3 , Shreeniwas Garden B wing , Shivajinagar , Pune -411016 Contact Person - Mr. Siddhu M. No - 7020489841/ 8308522562 Thanking You, | 2023-08-29 | 2023-09-04 17:42 | No | Warranty | SIDDHARTH SIDDHARTH | 1st Floor , Flat no.3 , Shreeniwas Garden B wing , Shivajinagar | Pune | 411016 | Maharashtra | India FS ED&I CSP West Team Alliance Controls Pvt Ltd Pune | Shmabhu Bone_Alliance Controls Pvt. Ltd | Alliance Controls Pvt. Ltd. (7966) | 1)Visited on site and checked clipsal C-bus key INP 8G-Neo-white product with C-bus voltage 34VDC but all keys blue indication blinking in low intensity. Also indication is not glowing after press key. 2)As per provided invoice copy of rexel india pvt ltd. Invoice No-2022/C14R03104, invoice date-04-11-2022 and as per invoice date product is in warranty. | Repair |  | 9- Service Validated | 2023-09-04 17:42 | =S= Consig Fill up 226010305 |  | 14 | INR | 14 | ENM HOME DISTRIBUTION
WO-11177332 | 103617888 | 2023-08-29 16:54 | 2023-08-29 | This product having under warranty, also this two way switch need has to be replaced. | 2023-08-29 10:39 | IN8401_N | IN8401_N | IN8401_N |  | Zencelo switch not working | 2023-08-29 | 2023-09-01 11:35 | No | Warranty | Nitin M | E905 , Ashwairam comfort gold , AKurdi | Pune | 411035 | Maharashtra | India FS ED&I CSP West Team Alliance Controls Pvt Ltd Pune | Shmabhu Bone_Alliance Controls Pvt. Ltd | Alliance Controls Pvt. Ltd. (7966) | 1)Visited to site and discuss with customer about complaint, done following activities: 2)For checking switch main supply shutdown, after that we found we faulty(2-way) switch on board(1 nos). | Repair |  | 9- Service Validated | 2023-09-04 11:38 |  |  | 10 | INR | 10 | ENM HOME DISTRIBUTION
WO-11178683 | 103618864 | 2023-08-29 20:39 | 2023-09-06 |  | 2023-08-29 13:54 | X1001WH_M3M_N | X1001WH_M3M_N | X1001WH_M3M_N |  | DOP: 7/3/2023 Opale Switches Qty: 40 P: Not Working C/o M/s. Electric Point 156-159 Paigah Apartment Secunderabad 500003. Krishna 9849471412 | 2023-08-29 | 2023-09-06 16:11 | No | Warranty | M/s. Electric Point | 156 159 Paigah apartments,S.P.Road null | Secunderabad | 500003 | Telangana | India FS ED&I CSP South Team Master Electrical Solutions Hyderabad | Narasimha Panusa_Master Electrical Solutions Hyderabad | Master Electrical Solutions | As per the complaint we have visited the customer and handed over the material to the customer. X1001WH - 40 Nos | Repair |  | 9- Service Validated | 2023-09-06 16:27 | Hi Team, Material booked zfre Zvo : 226022455 |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11178940 | 103623107 | 2023-08-29 16:16 | 2023-08-29 |  | 2023-08-29 15:41 | A9KF71463 | A9KF71463 | A9KF71463 |  | DOP: 3/8/2023 A9KF71463 Qty:1 P: Dolly free MULPUDI SARATH CHOUDHARY MY SHOP SURYABAGH VSP -530020 PHONE NUMBER : 9962059520 | 2023-08-29 | 2023-09-01 13:06 | No | Warranty | MULPUDI SARATH CHOUDHARY |  | Visakhapatnam | 530020 | Andhra Pradesh | India FS ED&I CSP South Team Voltamp Electrical Works Visakhapatnam | Vydha Venkatesh_VOLT AMP ELECTRICAL WORKS Visakhapatnam | Voltamp Electrical Works | visited the site and found above the Act 9 4 pole MCB is not working so we have observed the problem of MCB is mechanical on/off issue so zvo materiel replaced | Repair |  | 9- Service Validated | 2023-09-01 13:07 |  |  | 10 | INR | 10 | ENM HOME DISTRIBUTION
WO-11179134 | 103597582 | 2023-08-30 10:25 | 2023-08-29 |  | 2023-08-29 17:19 | UNS5STFAN2M_WE | UNS5STFAN2M_WE | UNS5STFAN2M_WE |  | I have purchased unica -P white 4 step Fan regulator (UNSESTFAN1M_WE) , Purchas | 2023-08-29 | 2023-09-02 16:01 | No | Warranty | Sreekanth Sreekanth | Kureeppuram House, Aruvappara | Enakulam | 653545 | Kerala | India FS South2 ED&I CSP PrinterPeople Cochin | Vysakht PrinterPeople Cochin | PRINTER PEOPLE-COCHIN | Replaced Fan regulator , now working fine | Repair |  | 9- Service Validated | 2023-09-03 22:10 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11179140 | 103630938 | 2023-08-30 11:45 | 2023-08-29 |  | 2023-08-29 17:24 | P1001_6_DG_N | P1001_6_DG_N | P1001_6_DG_N |  | DOP: 10/9/2022 P1120 Livia Switches Qty: 11 P: Not Working Kindly check invoice at site | 2023-08-29 | 2023-09-06 12:01 | No | Warranty | Balaram Balaram | Plot 679 Harish Market Near Petrol pump Basni 2nd stage | Jodhpur | 342005 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Amarjeet Singh Sharma Electric Jaipur | Sharma Electric Works | Checke the switch found not power up, Hence faulty replaced. P1101 - 5 nos P1002 - 1 nos P1132 - 1 nos P5001 - 4 nos Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-06 12:04 |  |  | 338 | INR | 338 | ENM HOME DISTRIBUTION
WO-11179211 | 103631765 | 2023-08-29 20:38 | 2023-08-29 |  | 2023-08-29 17:49 | IH14000100 | IH14000100 | IH14000100 |  | DOP: 5/6/2023 IH14000100 4 Channel Relay IH101ZWIFI Gateway P: Installation Name: Ashok Contact number: 9182268936 Location: Villa no 6, Kajipalli, Near Bachupalli, Hyd 500090. | 2023-08-29 | 2023-09-13 10:18 | No | Commercial Action - Sales | Ashok Ashok | Villa no 6, Kajipalli, Near Bachupalli, | Hyderabad | 500090 | Telangana | India FS ED&I CSP South Team Master Electrical Solutions Hyderabad | DEBANGSHU BOSE Master Electrical Solutions SECUNDERABAD | Master Electrical Solutions | Visited the site and carried out the following jobs. Its a installation request so we have installed the relay and briefly describe the operation to the customer . | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-13 10:22 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11182976 | 103636925 | 2023-08-31 17:10 | 2023-08-30 |  | 2023-08-30 11:01 | EZ9ESND12 | EZ9ESND12 | EZ9ESND12 |  | Customer name - shraddhay jain address - Near UMH hospital Rawatpura Road, Bhatagon, Raipur 492001 mob : 7089882766 product - SCHNEIDER EASY9 DB 12WAY SPN DD - 4pcs code - EZ9ESND12 problem - door lock not available , and patti , not complete -- THANKS & REGARD DAULAT RAM NISHAD Following attachments are linked to this email: 1.CODE.jpeg 2.VEDIO.mp4 3.DB.jpeg 4.DB1.jpeg | 2023-08-30 | 2023-09-06 12:00 | No | Warranty | Shraddhay Jain | Near UMH Hospital Rawatpura Road Bhatagon | Raipur | 492001 | chhattisgarh | India FS ED&I CSP East Team SOMDEV & COMPANY RAIPUR | SOUMYA BEHERA_SOMDEV & COMPANY RAIPUR | Somdev & Company | the db mcb cover and door lock is missing | Repair |  | 9- Service Validated | 2023-09-06 10:20 |  |  | 12 | INR | 12 | ENM HOME DISTRIBUTION
WO-11182989 | 103649405 | 2023-09-01 12:22 | 2023-09-08 |  | 2023-08-30 11:06 | IH14000100 | IH14000100 | IH14000100 |  | Sanjeev jain Alpha 19 Omaxe Rudrapur 9971290641 IH141000100-2pcs | 2023-08-30 | 2023-09-11 23:14 | No | Warranty | Sanjeev Jain | Alfa 19 Omaxe Rudrapur | Udham Singh Nagar | 244923 | Uttarakhand | India FS ED&I CSP North Team Seamtek International Pvt. Ltd. GHAZIABAD | Satish Raika Seamtek International Pvt. Ltd. GHAZIABAD | Seamtek International Pvt. Ltd. | following wiser components has been repaired and reconfigured 4 ch. relay: 2 qty note: we observer that there was wiring changed by client & due to that reason system was not operative wiring corrected | Repair |  | 9- Service Validated | 2023-09-11 11:15 |  |  | 240 | INR | 240 | ENM HOME DISTRIBUTION
WO-11183083 | 103651622 | 2023-08-30 13:24 | 2023-08-30 |  | 2023-08-30 11:53 | P1001_6_DG | P1001_6_DG | P1001_6_DG |  | DOP: 29/12/2022 P1001 P: Not Working 11B nfopark road Kakkanad SFS Sunnyvale Kakkanad Kerala 682030 Rani 9920980528 anoop@sfscochin.com | 2023-08-30 | 2023-09-01 13:24 | No | Warranty | Rani Rani | 11B nfopark road Kakkanad SFS Sunnyvale Kakkanad | Ernakulam | 682030 | Kerala | India FS South2 ED&I CSP PrinterPeople Cochin | Renjith PR PrinterPeople Cochin | PRINTER PEOPLE-COCHIN | 1 nos switch fault.. replaced | Repair |  | 9- Service Validated | 2023-09-01 13:26 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11183168 | 103654286 | 2023-08-30 17:00 | 2023-08-30 |  | 2023-08-30 12:26 | IN8486/32>SZ-OS | IN8486/32>SZ-OS | IN8486/32>SZ-OS |  | Zencelo 32 amps switch not working 8 26 , belakunilaya , sirmv lay out 5 th block ulaal Bangalore 560056 Karnataka India | 2023-08-30 | 2023-09-01 10:54 | No | Warranty | Praveen Deepa | 8 26 , belakunilaya , sirmv lay out 5 th block ulaal | Bangalore | 560056 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Chethan SC P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | Inspected and found below mentioned, 1)Ref:IN8486/32 S/N:22046L = 2 No'S Switches ON/OFF issues. Switches are replaced from our PKS stock. after tested switches are working found ok | Repair |  | 9- Service Validated | 2023-09-01 10:56 |  |  | 6 | INR | 6 | ENM HOME DISTRIBUTION
WO-11183185 | 103651911 | 2023-09-01 15:06 | 2023-08-30 |  | 2023-08-30 12:36 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Hi , Site address is Nova West 3401 Sector 94 Noida 201303. Contact Person: Mr Salman: +91-9818003697 Mr Anirudh : +91-7800001008. Please create Work Order to Seamtek International. Regards Anchal | 2023-08-30 | 2023-08-30 23:46 | No | Warranty | Salman salman | Nova West 3401 Sector 94 | Noida | 201303 | Uttar Pradesh | India FS ED&I CSP North Team Seamtek International Pvt. Ltd. GHAZIABAD | Satish Raika Seamtek International Pvt. Ltd. GHAZIABAD | Seamtek International Pvt. Ltd. | following wiser components has been installed gateway : 1 qty 4 channel relay : 3 qty | Repair |  | 9- Service Validated | 2023-09-11 11:48 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11183248 | 103655519 | 2023-08-31 11:07 | 2023-08-30 |  | 2023-08-30 12:59 | P6005 | P6005 | P6005 |  | Livia Key card 2 no , Purchased on 18th august from Viod enterprise in Chennai 160, govidapa , nykan street , Chennai 600001 Indi | 2023-08-30 | 2023-09-04 15:13 | No | Warranty | J Amar | 160, govidapa , nykan street , | Chennai | 600001 |  | India FS South2 ED&I CSP UpservePowerSystems Chennai | HARI PRASATH UpservePowerSystems Chennai | Upserve Power Systems | P6005 02 nos Replaced. | Repair |  | 9- Service Validated | 2023-09-04 15:16 | case registered in parent territory |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11183396 | 103656341 | 2023-08-30 19:51 | 2023-08-30 |  | 2023-08-30 14:08 | UNS5STFAN2M_WE | UNS5STFAN2M_WE | UNS5STFAN2M_WE |  | DOP: 6/9/2022 UNS5STFAN2M_WE P: Not Working One byte Jayanagara 1st cross Shivamogga. 577201 Sumukh Mob:8147085984 Mob: 8880666880 | 2023-08-30 | 2023-09-06 09:52 | No | Warranty | SUMUKH SUMUKH | Onebite Jayanagar 1st cross | Shivamogga | 577201 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | MANOJ GANESAN SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported 32Adp switches the problem found was switches got broken and knob broken, so we had replaced new and checked found working ok. The same shown to the customer. | Repair |  | 9- Service Validated | 2023-09-06 10:00 |  |  | 274 | INR | 274 | ENM HOME DISTRIBUTION
WO-11183724 | 103655913 | 2023-08-30 18:06 | 2023-08-30 |  | 2023-08-30 17:13 | UNS5STFAN2M_WE | UNS5STFAN2M_WE | UNS5STFAN2M_WE |  | DOP: 3/4/2023 Unicapure Switches UNS5STFAN2M_WE P: Not Working Vinod Dalabanjan Near Tolankere, Ravi nagar, Hubballi - 580030. +919844218173 | 2023-08-30 | 2023-09-11 10:31 | No | Warranty | Vinod Vinod | Near Tolankere, Ravi nagar | Hubli | 580030 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Nagaraja G_P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | Inspected the product 1)Ref:E8315_6_DG S/N:21376L = 4 No'S, strucking issue. 2)Ref: UNPSP8ML_MD = 7 No'S, colour was shaded products warranty replacement ASAP. | Repair |  | 9- Service Validated | 2023-09-11 10:32 |  |  | 10 | INR | 10 | ENM HOME DISTRIBUTION
WO-11183880 | 103664301 | 2023-09-01 10:25 | 2023-08-30 |  | 2023-08-30 18:29 | IH14000100 | IH14000100 | IH14000100 |  | DOP: 30/8/2023 IH14000100 4 Channel Relay IH101ZWIFI Gateway P: Installation Jose Lukose poondikulam house Mrala p o Thodupuzha Pin 685584 Ph: 9747152230, 9947383399. | 2023-08-30 | 2023-09-01 13:55 | No | Commercial Action - Sales | Jose Jose | poondikulam house Mrala p o Thodupuzha | Idukki | 685584 | Kerala | India FS South2 ED&I CSP PrinterPeople Cochin | Renjith PR PrinterPeople Cochin | PRINTER PEOPLE-COCHIN | 1- 4 channel relay 1- gate way installed | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-01 13:55 |  |  | 65 | INR | 65 | ENM HOME DISTRIBUTION
WO-11185952 | 103665592 | 2023-08-31 13:19 | 2023-08-31 |  | 2023-08-31 09:53 | EZ9R35463 | EZ9R35463 | EZ9R35463 |  | Ibrahim Nedungal house Oyoor post , onakkad , puthanathani Malappuram dt.pin: 676307 Kerala. Ibrahim 8,129,010,190 Easy9 RCCB 63/30 4pole (EZ9R35463) RCCB complaint yes Under Warranty 16 months Muhammed Ali - 8606739993 | 2023-08-31 | 2023-09-01 19:14 | No | Warranty | Ibrahim Ibrahim | Nedungal house Oyoor post , onakkad , puthanathani | Malappuram | 676307 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found Easy9 Residual Current Circuit Breaker - 4Pole continous tripping issue EZ9R35463 replaced problem solved | Repair |  | 9- Service Validated | 2023-09-02 19:19 |  |  | 45 | INR | 45 | ENM HOME DISTRIBUTION
WO-11185955 | 103674860 | 2023-09-01 11:33 | 2023-08-31 |  | 2023-08-31 10:07 | IN8486/32>SZ-OS | IN8486/32>SZ-OS | IN8486/32>SZ-OS |  | Dear team, Pls register complaint of zencelo grey. Rakesh Kumar Goel 276. Aggarsain colony Sirsa 125055 Haryana 9082790000 Thanks Sanjay kumar Get Outlook for Android | 2023-08-31 | 2023-09-02 15:27 | No | Warranty | Rakesh Kumar Goel | 276. Aggarsain colony | Sirsa | 125055 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Rakesh Kumar Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the switch found play problem. Hence faulty replaced. IN8486/32(BZ) - 1 Nos. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-02 15:31 |  |  | 255 | INR | 255 | ENM HOME DISTRIBUTION
WO-11186755 | 103669463 | 2023-09-07 19:05 | 2023-08-31 |  | 2023-08-31 10:42 | IH14000100 | IH14000100 | IH14000100 |  | Site 1 - Avinash T No /38, amreshwara nilaya S S lay out. B block 8th cross 4th main Davangere Mob No -9019001415 Site 2 - M N SATHYAPRAKASH NO 306/1 1st CROSS 5th MAIN J H PATEL LAYOUT A BLOCK DAVANAGERE Mob - 8317341010 | 2023-08-31 | 2023-09-07 19:16 | No | Commercial Action - Sales | SATHYAPRAKASH SATHYAPRAKASH | NO 306/1 1st CROSS 5th MAIN J H PATEL LAYOUT A BLOCK | Davangere | 577004 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Mohammad Riyaz_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | As per the customer's PO, we had visited the site and de-installed wiser automation gateway -1nos and 4channel relays- 23nos. After de-commissioning above mentioned gateway and 4 channel relays handed over to Sri lingeshwara electrical. - IH101ZWIFI-1nos - IH14000100-23nos - In the gateway only power cord is available, LAN cable not available with the customer. | Decommissioning | Uninstall | 9- Service Validated | 2023-09-07 19:22 |  |  | 260 | INR | 260 | ENM HOME DISTRIBUTION
WO-11187900 | 103685103 | 2023-09-01 10:20 | 2023-08-31 |  | 2023-08-31 13:39 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | DOP: 29/6/2023 IH100WFVDP Smart Doorbell Qty:1 P: Installation RINSHAD RASHEED PERIYAR HERMITAGE FLAT NO : A1C5 aluva ,company padi, spw Road, Near SPW school Pincode : 683106 Ph : 8289830063 | 2023-08-31 | 2023-09-02 10:23 | No | Commercial Action - Sales | RINSHAD RASHEED RINSHAD RASHEED | PERIYAR HERMITAGE FLAT NO : A1C5 aluva ,company padi, spw Road, Near SPW school | Ernakulam | 683106 | Kerala | India FS South2 ED&I CSP PrinterPeople Cochin | Renjith PrinterPeople Cochin | PRINTER PEOPLE-COCHIN | 1 vdf installed | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-04 10:23 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11188049 | 103688335 | 2023-08-31 16:23 | 2023-08-31 |  | 2023-08-31 14:36 | IN8401_16_SP | IN8401_16_SP | IN8401_16_SP |  | DOP: 27/7/2022 IN8486 WH Qty: 1 PCS P: Not working JAISAL PM PADINJAREMARYANGATTU MODKKALLUR ATHOLI (PO), ATHOLI KOZHIKODE - 673323 JAISAL PM 9846119001 | 2023-08-31 | 2023-09-02 21:20 | No | Warranty | JAISAL JAISAL | PADINJAREMARYANGATTU MODKKALLUR ATHOLI (PO), ATHOLI | KOZHIKODE | 673323 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found zencelo switch struck issue IN8486/32 replaced 1nos problem solved | Repair |  | 9- Service Validated | 2023-09-05 05:51 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11188276 | 103693776 | 2023-08-31 17:30 | 2023-08-31 |  | 2023-08-31 16:29 | E8332ACQUSB_WE | E8332ACQUSB_WE | E8332ACQUSB_WE |  | Mr.Omveer ( Phone No. - 9818911357) H-38 , Kusum Marg DLF Phase -1 Gurgaon. Nature of Complaint - E8332ACQUSB_WE - USB CHARGER (A+C) - 01 PCS NOT WORKING Invoice No- 7413 | 2023-08-31 | 2023-09-05 16:56 | No | Warranty | Omveer Omveer | H-38 , Kusum Marg DLF Phase -1 | Gurgaon | 122008 |  | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the USB socket and found USB socket have output issue, We replace the faulty USB socket with new. | Repair |  | 9- Service Validated | 2023-09-05 16:56 |  |  | 54 | INR | 54 | ENM HOME DISTRIBUTION
WO-11194635 | 103723524 | 2023-09-01 17:03 | 2023-09-01 |  | 2023-09-01 14:23 | IN8401_N | IN8401_N | IN8401_N |  | CUSTOMER REQUESTCustomer Request is visible on the customer portal, ensure clarity 24,1st floor, Bunglow Road, Kamla Nagar, Delhi Delhi 110007 Delhi India | 2023-09-01 | 2023-09-04 16:16 | No | Warranty | Mr. Siddhant | 24,1st floor, Bunglow Road, Kamla Nagar, Delhi | Delhi | 110007 | Delhi | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the switch and found switch have stuck issue, We replace the faulty switch with new. | Repair |  | 9- Service Validated | 2023-09-04 16:20 |  |  | 22 | INR | 22 | ENM HOME DISTRIBUTION
WO-11195239 | 103727210 | 2023-09-01 19:38 | 2023-09-01 |  | 2023-09-01 17:17 | P1001_6_DG_N | P1001_6_DG_N | P1001_6_DG_N |  | DOP: 19/7/2023 Livia Switches P: Not Working Chandra shekhar Ph No : 7702133055 Nandini Nagar Hafeezpet Hyderabad -500049 | 2023-09-01 | 2023-09-09 12:58 | No | Warranty | Chandra shekhar Chandra shekhar | Nandini Nagar Hafeezpet | Hyderabad | 500049 | Telangana | India FS ED&I CSP South Team Master Electrical Solutions Hyderabad | DEBANGSHU BOSE Master Electrical Solutions SECUNDERABAD | Master Electrical Solutions | VISITED THE SITE AND CARRIED OUTB THE FOLLOWING JOB.NEW MATERIAL IS REPLACED | Repair |  | 9- Service Validated | 2023-09-09 13:01 |  |  | 20 | INR | 20 | ENM HOME DISTRIBUTION
WO-11200493 | 103731078 | 2023-09-02 14:42 | 2023-09-02 |  | 2023-09-02 11:15 | X3200WH_N | X3200WH_N | X3200WH_N |  | DOP: 17/8/2023 X3200WH Qty- 1 PCS P: Not Working | 2023-09-02 | 2023-09-06 15:18 | No | Warranty | Lan Marketing - 500014411 | AP-7/505C, Areacode, | Malappuram | 673639 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found opela fan regulator knob broken X3200 replaced 1nos problem solved | Repair |  | 9- Service Validated | 2023-09-06 15:21 |  |  | 40 | INR | 40 | ENM HOME DISTRIBUTION
WO-11200497 | 103740679 | 2023-09-02 14:19 | 2023-09-02 |  | 2023-09-02 11:26 | EZ9ETND06 | EZ9ETND06 | EZ9ETND06 |  | DOP: 4/4/2023 EZ9ETND06 Qty- 1 PCS DB DOOR REST LINEESHKUMAR NP KUNNATH HOUSE CHORODE (PO) VADAKARA (VIA) KOZHIKODE - 673106 LINEESHKUMAR NP 9539147196 | 2023-09-02 | 2023-09-08 15:36 | No | Warranty | LINEESHKUMAR LINEESHKUMAR | KUNNATH HOUSE CHORODE (PO) VADAKARA (VIA) | KOZHIKODE | 673106 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | PRAMEESH P.S APSMarketingCompany Calicut | APS Marketing Company | visited this site found Easy9 - TPN DB - double door rust issue EZ9ETND06 replaced problem solved | Repair |  | 9- Service Validated | 2023-09-08 21:27 |  |  | 55 | INR | 55 | ENM HOME DISTRIBUTION
WO-11200507 | 103740734 | 2023-09-02 14:12 | 2023-09-02 |  | 2023-09-02 11:32 | UNS61SW1M_WE | UNS61SW1M_WE | UNS61SW1M_WE |  | DOP: 25/11/2022 UNS61SW1M_WE - 2 PCS UNS62SW1M_WE - 3 PCS UNS61SWL1M_WE - 1 PCS UNS161SWL1M_WE - 1 PCS P: NOT WORKING SAJEESH KUMAR KULAMULLATHIL IRINGANNUR IRINGANNUR KOZHIKODE - 673505 SAJEESH KUMAR 9539666760 OR 9961439642 | 2023-09-02 | 2023-09-05 15:38 | No | Warranty | SAJEESH KUMAR SAJEESH KUMAR | KULAMULLATHIL IRINGANNUR IRINGANNUR | Kozhikode | 673505 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | PRAMEESH P.S APSMarketingCompany Calicut | APS Marketing Company | visited this site found unica switchs contact issue and fan regulater speed control issue unica 1way 2nos unica 5st fan 1nos replaced problem solved | Repair |  | 9- Service Validated | 2023-09-06 15:40 |  |  | 70 | INR | 70 | ENM HOME DISTRIBUTION
WO-11200560 | 103741119 | 2023-09-04 10:15 | 2023-09-02 |  | 2023-09-02 12:15 | X1001WH_M3M_N | X1001WH_M3M_N | X1001WH_M3M_N |  | DOP: 15/9/2022 X1002WH-4 X1001WH-6 P: Not Working Abdul Salam Olickapara house koottickal po.Pin: 686514, Kottayam, Kerala Ph: 9446304879 | 2023-09-02 | 2023-09-04 16:40 | No | Warranty | Abdul Abdul | Abdul Salam Olickapara house koottickal | Kottayam | 686514 | Kerala | India FS South2 ED&I CSP PrinterPeople Cochin | Vysakht PrinterPeople Cochin | PRINTER PEOPLE-COCHIN | x1001&x1002= 10 nos each replaced at site | Repair |  | 8- Service Completed | 2023-09-06 16:42 |  |  | 110 | INR | 110 | ENM HOME DISTRIBUTION
WO-11200565 | 103741201 | 2023-09-04 10:17 | 2023-09-02 |  | 2023-09-02 12:20 | EZ9R35263 | EZ9R35263 | EZ9R35263 |  | DOP: 20/11/2022 EZ9R35263 Qty:1 P: Not Working Liju P T Parackal H Manary P O Paipra Muvattupuzha Ernakulam Ph 9744444867 | 2023-09-02 | 2023-09-07 16:51 | No | Warranty | Liju Liju | Parackal H Manary P O Paipra Muvattupuzha | Ernakulam | 686661 | Kerala | India FS South2 ED&I CSP PrinterPeople Cochin | Vysakht PrinterPeople Cochin | PRINTER PEOPLE-COCHIN | rccb not triping.. send to location. will be installed onsite on getting down time | Repair |  | 9- Service Validated | 2023-09-07 16:53 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11200668 | 103741540 | 2023-09-02 21:16 | 2023-09-02 |  | 2023-09-02 14:35 | UNS5STFAN2M_WE | UNS5STFAN2M_WE | UNS5STFAN2M_WE |  | DOP: 5/6/2023 UNS5STFAN2M_WE Unica Pure 6AX 1WAY SWITCH GRAY P: Customer is facing issues with Unica Pure 6ax 1WAY SWITCH Shamseer Dar al ain ,Street no-16,Nelliparamba Taliparamba ,pincode - 679341 Kannur Shamseer 6282547121 | 2023-09-02 | 2023-09-05 11:41 | No | Warranty | Shamseer Shamseer | Nelliparamb Taliparamba Street number 16 | Kannur | 670141 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Rejilesh APSMarketingCompany Calicut | APS Marketing Company | visited this site found unica switchs struck issue UNS61SW1M replaced 4nos problem solved | Repair |  | 9- Service Validated | 2023-09-05 11:44 |  |  | 110 | INR | 110 | ENM HOME DISTRIBUTION
WO-11200669 | 103741629 | 2023-09-03 19:09 | 2023-09-02 |  | 2023-09-02 14:40 | A9N1P02C | A9N1P02C | A9N1P02C |  | Inv. No : 9008671379 DOP: 7/8/2023 A9N1P02C Qty:1 P: no Dinrail Mount M/s. L.G.BALAKRISHNAN & BROS LTD., SF NO : 402, G.V GARDENS, INDIRA GARDEN ROAD, UPPILIPALAYAM (POST), COIMBATORE - 641015. Kirubakaran K 8072589599 smd.designcontrols <smd.designcontrols@lgb.co.in> | 2023-09-02 | 2023-09-04 18:32 | No | Warranty | M/s. L.G.BALAKRISHNAN & BROS LTD., | SF NO : 402, G.V GARDENS, INDIRA GARDEN ROAD, UPPILIPALAYAM (POST) null | Coimbatore | 641015 | Tamil Nadu | India FS ED&I CSP South Team Power Pro Engineering Services Coimbatore | KV ARUNKUMAR_POWER PRO ENGINEERIG SERVICES COIMBATORE | Powerpro Engineering Services | WE HAVE VISITED THE SITE AND INSPECTED WE FOUND MCB ON & OFF KNOB FOUND DOLYY FREE WE HAVE RECTIFIED THE SAME TESTED AND FOUND OK TESTED ELECTRICALLY FOUND WORKIG OK | Repair |  | 9- Service Validated | 2023-09-04 18:33 |  |  | 31 | INR | 31 | ENM HOME DISTRIBUTION
WO-11200810 | 103743104 | 2023-09-04 11:01 | 2023-09-02 |  | 2023-09-02 18:13 | MTN627819 | MTN627819 | MTN627819 |  | DOP: 31/3/2023 MTN627819 Qty:3 P: Hang issue FUTURE AUTOMATION SOLUTIONS First Floor, Nirman house, Opposite Dharmadev Developers, Beside Navrang pauva and food zone, Shyamal Cross Road, Shyamal-Prahladnagar Road, Satellite, Ahmedabad-380015 Saurav Dhanopiya - +919712927430 Contact Person at Site - Email Address** logistics.fas2022@gmail.com | 2023-09-02 | 2023-09-05 11:18 | No | Warranty | Dhanopiya Dhanopiya | First Floor, Nirman house, Opposite Dharmadev Developers, Beside Navrang pauva and food zone, Shyamal Cross Road, Shyamal-Prahladnagar Road, Satellite | Ahmedabad | 380015 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Mistri Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physically observed ok. MTN627819 SR NO : 2023 W07 / -13 Nos observed physically observed ok. according to customer knx connect with push button then its working ok. but after some time push time button led indiction not working and push button also not working. and customer remove the knx supply and reconnect with push button also not working. so customer satisfaction free replacement for customer satisfaction. | Repair |  | 9- Service Validated | 2023-09-05 11:19 | =S= Consig Fill up 226018759 |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11208853 | 103743227 | 2023-09-04 21:36 | 2023-09-04 |  | 2023-09-04 10:09 | EZ9R35240 | EZ9R35240 | EZ9R35240 |  | DOP: 10/4/2023 EZ9R35240 Qty - 1 PCS P: NOT WORKING ABDULLA VANNATHARA HOUSE KADIYANGAD FISH MARKET ROAD KADIYANGAD PO. KOZHIKODE - 673525 ABDULLA 9048928731 | 2023-09-04 | 2023-09-05 13:59 | No | Warranty | ABDULLA ABDULLA | VANNATHARA HOUSE KADIYANGAD FISH MARKET ROAD KADIYANGAD PO. | Kozhikode | 673525 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Rejilesh APSMarketingCompany Calicut | APS Marketing Company | visited this site found Easy9 Residual Current Circuit Breaker - 2Pole test button not working EZ9R35240 replaced problem solved | Repair |  | 9- Service Validated | 2023-09-06 14:02 |  |  | 45 | INR | 45 | ENM HOME DISTRIBUTION
WO-11209108 | 103755426 | 2023-09-04 12:33 | 2023-09-04 | Part order request validated by Mr. Chandrakant Panchal Sir, Also we booked material from kiron electrical Regarding WO-10746248, Case No. 100862378, M/s Kiron Electricals | 2023-09-04 10:33 | X1001WH_M3M_N | X1001WH_M3M_N | X1001WH_M3M_N |  | DOP: 18/11/2022 Opale Switches Qty:1 P: Not Working Kindly check invloice at site Shyam kunj, Agrawal Complex, Near Dutt Mandir, Kampoo Road, lashkar, Gwalior (MP) - 474001 Amit 9893846868 | 2023-09-04 | 2023-09-05 18:28 | No | Warranty | Amit Agarwal | Agarwal Complex, Near Dutt Mandir, Kampoo Road, Lashkar, | Gwalior | 474001 | Madhya Pradesh | India FS ED&I CSP West Team ABR Technical Service Indore | Lalu Sen_ABR Tecneical Services Indore | ABR Technical Services (9574) | Reached at site and checked switches and found details below 1) X1002WH - 18.- Nov. 2022- Broken Only for customer satisfaction we recommended to replace 1 Nos. Switch switch replace from our stock and we are clos this case. | Repair |  | 9- Service Validated | 2023-09-06 10:32 | =S= Consig Fill up 226019047 |  | 550 | INR | 550 | ENM HOME DISTRIBUTION
WO-11209412 | 103743278 | 2023-09-04 13:55 | 2023-09-04 |  | 2023-09-04 10:37 | IH14000100 | IH14000100 | IH14000100 |  | DOP: 19/7/2023 IH14000100 4 Channel Relay IH101ZWIFI Gateway P: Not Working M/s KARTHIK CONSTRUCTION KANNAKURICHI MAIN ROAD CHINNATHIRUPATHI salem. Person :Karthik &9842710447 | 2023-09-04 | 2023-09-08 14:07 | No | Warranty | M/s KARTHIK CONSTRUCTION | KANNAKURICHI MAIN ROAD CHINNATHIRUPATHI | Salem | 636008 | Tamil Nadu | India FS South2 ED&I CSP UpservePowerSystems Chennai | HARI PRASATH UpservePowerSystems Chennai | Upserve Power Systems | IH14000100 2NOS REPLACED | Repair |  | 8- Service Completed | 2023-09-08 14:16 |  |  | 305 | INR | 305 | ENM HOME DISTRIBUTION
WO-11209794 | 103744245 | 2023-09-04 10:57 | 2023-09-04 |  | 2023-09-04 10:44 | TM2AMI4LT | TM2AMI4LT | TM2AMI4LT | 21203409162 | Model No - TM2AMI4LT Serial No - 21203409162 Customer - Viyash Life Sciences Pvt. Ltd. Site Address - plot no. 1A/2, MIDC Industrial Estate, Taloja, Maharashtra 410208 Contact Person - Amit Patil (7276563252 | 2023-09-04 | 2023-09-04 15:31 | No | Warranty | Viyash Life sciences Pvt. Ltd | Plo No - 1A/2, MIDC Industrial Estate,Taloja, | Raigad | 410208 | Maharashtra | India FS ED&I CSP West Team R P Electrical Mumbai | Sanket Jadhav R P Electrical Mumbai | R P Electrical | Visited at site for TM2AM142T I/O device module not communicate. Internal defect on module so that it not works properly. We replace a new module. | Repair |  | 9- Service Validated | 2023-09-04 15:39 |  |  | 56 | INR | 56 | ENM HOME DISTRIBUTION
WO-11210400 | 103747447 | 2023-09-04 16:39 | 2023-09-04 |  | 2023-09-04 10:53 | CPX32DP2M_WE | CPX32DP2M_WE | CPX32DP2M_WE |  | Hi Team, Please send your technical engineer at the site as the client is facing issues in the ClipsalX range. CPX32DP2M_WE - 5 pieces Customer Details Sanjeev Bhatnagar Address - MIG-135, Ramganga Vihar, Moradabad - 244001, (U.P.) Contact number - 9897048770 Regards Tushar Agarwal | 2023-09-04 | 2023-09-27 13:26 | No | Warranty | Sanjeev Bhatnagar | MIG-135, Ramganga Vihar, | Moradabad | 244001 | Uttar Pradesh | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the DP switches found DP switches have stuck issue and breaking issue. As per serial number product not covered under warranty. Customer providing the invoice details 10-04-2022. We replace the faulty DP switches with new. | Repair |  | 8- Service Completed | 2023-09-27 14:32 |  |  | 175 | INR | 175 | ENM HOME DISTRIBUTION
WO-11210519 | 103755088 | 2023-09-04 18:03 | 2023-09-04 |  | 2023-09-04 11:00 | UNS5STFAN2M_WE | UNS5STFAN2M_WE | UNS5STFAN2M_WE |  | DOP: 7/6/2023 Unica Pure VG 32A DP SWITCH UNS5STFAN2M_WE P: Not Working Thafsal np House name zynab,Pudussery mukku ,Near mambaram pincode -670649 Kannur Thafsal np 9686110153 | 2023-09-04 | 2023-09-06 16:52 | No | Warranty | Thafsal np Thafsal np | House name zynab,Pudussery mukku ,Near mambaram | Kannur | 670649 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Rejilesh APSMarketingCompany Calicut | APS Marketing Company | visited this site found unica one way & two way switchs struck issue, 32dp switch dolly broken unica 1way 4nos unica2way 4nos unica 32dp switch 2nos replaced problem solved | Repair |  | 9- Service Validated | 2023-09-06 16:56 |  |  | 80 | INR | 80 | ENM HOME DISTRIBUTION
WO-11210676 | 103757540 | 2023-09-04 12:42 | 2023-09-04 |  | 2023-09-04 12:02 | P1001_6_DG_N | P1001_6_DG_N | P1001_6_DG_N |  | DOP: 28/8/2023 Livia Regulator Qty: 1 P: Not Working Kindly check oinvoice at site Rockdael Hotels and Resort 11-5-1,Beside ICICI Bank, Waltair Main Road, Seven Hills Hospital Road Visakhapatnam | 2023-09-04 | 2023-09-05 09:59 | No | Warranty | Rockdael Hotels and Resort | 11-5-1,Beside ICICI Bank, Waltair Main Road, Seven Hills Hospital null | Visakhapatnam | 530002 | Andhra Pradesh | India FS ED&I CSP South Team Voltamp Electrical Works Visakhapatnam | Doni RajeshReddy_VOLT AMP ELECTRICAL WORKS Visakhapatnam | Voltamp Electrical Works | As per the complaint visited the site and found above the Livia Fun regulator is not working so today we have observed the problem of fun regulator on off mechanism issue so Schneider stock replaced so issue closed | Repair |  | 9- Service Validated | 2023-09-05 09:59 |  |  | 10 | INR | 10 | ENM HOME DISTRIBUTION
WO-11210701 | 103757909 | 2023-09-04 13:11 | 2023-09-05 |  | 2023-09-04 12:13 | A9N4P32C | A9N4P32C | A9N4P32C |  | A9N4P32C D2147 Qty:2 P: Pole issue Kindly check invoice at site | 2023-09-04 | 2023-09-05 12:35 | No | Warranty | Ambika electrical and mechanical works | Shop No. 2 , L- Type Road, JIDC Estate | Ahmedabad | 382418 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | Parthiv Patel JKS Ahmedabad | JKS Engineering Co. | Check mcb a9n4p32 1nos mcb dolly free and check mcb a9n4p32 body and terminal side not any damage.check mcb 3th pole open found total 2nos replacement | Repair |  | 9- Service Validated | 2023-09-05 16:08 | =S= Consig Fill up 226026388 |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11210885 | 103759366 | 2023-09-04 13:15 | 2023-09-04 |  | 2023-09-04 12:54 | EZ9F76125 | EZ9F76125 | EZ9F76125 | D2239 | Product : EZ9F76125 MCB Sr No. D2239 , DOM Aug 2022 Within Warranty Yes Not getting ON / Knob Free Mr Inder H. no. 1321,Gali no. 8 Hall Bazar Amritsar 143006 Mr Inder 9592901500 | 2023-09-04 | 2023-09-04 13:18 | No | Warranty | Inder Inder | H. no. 1321,Gali no. 8 Hall Baza | Amritsar | 143006 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the MCB found not getting on due to phase missing & not giving output and fan regulator found speed variation issue. EZ9F76125 - 3 Nos. P3100 - 4 Nos. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-04 16:17 |  |  | 150 | INR | 150 | ENM HOME DISTRIBUTION
WO-11211569 | 103765431 | 2023-09-05 10:11 | 2023-09-04 |  | 2023-09-04 16:38 | P1001_6_DG_N | P1001_6_DG_N | P1001_6_DG_N |  | DOP: 29/12/2022 P 1001 10AX 1 WAY ? 2NOS P 1002 10AX 1 WAY ? 1NOS P: Not Working SFS Sunnyvale flat no 1G infopark road Kakkanad mob. 9447779775 | 2023-09-04 | 2023-09-05 10:52 | No | Warranty | Anoop Anoop | SFS Sunnyvale flat no 1G infopark road Kakkanad | Ernakulam | 682042 | Kerala | India FS South2 ED&I CSP PrinterPeople Cochin | Vysakht PrinterPeople Cochin | PRINTER PEOPLE-COCHIN | replaced rccb at site.. rccb arranged by se sales team.. p1001-4 nos and p1002-1 nos faulty.. replacement booking approved by pramod sir.. | Repair |  | 9- Service Validated | 2023-09-06 10:55 | Hi Team, Material booked zfre Zvo : 226029787 |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11211689 | 103767305 | 2023-09-05 10:14 | 2023-09-04 |  | 2023-09-04 17:28 | UNS5STFAN2M_WE | UNS5STFAN2M_WE | UNS5STFAN2M_WE |  | DOP: 17/7/2023 Unica Pure --UNS5STFAN2M_WE--5 Steps 360 Deg Fan Regulator, 2M--1No. P: Not Working Mr. Jose N Abraham Naduvath House, Kottappady P.O., Kottappady, Kothamangalam - 686692. Jose N Abraham 9447170142 | 2023-09-04 | 2023-09-07 16:58 | No | Warranty | Jose N Abraham | Naduvath House, Kottappady P.O., | Ernakulam | 686692 | Kerala | India FS South2 ED&I CSP PrinterPeople Cochin | Renjith PrinterPeople Cochin | PRINTER PEOPLE-COCHIN | reuglator sped adjustment issue.. replacement send to site location. onsite replacement on customer downtime confirmation | Repair |  | 8- Service Completed | 2023-09-07 17:00 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11211706 | 103767543 | 2023-09-04 18:00 | 2023-09-04 |  | 2023-09-04 17:33 | EZ9ESND12 | EZ9ESND12 | EZ9ESND12 |  | DOP: 15/7/2022 EZ9ESND12 Qty : 1 PCS P: Db Door Knob complaint IBRAHIM K KUNIYIL HOUSE VALAYAM (PO) VALAYAM KOZHIKODE - 673517 IBRAHIM K 9539168269, 7909180181 | 2023-09-04 | 2023-09-05 15:36 | No | Warranty | IBRAHIM IBRAHIM | KUNIYIL HOUSE VALAYAM (PO) VALAYAM | KOZHIKODE | 673517 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Rejilesh APSMarketingCompany Calicut | APS Marketing Company | visited this site found Easy9 - SPN DB - double door lock complaint db door lock replaced problem solved | Repair |  | 9- Service Validated | 2023-09-05 15:38 |  |  | 70 | INR | 70 | ENM HOME DISTRIBUTION
WO-11213658 | 103767826 | 2023-09-05 13:41 | 2023-09-05 |  | 2023-09-05 10:13 | EZ9R35463 | EZ9R35463 | EZ9R35463 |  | JUMA MASJID OTHAYOTH THACHAMPOYIO PO THAMARASSERY THAMARASSERY KOZHIKODE - 673573 JUMA MASJID OTHAYOTH 8943662199 EZ9R35463 - 1 PCS Not working Yes Under Warranty Before Three Months | 2023-09-05 | 2023-09-06 20:21 | No | Warranty | JUMA MASJID OTHAYOTH | THACHAMPOYIO PO THAMARASSERY THAMARASSERY | KOZHIKODE | 673573 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | PRAMEESH P.S APSMarketingCompany Calicut | APS Marketing Company | visited this site found Easy9 Residual Current Circuit Breaker - 4Pole tripping issue checked the breaker no abnormality found its working fine | Repair |  | 9- Service Validated | 2023-09-06 20:25 |  |  | 40 | INR | 40 | ENM HOME DISTRIBUTION
WO-11213607 | 103767674 | 2023-09-05 13:46 | 2023-09-05 |  | 2023-09-05 09:41 | UNS61SW1M_WE | UNS61SW1M_WE | UNS61SW1M_WE | UNS32DP2M_WE | HAMEED VP VAZHAYIL PEEDIKAYIL NITTOOR KUTTIYADI KOZHIKODE - 673507 HAMEED VP 9946664242 UNS61SW1M_WE - 8 PCS UNS161SWL1M_WE - 5 PCS UNS32DP2M_WE - 2 PCS Not working Yes Under Warranty Before Three Months LAN Marketing 8075581561 | 2023-09-05 | 2023-09-13 18:03 | No | Warranty | HAMEED VP | VAZHAYIL PEEDIKAYIL NITTOOR KUTTIYADI | KOZHIKODE | 673507 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found unica one way & two way and 16ax indicator, 6ax indicator some time working, checked that switchs dust and ant issue switchs clean done some switchs replaced UNS16SWL1M 2NOS UNS62SW1M 2NOS UNS61SW1M 1NOS UNS21USB1P1M _WE 1NOS UNS61SW1M 3NOS UNS62SW1M 3NOS UNS61SWL1M_WE 4NOS UNS20DP2M 1NOS REPLACED PROBLEM SOLVED | Repair |  | 9- Service Validated | 2023-09-14 18:08 |  |  | 60 | INR | 60 | ENM HOME DISTRIBUTION
WO-11213672 | 103769664 | 2023-09-05 13:52 | 2023-09-05 |  | 2023-09-05 10:27 | UNS162SW2M_GY | UNS162SW2M_GY | UNS162SW2M_GY |  | DR KISHOREKUMAR M P MOOTHEDATH 'SWASTHIKA' CHENNALODE (PO) NEAR HS JUNCTION, KAVUMANNAM WAYANAD - 673122 DR KISHOREKUMAR M P 9447963008, 9495316138 UNS162SW2M_GY : 1 PCS Not working Yes Under Warranty Before Three Months | 2023-09-05 | 2023-09-08 15:40 | No | Warranty | KISHOREKUMAR M P | MOOTHEDATH 'SWASTHIKA' CHENNALODE (PO) NEAR HS JUNCTION, KAVUMANNAM | WAYANAD | 673122 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Rejilesh APSMarketingCompany Calicut | APS Marketing Company | visited this site found unica 16A switch struck issue UNS162SW2M_GY replaced 1nos | Repair |  | 9- Service Validated | 2023-09-09 15:44 |  |  | 80 | INR | 80 | ENM HOME DISTRIBUTION
WO-11213649 | 103781533 | 2023-09-05 12:12 | 2023-09-05 | Validated By Prashant | 2023-09-05 10:07 | P3100_DG | P3100_DG | P3100_DG |  | Livia 2 module step fan regulator , 2 no isworking Purchased from amazon datd on 23 -05-2023 | 2023-09-05 | 2023-09-06 12:30 | No | Warranty | Praveen GB | S 2 , Titan block , 204 , Godrej prime , Shell colony chembur | Mumbai | 400071 | Maharashtra | India FS ED&I CSP West Team S K SERVICES Mumbai | Ganesh Tati_S K SERVICES Mumbai | S.K. Services (10237) | We Visited the site Product Ref No:-P3200-2Nos. Serial No:-19103, 231705. We check the material fan regulator is 1 step to 4 Step operating problem and another is 1 step to 2 step operating problem We replace the product book ZVO. | Repair |  | 9- Service Validated | 2023-09-08 20:47 | 226031643 |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-11213669 | 103768034 | 2023-09-05 12:40 | 2023-09-05 | NA | 2023-09-05 10:26 | IN8401_16_SP | IN8401_16_SP | IN8401_16_SP |  | DOP: 5/6/2023 IN8401_16_SP P: Not Working Mr. Kunal Vasa Address - Lansdowne Heights 6, Sarat Bose Road. Flat-4D, 4th Floor. Also, CONTACT Ekta - 9038917287 | 2023-09-05 | 2023-09-08 14:00 | No | Warranty | Kunal Kunal | Lansdowne Heights 6, Sarat Bose Road. Flat-4D, 4th Floor. | Kolkata | 700020 | West Bengal | India FS ED&I CSP East Team B.D Electroservices Kolkata | KOUSHIK MONDAL_B.D Electroservices Kolkata | B.D Electroservices(500017330) | On received of ZVO material will delivered to customer. | Repair |  | 9- Service Validated | 2023-09-11 10:48 |  |  | 16 | INR | 16 | ENM HOME DISTRIBUTION
WO-11213783 | 103768368 | 2023-09-05 11:08 | 2023-09-05 | NA | 2023-09-05 10:35 | A9KESND12 | A9KESND12 | A9KESND12 |  | DOP: 14/7/2022 A9KESND12 P: Lock issue Nashra Gaonkar, Contact No.: 9004019401, NOOR ELECTRICAL CONTRACTOR, Shop No.08 Haji Mohd Noora Lane, Near Bandra Jain Mandir, Behind Hill Road Bandra West Mumbai-400050 | 2023-09-05 | 2023-09-07 14:21 | No | Warranty | NOOR ELECTRICAL | Shop No.08 Haji Mohd Noora Lane, Near Bandra Jain Mandir, Behind Hill Road Bandra West null | Mumbai | 400050 | Maharashtra | India FS ED&I CSP West Team East India Power Engineers Mumbai | Ratnesh Shigvan East India Power engineers Mumbai | East India Power Engineers (5043) | Visited the site & checked the DB door found not fitting properly due to DB frame putty available. Removed the putty from& checked door closed & found lock working ok. Also found customer not fitted lock properly on a door due lock was not fitting. Give the demo to the customer for having to fix the lock door. | Repair |  | 8- Service Completed | 2023-09-07 16:27 |  |  | 12 | INR | 12 | ENM HOME DISTRIBUTION
WO-11214780 | 103770759 | 2023-09-05 12:03 | 2023-09-05 | IN8401/6A- 04 Nos need to be replaced. | 2023-09-05 10:51 | IN8401_N | IN8401_N | IN8401_N |  | heck-list for Complaint Registration 1 Name of Customer:- Castel Royale Tower No 7 Flat No G2-2202 2 Castel Royale Tower No 7 Sr No 186 to 190, Bopodi Pune 411020 3 Name of contact person at site:- Nilesh Gajmal 4 Contact Phone / Mob. No: 9881229776 5 Defective product details:-(1) IN8401- 03 6 Nature of Defect:-Not Operating proper 7 Shut-down availability if applicable:-Yes 8 Warranty status:-Yes 9 Commissioned / Installed date:-07/8/23 | 2023-09-05 | 2023-09-05 17:45 | No | Warranty | Nilesh Gajmal | Castel Royale Tower No 7 Flat No G1-902 Tower No 7 Sr No 186 to 190, Bopodi | Pune | 411020 | Maharashtra | India FS ED&I CSP West Team Alliance Controls Pvt Ltd Pune | Shmabhu Bone_Alliance Controls Pvt. Ltd | Alliance Controls Pvt. Ltd. (7966) | (1) Visited on site and checked IN8401- 04Nos of switches found switches having ON/OFF operating issue. This 04Nos of switches is need to be replace. (2) So, we have replaced faulty switches with the new switches from customers stock and taken trial found OK. (3) Also 1 gang switch (zigbee) switch having coverplate pushbutton, removed push button from coverplate and fixed again properly and then taken trial found 1 gang switch working OK. IN8401/6A- 04 Nos need to be replaced. | Repair |  | 9- Service Validated | 2023-09-06 11:46 | =S= Consig Fill up 226031337 |  | 10 | INR | 10 | ENM HOME DISTRIBUTION
WO-11215193 | 103769121 | 2023-09-05 12:19 | 2023-09-05 | Validated By Prashant | 2023-09-05 10:56 | L5508D1A | L5508D1A | L5508D1A |  | DOP: 3/6/2022 L5508D1A Qty:1 P: Not working Praful - 9920700075 Samarth Enterprise Gala no 112, Municipal Industrial Estate, Opp. Lady Ratan Tower, Gandhi Nagar, Worli, Mumbai. | 2023-09-05 | 2023-09-06 12:52 | No | Warranty | Samarth enterprise | 112, Municipal Industrial Estate , Gandhi Nagar , Opp. Lady Ratan Tower , Worli , Mumbai | Mumbai | 400018 | Maharashtra | India FS ED&I CSP West Team S K SERVICES Mumbai | Ganesh Tati_S K SERVICES Mumbai | S.K. Services (10237) | We Visited the site Product Ref No:-L55081AP Serial No:-001008481900 Dimmer is totally off and out f warranty. | Repair |  | 9- Service Validated | 2023-09-11 12:55 |  |  | 20 | INR | 20 | ENM HOME DISTRIBUTION
WO-11215389 | 103773757 | 2023-09-05 14:07 | 2023-09-05 |  | 2023-09-05 11:27 | EZ9EPS63SN | EZ9EPS63SN | EZ9EPS63SN |  | Abdullah km Koorimannil mele mannil house Vallikkapatta post , checkpost , anakkayam , manjeri Malappuram dt , pin : 679324 Kerala. Abdullah km 8,589,805,805 Easy9 63 a selector switch ( EZ9EPS63SN) Rotary switch complaint yes Under Warranty 4 months | 2023-09-05 | 2023-09-07 14:12 | No | Warranty | Abdullah km | Koorimannil mele mannil house Vallikkapatta post , checkpost , anakkayam , manjeri | Malappuram | 679324 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found easy 9 selecter switch blue indicator not working, indicator replaced problem solved | Repair |  | 9- Service Validated | 2023-09-07 14:15 |  |  | 60 | INR | 60 | ENM HOME DISTRIBUTION
WO-11215411 | 103775873 | 2023-09-05 17:39 | 2023-09-05 |  | 2023-09-05 11:34 | SAE_UE_MS_CSAWE | SAE_UE_MS_CSAWE | SAE_UE_MS_CSAWE |  | DOP: 30/11/2022 CSCC54E_WE Qty:1 P: No light appearing Shakir Hussain Address: Near Bank of India Delhi Road Pakwara Moradabad - 244001 Mobile No: 9719195454 | 2023-09-05 | 2023-09-11 14:22 | No | Warranty | Shakir Hussain Shakir Hussain | Near Bank of India Delhi Road Pakwara | Moradabad | 244001 | Uttar Pradesh | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the sensor and found sensor have output problem, We replace the faulty sensor with new. Mail Id. tusharagarwal2509@gmail.com | Repair |  | 9- Service Validated | 2023-09-11 17:45 |  |  | 159 | INR | 159 | ENM HOME DISTRIBUTION
WO-11215606 | 103785054 | 2023-09-05 15:01 | 2023-09-05 |  | 2023-09-05 13:02 | X1001WH_N | X1001WH_N | X1001WH_N |  | DOP: 2/5/2023 X1001WH X1286WH P: Not Working CYBERCITY Marina Skies Green Hills Rd opposite IDL near Moosapet Hyderabad Telangana 500018 SAHU 9100093460 | 2023-09-05 | 2023-09-12 17:47 | No | Warranty | Sahu Sahu | CYBERCITY Marina Skies Green Hills Rd opposite IDL near Moosapet, | Hyderabad | 500018 | Telangana | India FS ED&I CSP South Team Master Electrical Solutions Hyderabad | SURYAKANTH YAMAGAR Master Electrical Solutions SECUNDERABAD | Master Electrical Solutions | VISITED THE SITE AND CARRIED OUT THE FOLLOWING JOB.MATERIAL REPLACED TO THE CUSTOMER .OLD FAULTY MATERIAL TAKEN BACK FROM THE CUSTOMER | Repair |  | 9- Service Validated | 2023-09-12 17:50 |  |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-11216201 | 103793704 | 2023-09-06 10:36 | 2023-09-05 | NA | 2023-09-05 16:38 | IN8486_20_BZ | IN8486_20_BZ | IN8486_20_BZ |  | n8486/20 Purchases form himmat electrical this month olnly | 2023-09-05 | 2023-09-08 14:00 | No | Warranty | Lokesh kankariya | HP electrical , 32 ezra street 3rd floor , | Kolkata | 700001 | West Bengal | India FS ED&I CSP East Team B.D Electroservices Kolkata | KOUSHIK MONDAL_B.D Electroservices Kolkata | B.D Electroservices(500017330) | On received of ZVO material will delivered to customer. | Repair |  | 9- Service Validated | 2023-09-11 11:29 |  |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-11216225 | 103794006 | 2023-09-05 18:16 | 2023-09-05 | NA | 2023-09-05 16:44 | UNS61SW1M_WE | UNS61SW1M_WE | UNS61SW1M_WE |  | Mrittick Choudhury mrittickchoudhury@gmail.com ?8617283176 Flat No 1E Dakshin Kali 12th Barrister P Mitra Road Kolkata 700035 West Bengal Indianot working | 2023-09-05 | 2023-09-11 13:30 | No | Warranty | Mrittick Choudhury | Flat No 1E Dakshin Kali 12th Barrister P Mitra Road | Kolkata | 700035 | West Bengal | India FS ED&I CSP East Team B.D Electroservices Kolkata | KOUSHIK MONDAL_B.D Electroservices Kolkata | B.D Electroservices(500017330) | On received of ZVO material will delivered to custmer. | Repair |  | 9- Service Validated | 2023-09-11 10:51 |  |  | 36 | INR | 36 | ENM HOME DISTRIBUTION
WO-11219303 | 103794399 | 2023-09-08 14:07 | 2023-09-06 |  | 2023-09-06 10:09 | IH14000100 | IH14000100 | IH14000100 |  | DOP: 5/9/2023 IH14000100 4 Channel Automation Relay IH101ZWIFI Automation Gateway Qty:2 P: Installation Madhur Mittal 9873095398 4 Maple Avenue DLF Chhatarpur Farms Delhi 110068 | 2023-09-06 | 2023-09-06 23:39 | No | Commercial Action - Sales | Madhur Mittal Madhur Mittal | 4 Maple Avenue DLF Chhatarpur Farms | Delhi | 110068 | Delhi | India FS ED&I CSP North Team Seamtek International Pvt. Ltd. GHAZIABAD | Satish Raika Seamtek International Pvt. Ltd. GHAZIABAD | Seamtek International Pvt. Ltd. | following wiser components has been installed gateway: 1 no 4 channel relay : 1 no | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-11 11:42 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11219305 | 103793387 | 2023-09-08 14:18 | 2023-09-06 |  | 2023-09-06 10:12 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Hi Team, Please find the attached invoice bill and Installation the balance material of the Wiser Automation is to be done at the address given below : Customer Name : Capt. Sanjay Kumar Mobile Number : 9810727885 Address : H.N-3276, Block B-3, Vasant Kunj, Delhi-110070 Thanks & Regards Zarrar Ahamad Manager - Sales, NCR Home and Distribution Division Schneider Electric Location: Gurgaon Landline: +91 124 6899000 Mobile: +91 9990728046 Email: zarrar.ahamad@se.com Customer Care 18001030011/ 18004254272 9th Floor, Building 10 C DLF Cyber City, Phase II Gurgaon - 122002 INDIA | 2023-09-06 | 2023-09-06 23:55 | No | Commercial Action - Sales | Sanjay Kumar | H.N-3276, Block B-3, Vasant Kunj, | Delhi | 110070 | Delhi | India FS ED&I CSP North Team Seamtek International Pvt. Ltd. GHAZIABAD | Satish Raika Seamtek International Pvt. Ltd. GHAZIABAD | Seamtek International Pvt. Ltd. | following wiser components has been installed 4 channel relay :2 qty | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-11 11:58 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11220169 | 103796719 | 2023-09-06 12:55 | 2023-09-06 |  | 2023-09-06 10:56 | IN8401_N | IN8401_N | IN8401_N |  | Dear Team, Please refer trail mail & kindly depute a Service Engineer for attending to a problem immediately. Product Reference : IN8401 System Docket No. 9008551232 dated 04.05.2023 Site address and contact details as mentioned below: Radisson Blu Hotel GRT 531, Grand Southern Trunk Rd, Parangi Malai, Pazavanthangal, Chennai, Tamil Nadu 600016. Contact Name & No.: Mr.Boopathy @ 9047635693. | 2023-09-06 | 2023-09-09 16:07 | No | Warranty | Radisson Blu Hotel GRT | 531 GST Road, ST.Thomas Mount, | Chennai | 600016 | Tamil Nadu | India FS South2 ED&I CSP UpservePowerSystems Chennai | HARI PRASATH UpservePowerSystems Chennai | Upserve Power Systems | Replaced the below parts. IN8401/16 10 NOs IN8401/16(BZ) 05 NOs | Repair |  | 8- Service Completed | 2023-09-09 16:11 |  |  | 10 | INR | 10 | ENM HOME DISTRIBUTION
WO-11220826 | 103798370 | 2023-09-06 11:21 | 2023-09-06 |  | 2023-09-06 11:08 | UNS5STFAN2M_WE | UNS5STFAN2M_WE | UNS5STFAN2M_WE |  | DOP: 1/3/2022 Unica pure grey switches P: Not Working Shabeer karattil Karattil house Parannakkad , near JM collage , tirur Malappuram dt , pin : 676101 Kerala. Shabeer karattil 9895144888 | 2023-09-06 | 2023-09-07 21:34 | No | Warranty | Shabeer karattil Shabeer karattil | Karattil house Parannakkad , near JM collage , tirur | Malappuram | 676101 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Rejilesh APSMarketingCompany Calicut | APS Marketing Company | visited this site found unica one way switch contact issue and bell switch struck issue unica 1way replaced 1nos, bell switch clean done | Repair |  | 9- Service Validated | 2023-09-07 21:39 |  |  | 55 | INR | 55 | ENM HOME DISTRIBUTION
WO-11221096 | 103794531 | 2023-09-08 14:27 | 2023-09-09 |  | 2023-09-06 11:31 | IH14000100 | IH14000100 | IH14000100 |  | DOP: 5/9/2023 IH14000100 4 Channel Automation Relay IH101ZWIFI Automation Gateway P: installation Customer Name ? Amarjit Singh Contact No ? 9810055154 Address ? House no-32, Road no-57, Punjabi Bagh( west) New Delhi-110026 | 2023-09-06 | 2023-09-09 23:25 | No | Commercial Action - Sales | Amarjit Singh Amarjit Singh | House no-32, Road no-57, Punjabi Bagh( west) | Delhi | 110026 | Delhi | India FS ED&I CSP North Team Seamtek International Pvt. Ltd. GHAZIABAD | Satish Raika Seamtek International Pvt. Ltd. GHAZIABAD | Seamtek International Pvt. Ltd. | following wiser components has been installed : gateway: 1 no 4 ch relay: 1 | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-11 11:28 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11221326 | 103813978 | 2023-09-06 13:16 | 2023-09-06 |  | 2023-09-06 12:36 | US727H_XPW | US727H_XPW | US727H_XPW |  | DOP: 2/6/2023 US727HXPW Qty-1 NO P: Not Working CHANDRA SEKAR NO-12 AD BLOCK 5TH STREET ANNA NAHAR CHENNAI-40 CHANRA SEKAR- 7358071485 payments@techmechelectrify.com | 2023-09-06 | 2023-09-25 15:28 | No | Warranty | CHANRA SEKAR CHANRA SEKAR | NO-12 AD BLOCK 5TH STREET ANNA NAHAR | Chennai | 600040 | Tamil Nadu | India FS South2 ED&I CSP UpservePowerSystems Chennai | HARI PRASATH UpservePowerSystems Chennai | Upserve Power Systems | US727HXPW 01 no replaced. | Repair |  | 9- Service Validated | 2023-09-25 15:59 | ZFRE: 226056562 booked in IN48 as US727HXPW not defined in BFS |  | 19 | INR | 19 | ENM HOME DISTRIBUTION
WO-11221339 | 103814721 | 2023-09-06 13:33 | 2023-09-06 |  | 2023-09-06 12:41 | A9N4P40C | A9N4P40C | A9N4P40C |  | DOP: 8/5/2023 "1 GREEN P.B INDICATION - 2BV-M3N 230V-2NO (LIGHT NO ON) 2 RED P.B INDICATION - 2BV-M4N 230V-7 NO ( NOT WORKING) 3 16A 4P MCB (A9N4P16C) -1 NO (TRIPPING) 4 18 CONTACTOR (LC1E1810M7) -2NO ( SCREW PROBLEM) 5 12A CONTCTOR (LC1E1210M7 -1 NO (NOT WORKING) 6 32A CONTACTOR (LC1E3210M7) - 3 NO (NOT WORKING) 7 40A 4POLE MCB (A9N4P40C) -2 NO (TRIPPING) 8 6A S/P MCB (A9N1P06C) - 1NO (TRIPPING) 9 1NO 1NC ADDON BLOCK(LAEN11)-1 NO (NOT WORKING) BLUE VOLT SERVICES "No.35, 13th MAIN, VRUSHABAVATHI NAGAR, KAMAKSHIPALYA, BANGALORE-79. Bangalore Karnataka 560079" R KAMALA - 9379422201 storesbluevoltservices@gmial.com | 2023-09-06 | 2023-09-19 11:38 | No | Warranty | BLUEVOLT SERVICES | 35, 13th, Main, Vrushabhavathinagar Kamakshipalya | BANGALORE | 560079 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Nagaraja G_P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | Inspected and found below mentioned 1)Ref: A9N4P40C S/N:D2116 = 1 No 2)Ref: A9N4P16C S/N:D2326 - 1 No MCB we have tested MCB working found ok 3)Ref: LC1E180M7 S/N:102245 = 1 No contactor tested working found ok 4)Ref: ZBV-M3N S/N:1022517 = 2 No 5)Ref: ZBV-M4N S/N:1022502 = 7 No 6)Ref: LC1E1210M7 S/N:1023091 = 1No 7)Ref: LC1E1810M7 S/N:1022245 = 1 No 8)Ref: LC1E3210M7 S/N:1023173 = 1 No 9)Ref: A9N4P40C S/N:D2304 = 1 No 10)Ref: LAEN11 S/N:8C2306 = 1 No 11)Ref: A9N1P06C S/N:D2311 = 1 No We retified the problem, hence we will give new good warranty replacement ASAP. Defective taken back to our ASC. | Repair |  | 9- Service Validated | 2023-09-19 11:39 | Hi Team, Material booked zfre Zvo : 226037254 |  | 9 | INR | 9 | ENM HOME DISTRIBUTION
WO-11221478 | 103816141 | 2023-09-06 17:21 | 2023-09-06 |  | 2023-09-06 13:40 | IN8401_16_SP | IN8401_16_SP | IN8401_16_SP |  | DOP: 7/4/2023 Zencelo Switches P: Not Working Manoj K K 9188138022 Kunninoth H Payyambalam Near old Sangeetha talkies Near water tank Kannur 670001 | 2023-09-06 | 2023-09-08 15:58 | No | Warranty | Manoj Manoj | Kunninoth H Payyambalam Near old Sangeetha talkies Near water tank | Kannur | 670001 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Rejilesh APSMarketingCompany Calicut | APS Marketing Company | visited this site found zencelo 32dp switch struck issue in8486/32 replaced 1nos | Repair |  | 9- Service Validated | 2023-09-09 16:02 |  |  | 105 | INR | 105 | ENM HOME DISTRIBUTION
WO-11221530 | 103816232 | 2023-09-06 17:22 | 2023-09-06 |  | 2023-09-06 13:48 | IN8401_16_SP | IN8401_16_SP | IN8401_16_SP |  | DOP: 9/11/2022 IN8401(BZ), IN8401, IN8402, IN8402(BZ),IN8481 P: Not Working Ar. Krishna Mohan "Aaram" , Abalan Nair Road, Nr. Eurokids Malaparamba, Calicut - 673009 Ar. Krishna Mohan 9846149454 | 2023-09-06 | 2023-09-08 15:22 | No | Warranty | Krishna Krishna | "Aaram" , Abalan Nair Road, Nr. Eurokids Malaparamba, Calicut | Kozhikode | 673009 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found zencelo switchs struck issue IN8401_BZ 2NOS IN8402_BZ 1NOS replaced problem solved | Repair |  | 9- Service Validated | 2023-09-08 15:25 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11221701 | 103821136 | 2023-09-07 12:17 | 2023-09-06 |  | 2023-09-06 14:38 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Shivaji Singh, Arunoday Apartment, 28K, Sonali Park, Near Sonali Park Club, Kolkata - 700084 MO ? 7038626968 Issue : unable to reset Smart Door bell. IH100WFVDP ? 1 Qty | 2023-09-06 | 2023-09-11 10:08 | No | Warranty | Shivaji , Singh | Arunoday Apartment, 28K, Sonali Park, Near Sonali Park Club | Kolkata | 700084 | West Bengal | India FS ED&I CSP East Team SREYAM SERVICES BHATPARA | AMIT BHATTACHARYA_SREYAM SERVICES BHATPARA | Sreyam Services(8513) | FOUND DEFFECTIVE VIDEO DOOR BELL REPLACED BY NEW ONE AND DEFFECTIVEMATERIAL IS COLLECTED. | Repair |  | 9- Service Validated | 2023-09-12 10:13 |  |  | 18 | INR | 18 | ENM HOME DISTRIBUTION
WO-11221806 | 103822571 | 2023-09-07 12:04 | 2023-09-06 |  | 2023-09-06 15:11 | E8331D32N_WE_G8 | E8331D32N_WE_G8 | E8331D32N_WE_G8 |  | DOP: 3/10/2022 E8331D32N Qty:1 P: Not Working Kindly check invoice at site | 2023-09-06 | 2023-09-08 13:45 | No | Warranty | Ali Ali | 1303 G Jawa The Metro Zone Behind VR mall Annanagar | Chennai | 600040 | Tamil Nadu | India FS South2 ED&I CSP UpservePowerSystems Chennai | HARI PRASATH UpservePowerSystems Chennai | Upserve Power Systems | Replacement is done. E8331D32N_WE_G8 01 no | Repair |  | 9- Service Validated | 2023-09-08 13:50 |  |  | 18 | INR | 18 | ENM HOME DISTRIBUTION
WO-11223433 | 103844936 | 2023-09-07 11:06 | 2023-09-07 |  | 2023-09-07 10:34 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | DOP: 21/6/2023 IH100WFVDP Qty:1 P: Not Working Manoj.K.G Kondrappassery House P.O Thanissery (Manapadi) Thrissur Pin: 680701 PH:9947669176 | 2023-09-07 | 2023-09-09 09:34 | No | Warranty | Manoj Manoj | Kondrappassery House P.O Thanissery (Manapadi) | Thrissur | 680701 | Kerala | India FS South2 ED&I CSP PrinterPeople Cochin | Vysakht PrinterPeople Cochin | PRINTER PEOPLE-COCHIN | vdf not working only light blinking replaced unit now working fine | Repair |  | 9- Service Validated | 2023-09-09 16:36 |  |  | 65 | INR | 65 | ENM HOME DISTRIBUTION
WO-11224525 | 103849408 | 2023-09-07 13:42 | 2023-09-07 |  | 2023-09-07 12:28 | IH14000100 | IH14000100 | IH14000100 |  | DOP: 12/7/2022 IH14000100 4 Channel Relay IH101ZWIFI Gateway Qty:4 P: Not Working | 2023-09-07 | 2023-09-08 10:00 | No | Warranty | Thomas Xavier | Kakkanad | Cochin | 682001 | Kerala | India FS South2 ED&I CSP PrinterPeople Cochin | Renjith PrinterPeople Cochin | PRINTER PEOPLE-COCHIN | alexa not working resetted alexa added in new account devices added working fine | Repair |  | 9- Service Validated | 2023-09-09 10:00 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11224745 | 103831626 | 2023-09-08 17:24 | 2023-09-09 |  | 2023-09-07 13:46 | A9N2P63C | A9N2P63C | A9N2P63C |  | DOP: 18/5/2023 A9N2P63C Qty:1 P: Not Working MR.JAGADEESH 14,C-SECTOR V G RAO NAGAR KATPADI VELLORE - 632007 PH : 9566365366 | 2023-09-07 | 2023-09-11 15:00 | No | Warranty | JAGADEESH JAGADEESH | 14 C-SECTOR V G RAO NAGAR KATPADI | Vellore | 632007 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | MCB Burnt condition issue - Replacement E-mail : jagadeesh55255@gmail.com | Repair |  | 9- Service Validated | 2023-09-12 09:53 |  |  | 132 | INR | 132 | ENM HOME DISTRIBUTION
WO-11224779 | 103849431 | 2023-09-07 14:22 | 2023-09-07 |  | 2023-09-07 13:59 | P3200_KNOB_N | P3200_KNOB_N | P3200_KNOB_N |  | DOP: 9/3/2023 P3200-4Nos P1001?17NOS P11201?6Nos P2005NS-8Nos P2106---9nos P: Not Working Trinadh Near RTC complex Yelamanchali Visakhapatnam-530013 Ph no: 9849657780 | 2023-09-07 | 2023-09-08 14:40 | No | Warranty | Trinadh Trinadh | Near RTC complex Yelamanchali | Visakhapatnam | 530013 | Andhra Pradesh | India FS ED&I CSP South Team Voltamp Electrical Works Visakhapatnam | Vydha Venkatesh_VOLT AMP ELECTRICAL WORKS Visakhapatnam | Voltamp Electrical Works | Visited the site and found above the Livia switches and socket and fun regulator is not working so today we have observed the problem of 1 way switches back side screw terminal issue and 20 A switches and fun regulator on/off mechanism issue socket plug top issue so Schneider stock replaced so issue closed | Repair |  | 9- Service Validated | 2023-09-08 14:42 |  |  | 70 | INR | 70 | ENM HOME DISTRIBUTION
WO-11229246 | 103880658 | 2023-09-15 22:57 | 2023-09-08 |  | 2023-09-08 11:56 | IH11000200 | IH11000200 | IH11000200 |  | DOP: 6/9/2023 IH11000200 Curtain Controller Qty: 39 P: Installation Sanju No.49,3rd cross Bayanna Layout Battralli virgonagar Post Bangalore-560049 Sanju 9980020958 | 2023-09-08 | 2023-09-13 21:00 | No | Commercial Action - Sales | Sanju Sanju | No.49 3rd cross Bayanna Layout Battralli virgonagar Post | Bangalore | 560049 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Mohammad Riyaz_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | As per the customer's request , we visited the site and installed wiser curtain controller as per the customer requirement and after the installation checked found working ok. IH11000200- 25nos. | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-21 22:04 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11229273 | 103881697 | 2023-09-08 12:55 | 2023-09-08 | Motion Sensor Not working | 2023-09-08 12:08 | CSS54E_WE | CSS54E_WE | CSS54E_WE |  | Ashoke Sharma home sencer 7020126623 Flat no B102 Marvel citrine nera gulmohar city kharadi Flat no B102 Marvel citrine nera gulmohar city kharadi 411014 allternate: 9324669783 15 october 2022 CSS54E_WE Not woring ashokanand.sharma@gmail.com | 2023-09-08 | 2023-09-11 10:34 | No | Warranty | Ashoke Sharma | Flat no B102 Marvel citrine nera gulmohar city kharadi | Pune | 411014 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Sachin Jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the Motion Sensor Not working. customer 4 motion sensor installed. and observed this product is out of warranty. we collect the material to our office and checked. we observed one sensor is not getting output sensor. and another is continuously on. & other two sensor is found ok. | Repair |  | 9- Service Validated | 2023-09-11 10:41 |  |  | 10 | INR | 10 | ENM HOME DISTRIBUTION
WO-11229643 | 103880828 | 2023-09-11 11:18 | 2023-09-11 |  | 2023-09-08 14:25 | A9N2P02C | A9N2P02C | A9N2P02C |  | A9N2P02C Qty:2 P: Not Working Kindly check invouce at site Schneider Electric Systems India Private Ltd (Formerly known as Invensys India Pvt. Ltd) Tamarai Tech Park, SP Plot# 16-19,20A, T.V.K.Industrial Estate,Guindy, Chennai-600032, India Praveen Kumar Balu Lead Engineer - Quality 91 9994186520 praveen.kumarB@non.se.com Customer Care www.schneider-electric.com | 2023-09-08 | 2023-09-15 16:00 | No | Warranty | Schneider Electric Systems (Invensys) | Tamarai Tech Park,SP Plot# 16-19 & 20A, Thiru Vi Ka Industrial Estate, Inner Ring Road,Guindy | Chennai | 600032 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | MCB is not working - Replacement E-mail ID: Praveen.kumarB@non.se.com | Repair |  | 9- Service Validated | 2023-09-15 17:20 |  |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-11229721 | 103865337 | 2023-09-09 12:48 | 2023-09-08 |  | 2023-09-08 14:48 | P1001_6_DG_N | P1001_6_DG_N | P1001_6_DG_N |  | DOP:10/9/2022 PI001 Qty:20 P: Not Working Kindly check invoice at site Mr.Harmeet Singh Vpo Mustfabad,Manka Manki Road. Near Janta Sr Sec School,Distt AMBALA - 133103 Mob No 9315860339 | 2023-09-08 | 2023-09-09 12:53 | No | Warranty | Harmeet Singh | VPO Mustafabad, Manka Manki road, Near Janta Sen Sec School | Yamuna Nagar | 133103 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Rakesh Kumar Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the switches found crack issue. Hence faulty replaced. P1001 - 3 Nos. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-09 13:48 |  |  | 65 | INR | 65 | ENM HOME DISTRIBUTION
WO-11229749 | 103862172 | 2023-09-08 15:57 | 2023-09-08 |  | 2023-09-08 14:58 | A9N4P63C | A9N4P63C | A9N4P63C |  | DOP: 27/8/2023 A9N4P63C P: Not Working SQUARE V ENGINEERING ENTERPRISES Survey no.298/P pipeline road phase-1 IDA jeedimetla Rangareddy Hyderabad 500055 Telangana Govindayya 9182830625 | 2023-09-08 | 2023-09-12 12:00 | No | Warranty | Square V Engineering Enterprises | Survey No. 298(P), Phase I, | Hyderabad | 500055 | Telangana | India FS ED&I CSP South Team Sumanth Electrical Services Hyderabad | Pramoud Kumar_SUMANTH ELECTRICAL SERVICES HYDERABAD | Sumanth Electrical Services | Visited Site and Inspected Schneider Electric A9N4P63C MCB in our observation we found that MCB is having Toggle Free and Dolly Free we have replaced with new MCB A9N4P63C MCB and complaint is closed | Repair |  | 9- Service Validated | 2023-09-12 15:56 |  |  | 10 | INR | 10 | ENM HOME DISTRIBUTION
WO-11229828 | 103888910 | 2023-09-09 13:07 | 2023-09-08 |  | 2023-09-08 15:34 | UNS32DP2M_WE | UNS32DP2M_WE | UNS32DP2M_WE |  | DOP: 13/5/2022 UNS32DP2M_WE P: Not Working BASITH AVALA KUTTOTH (PO) KUTTOTH, PERAMBRA KOZHIKODE - 673525 BASITH 9946921603 | 2023-09-08 | 2023-09-12 17:11 | No | Warranty | BASITH BASITH | AVALA KUTTOTH (PO) KUTTOTH, PERAMBRA | Kozhikode | 673525 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | viisted this site found unica switchs conact issue unica 1way replaced 1nos problem solved | Repair |  | 9- Service Validated | 2023-09-12 17:13 |  |  | 45 | INR | 45 | ENM HOME DISTRIBUTION
WO-11230002 | 103889542 | 2023-09-09 13:09 | 2023-09-08 |  | 2023-09-08 16:42 | EZ9EPVD06N | EZ9EPVD06N | EZ9EPVD06N |  | DOP: 7/3/2023 EZ9EPVD06N : 1 PCS Db Door Knob issue ABDU SHAREEF T K THANNIKKUNDUNGAL HOUSE VALIYA PARAMBA (PO) KODUVALLY (VIA) KODUVALLY KOZHIKODE - 673572 ABDU SHAREEF T K 9447413786 | 2023-09-08 | 2023-09-12 17:07 | No | Warranty | ABDU SHAREEF T K ABDU SHAREEF T K | THANNIKKUNDUNGAL HOUSE VALIYA PARAMBA (PO) KODUVALLY (VIA) KODUVALLY | KOZHIKODE | 673572 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Rejilesh APSMarketingCompany Calicut | APS Marketing Company | visited this site found Vertical phase selector DB, Easy9, metal double door clmb broken db door replaced problem solved | Repair |  | 9- Service Validated | 2023-09-12 17:10 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11230024 | 103889724 | 2023-09-09 10:12 | 2023-09-08 |  | 2023-09-08 16:47 | IN8401_16_SP | IN8401_16_SP | IN8401_16_SP |  | DOP: 29/4/2023 IN8486/32--1 No., IN8486/32(BZ)---1 No. P: Not Working Mr. Sunil PTL Victory Bay Villa No.1, Nayathode, Near St. Joseph Church Airport Kalady Church, Nedumbassery, Cochin--683572. Mr. Sunil 8943259825 | 2023-09-08 | 2023-09-12 16:35 | No | Warranty | Sunil Sunil | PTL Victory Bay Villa No.1, Nayathode, Near St. Joseph Church Airport Kalady Church, Nedumbassery, Cochin | Ernakulam | 683572 | Kerala | India FS South2 ED&I CSP PrinterPeople Cochin | Vysakht PrinterPeople Cochin | PRINTER PEOPLE-COCHIN | in8486/32 2018 batch switch.. invoice not received. replacement not given in warranty | Repair |  | 9- Service Validated | 2023-09-12 16:38 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11232907 | 103892883 | 2023-09-09 12:25 | 2023-09-09 | MCb Dolly Free | 2023-09-09 10:39 | A9N3P10C | A9N3P10C | A9N3P10C |  | DOP: May 2023 A9N3P10C Qty:1 P: Tripping and Short in off condition Kindly check invocie at site Hyosung T&D India pvt. Ltd. IP -11, Khed city, village Nimgaon, taluka Khed, Dist. Pune. Pune 410505 Shubham Joshi 8956970118 | 2023-09-09 | 2023-09-12 11:10 | No | Warranty | Hyosung T & D India Private Limited | Plot no. IP-11, Khed City, Village Nimgaon | Pune | 410505 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Swamesh S_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the MCB found dolly free. this problem observed during testing. we On The MCB then MCB not goes to On. it's dolly free. this MCb is not repairable. So MCB needs to be replaced. Required material :A9N3P10C- 01 nos | Repair |  | 9- Service Validated | 2023-09-12 15:46 | =S= Consig Fill up 226049701 |  | 55 | INR | 55 | ENM HOME DISTRIBUTION
WO-11233679 | 103893105 | 2023-09-09 13:11 | 2023-09-09 |  | 2023-09-09 10:50 | UNS61SW1M_GY | UNS61SW1M_GY | UNS61SW1M_GY |  | DOP: 19/9/2022 UNS61SW1M_GY : 4 PCS UNS62SW1M_GY : 4 PCS P: Switch is Broken MUHAMMED SHUAIB CHENAKKAL HOUSE POOTHIKAD ROAD, KORAN COLONY,MANICHIRA POOMALA (PO), SULTHAN BATHERY WAYANAD - 680581 MUHAMMED SHUAIB 9037737980, 9207288599, | 2023-09-09 | 2023-09-09 15:51 | No | Warranty | MUHAMMED SHUAIB SHUAIB | CHENAKKAL HOUSE POOTHIKAD ROAD, KORAN COLONY,MANICHIRA POOMALA (PO), SULTHAN BATHERY | Wayanad | 673592 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Rejilesh APSMarketingCompany Calicut | APS Marketing Company | visited this site found unica one way switch struck issue unica 1way replaced 1nos | Repair |  | 9- Service Validated | 2023-09-09 15:54 |  |  | 115 | INR | 115 | ENM HOME DISTRIBUTION
WO-11234277 | 103909048 | 2023-09-09 13:47 | 2023-09-09 |  | 2023-09-09 12:27 | UNS5STFAN2M_WE | UNS5STFAN2M_WE | UNS5STFAN2M_WE |  | DOP: 30/8/2023 Unica pure switches P: Not working Farsana Mannil thodi parammal house Keezhuparamba house ,areekode Malappuram dt. Pin : 673639 Kerala. Farsana 9846617185 | 2023-09-09 | 2023-09-11 16:35 | No | Warranty | Farsana Farsana | Mannil thodi parammal house Keezhuparamba house ,areekode | Malappuram | 673639 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found unica switchs abnormal sound issue unica 1way replaced 4nos problem solved | Repair |  | 9- Service Validated | 2023-09-11 16:40 |  |  | 45 | INR | 45 | ENM HOME DISTRIBUTION
WO-11234307 | 103909917 | 2023-09-29 10:52 | 2023-09-09 |  | 2023-09-09 13:06 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | DOP: 9/9/2023 IH100WFVDP Smart Doorbell Qty:1 P: Installation Kindly check invoice at site Mukesh 9451990033 vista A 906 Shalimar one world shahid path gomti nagar lucknow | 2023-09-09 | 2023-09-29 17:59 | No | Commercial Action - Sales | Mukesh Mukesh | vista A 906 Shalimar one world shahid path gomti nagar | Lucknow | 226010 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Abhishek Patel Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Visit the site customer dined for VDP installation due to he think schneider VDP having display . | Commissioning & Installation | Start-up | 8- Service Completed | 2023-09-29 18:06 |  |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-11239997 | 103911952 | 2023-09-11 16:42 | 2023-09-11 |  | 2023-09-11 10:01 | A9N4P63C | A9N4P63C | A9N4P63C |  | MENON K K KRISHNAPARABHA HOUSE ALINGAL MA PULIKKAL ALINGAL, PULIKKAL (PO) KOZHIKODE - 673637 MENON K K 9495543454 A9N26643 : 1 PCS A9N4P63C : 1 PCS Not working Yes Under Warranty Before Three Months LAN Marketing 8075581561 | 2023-09-11 | 2023-09-20 17:38 | No | Warranty | MENON K K | KRISHNAPARABHA HOUSE ALINGAL MA PULIKKAL ALINGAL, PULIKKAL (PO) | KOZHIKODE | 673637 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Rejilesh APSMarketingCompany Calicut | APS Marketing Company | visited this site found miniature circuit breaker - xC60 continous tripping issue A9N4P63C replaced its working fine | Repair |  | 9- Service Validated | 2023-09-20 17:40 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11241179 | 103918889 | 2023-09-12 16:48 | 2023-09-11 |  | 2023-09-11 11:10 | A9N2P63C | A9N2P63C | A9N2P63C |  | MCB 2 pole 63 amps- 4 pcs nit working MCB 2 pole 40 amps - 1 pc Single 25 amps - 2 pc Single pole 16 amps - 1 pc Purchased 4 months knob free issue | 2023-09-11 | 2023-09-14 13:19 | No | Warranty | lovan Jain | hindustan elecrical , samarala road machwada | Ludhiana | 141115 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the isolator(EZ9S66240) found "R" Pole open and EZ9S66263 found dolly free. Hence faulty replaced. EZ9S66240 - 1 Nos. EZ9S66263 - 1 Nos. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-14 13:24 |  |  | 52 | INR | 52 | ENM HOME DISTRIBUTION
WO-11241339 | 103919276 | 2023-09-11 14:05 | 2023-09-11 |  | 2023-09-11 12:07 | IN8485_BZ_N | IN8485_BZ_N | IN8485_BZ_N |  | DOP: 2/2/2023 IN8485 P: Not Working SAMAS HOME CONCEPT LLP OOTY ROAD, CHERANI CHERANI MALAPPURAM-KERALA PIN: 676123 SAMAS HOME CONCEPT LLP 7907427001 | 2023-09-11 | 2023-09-13 21:05 | No | Warranty | SAMAS SAMAS | SAMAS HOME CONCEPT LLP OOTY ROAD, CHERANI CHERANI | Malappuram | 676123 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found zencelo bell switch struck issue IN8485 replaced 1nos problem solved | Repair |  | 9- Service Validated | 2023-09-13 21:08 |  |  | 60 | INR | 60 | ENM HOME DISTRIBUTION
WO-11241371 | 103920842 | 2023-09-12 15:29 | 2023-09-11 |  | 2023-09-11 12:24 | UNS5STFAN2M_WE | UNS5STFAN2M_WE | UNS5STFAN2M_WE |  | DOP: Aug 2022 Unica Pure Switches Qty: 13 P: Not Working Kindly check invoice at site | 2023-09-11 | 2023-09-12 15:32 | No | Warranty | Vikram Singh Singh | Village Chibbra Po Dhurala Near by Shiv M | Kurukshetra | 136118 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the switches found not working. As per product serial number out of warranty. Hence no replacement given to customer. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-12 15:41 |  |  | 105 | INR | 105 | ENM HOME DISTRIBUTION
WO-11241636 | 103924368 | 2023-09-23 20:21 | 2023-09-11 |  | 2023-09-11 14:08 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Badrinath 779, 1st floor, 9th A main off 100 feet road, Indiranagar, 1st stage, Bangalore-560038 Badrinath 9448312528 | 2023-09-11 | 2023-09-23 17:00 | No | Commercial Action - Sales | Badrinath Badrinath | 779, 1st floor, 9th A main off 100 feet road, Indiranagar, 1st stage | Bangalore | 560038 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Mohammad Riyaz_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | As per the customer's PO, we had visited the site and installed wiser automation gateway -1nos and 4 channel relay -2nos as per the customer's requirement and after installation checked found working ok. The same shown to the customer. IH101ZWIFI-1nos IH14000100-2nos | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-23 20:26 |  |  | 20 | INR | 20 | ENM HOME DISTRIBUTION
WO-11241743 | 103920850 | 2023-09-11 16:50 | 2023-09-11 |  | 2023-09-11 14:43 | IN8401_16_SP | IN8401_16_SP | IN8401_16_SP |  | DOP: 30/9/2022 Zencelo switches P: Not Working Jafar sadik Verkot house Chapanangadi kottakkal Malappuram dt , pin : 676503 Kerala. Jafar sadik 9846301878 | 2023-09-11 | 2023-09-13 21:11 | No | Warranty | Jafar sadik Jafar sadik | Verkot house Chapanangadi kottakkal | Malappuram | 676503 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Rejilesh APSMarketingCompany Calicut | APS Marketing Company | visited this site found zencelo one way switchs struck issue IN8401_BZ replaced 1nos | Repair |  | 9- Service Validated | 2023-09-13 21:15 |  |  | 60 | INR | 60 | ENM HOME DISTRIBUTION
WO-11241768 | 103923388 | 2023-09-11 16:47 | 2023-09-11 |  | 2023-09-11 14:51 | UNS5STFAN2M_WE | UNS5STFAN2M_WE | UNS5STFAN2M_WE |  | DOP: 23/6/2023 Unica Pure 6AX 1WAY SWITCH P: Customer is facing issues with Unica Pure 6AX 1 WAY SWITCH Saheer Velayudhanmotta,Peringadi ,Chokli pincode - 673312. Kannur Thafsal np 9567188330 | 2023-09-11 | 2023-09-14 21:00 | No | Warranty | Saheer Saheer | Velayudhanmotta,Peringadi ,Chokli | Kannur | 673312 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site gound unica bell switch struck issue unica bell switch replaced problem solved | Repair |  | 9- Service Validated | 2023-09-15 21:03 |  |  | 70 | INR | 70 | ENM HOME DISTRIBUTION
WO-11241792 | 103924123 | 2023-09-12 11:02 | 2023-09-11 |  | 2023-09-11 15:04 | UNS4STFAN1M_GY | UNS4STFAN1M_GY | UNS4STFAN1M_GY |  | UNS4STFAN1M_GY - 3 pcs UNS61SW1M_GY - 2 pss UNS61SW1M_ WE - 1 pss UNS32DP2M_WE - 1 pcs IN8401 - 1 pcs -- Thanx & Regards, CUSTOMER NAME - Mr Ajay ADDRESS - 37/19F, Mall Road, Kanpur PinCode - 208001 CONTACT NO - + 7897988637 | 2023-09-11 | 2023-09-19 17:40 | No | Warranty | Ajay Ajay | 37/19F, Mall Road, | Kanpur |  | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Aman Khare_Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | SWITCHES HAVING ON/OFF ISSUE SO WE REPLACED | Repair |  | 8- Service Completed | 2023-09-19 17:43 |  |  | 115 | INR | 115 | ENM HOME DISTRIBUTION
WO-11241833 | 103924598 | 2023-09-11 17:30 | 2023-09-11 |  | 2023-09-11 15:20 | SAE-UE-MS-CDBWE | SAE-UE-MS-CDBWE | SAE-UE-MS-CDBWE |  | AS PER YOUR REQUIREMENT, WE ARE ENCLOSING THE FOLLOWING DETAILS: SITE NAME: WATT ADDRESS: GOVIND BHAWAN, 2 BRABOURNE ROAD, 1ST FLOOR, KOLKATA-700001 CONTACT NO.: 9830021011 (MR. MOHIT MADAN) | 2023-09-11 | 2023-09-14 15:37 | No | Warranty | Watt | R5-MB-3, 22B, Rabindra Sarani, | Kolkata | 700073 | West Bengal | India FS ED&I CSP East Team SREYAM SERVICES BHATPARA | AMIT BHATTACHARYA_SREYAM SERVICES BHATPARA | Sreyam Services(8513) | FOUND PIR SENSOR REPLACED BY NEW ONE AND DEFFECTIVE MATERIAL IS COLLECTED. | Repair |  | 9- Service Validated | 2023-09-15 15:38 | Part not mapping properly in BFS =S= Free Order 226040628 has been saved |  | 14 | INR | 14 | ENM HOME DISTRIBUTION
WO-11241985 | 103927444 | 2023-09-11 17:40 | 2023-09-11 |  | 2023-09-11 16:42 | UNS5STFAN2M_WE | UNS5STFAN2M_WE | UNS5STFAN2M_WE |  | Bhuvi by amsha - switch not working | 2023-09-11 | 2023-09-12 15:11 | No | Warranty | Radha Thakore Radha Thakore | E-302 Bhuvi by amsha kadubeesanhalli road panathur | Bangalore | 560103 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | C Gunasekaran_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | We had visited the site and checked the customer reported unica switch. Found dolly free issue. So we had replaced and checked working ok. | Repair |  | 9- Service Validated | 2023-09-12 23:14 |  |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-11242233 | 103922557 | 2023-09-12 11:52 | 2023-09-11 |  | 2023-09-11 17:50 | 18730 | 18730 | 18730 |  | DOP: 25/3/2023 Reference -18730 & 18724 Qty:1 P: MCB reset issue ELECTRIC LOCO SHED Bondamunda Bondamunda, Rourkela, Odisha 769011 Sunil Kumar 9777582509 | 2023-09-11 | 2023-09-18 19:14 | No | Warranty | Bondamunda Loco Shed | Diesel Shed Rd, Bondamunda, | Rourkela | 769011 | Odisha | India FS ED&I CSP East Team UNIVERSAL ELECTRIC POWER SOLUTION BHUBANESWAR | Banty Kumar_UNIVERSAL ELECTRIC POWER SOLUTION BHUBANESWAR | Universal Electric Power Solution(500012032) | material to be booked | Repair |  | 9- Service Validated | 2023-09-18 19:17 |  |  | 332 | INR | 332 | ENM HOME DISTRIBUTION
WO-11242263 | 103928796 | 2023-09-12 11:28 | 2023-09-11 | NA | 2023-09-11 18:00 | A9N3P63C | A9N3P63C | A9N3P63C |  | DOP: 25/2/2023 A9N3P63C Qty:3 P: a) One MCB Pole has direct Contact. b) One MCB Pole has no Contact. c) One MCB ON /OFF is not working dolly free WELDSONIC WELDING TECHNOLOGY JAGADISHPUR KAYALPARA PO - JAGADISHPUR HAT DIST - HOWRAH -711115 Location - Near Jagadishpur Hat TMC party office Bijan 9163045650 | 2023-09-11 | 2023-09-13 14:45 | No | Warranty | WELDSONIC WELDING TECHNOLOGY | JAGADISHPUR KAYALPARA PO - JAGADISHPUR HAT null | Howrah | 711115 | West Bengal | India FS ED&I CSP East Team B.D Electroservices Kolkata | RAHUL RAY_B.D Electroservices Kolkata | B.D Electroservices(500017330) | On received of ZVO material will delivered to customer. | Repair |  | 9- Service Validated | 2023-09-13 17:32 |  |  | 20 | INR | 20 | ENM HOME DISTRIBUTION
WO-11242292 | 103928896 | 2023-09-15 12:56 | 2023-09-11 |  | 2023-09-11 18:14 | X2005WH_N | X2005WH_N | X2005WH_N |  | DOP: 21/10/2022 X1181WH-10 Nos, X2005WH-10 nos, X2106WH-10 P: not working Nishant 11A, Asset Sunnydays Civil Station Road,Kudappanakunnu Peroorkada, Trivandarm-695005 Nishant 7558889104 | 2023-09-11 | 2023-09-21 15:52 | No | Warranty | Nidhand Nidhand | Asset Sunnydays Civil station road,Kudappanakunnu Peroorkada | Thiruvananthapuram | 695005 | Kerala | India FS ED&I CSP South Team Connect Plus Technologies Cochin | Azif J_Connectplus Technologies Cochin | Connect Plus Technologies | Changed eight numbers of livia 6A socket . | Repair |  | 8- Service Completed | 2023-09-21 15:53 |  |  | 5 | INR | 5 | ENM HOME DISTRIBUTION
WO-11242357 | 103929643 | 2023-09-12 10:50 | 2023-09-11 |  | 2023-09-11 18:29 | EZ9ESND06 | EZ9ESND06 | EZ9ESND06 |  | DOP: 9/9/2023 EZ9ESND06 Qty: 1 PCS P: Db Door Knob Issue SAMAD CHAPPANGATHODI ELAMARAM CHERUVAYOOR (PO), EDAVANNAPARA MALAPPURAM - 673645 SAMAD 9961665004 | 2023-09-11 | 2023-09-14 20:51 | No | Warranty | Samad Samad |  | MALAPPURAM | 673645 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Rejilesh APSMarketingCompany Calicut | APS Marketing Company | visited this site found Easy9 - SPN DB - double door lock issue db door lock fitting properly done, door lock working fine | Repair |  | 9- Service Validated | 2023-09-14 20:56 |  |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11242395 | 103929768 | 2023-09-12 10:14 | 2023-09-11 | 4 Channel Relay is not working | 2023-09-11 18:37 | IH14000100 | IH14000100 | IH14000100 |  | DOP: 20/8/2023 IH14000100 Qty:1 P: Not Working Abhijit Bhosale 9822373375 Flat 404, Seya Apartment, Opp. Union Bank, Near Navashya Maruti Mandir, Sinhgad Road, Pune ? 411030. | 2023-09-11 | 2023-09-12 11:29 | No | Warranty | Abhijit Abhijit |  | Pune | 411030 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Kunal jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked 4 Channel Relay is not working. this relay is inactive so we reset the relay and set up again but again inactive. we reset the 4 - 5 times problem not resolved. So Relay Needs to be replaced. Required Material : IH14000100- 01 nos | Repair |  | 9- Service Validated | 2023-09-12 15:44 | =S= Consig Fill up 226023494 |  | 40 | INR | 40 | ENM HOME DISTRIBUTION
WO-11245315 | 103931267 | 2023-09-13 15:44 | 2023-09-12 |  | 2023-09-12 09:33 | EZ9F71463 | EZ9F71463 | EZ9F71463 |  | Dear team, Pls register complaint of EZ9F71463 DETAIL OF CUSTOMER Kunwar Singh Blue olives Near NM college C? Mahak Hotel Mansa 151505 Punjab 9914102102 | 2023-09-12 | 2023-09-13 17:18 | No | Warranty | Kunwar Singh | Blue olives Near NM college C? Mahak Hotel | Mansa | 151505 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the mcb found one pole open & melt. Hence faulty replaced. EZ9F71463 - 1 Nos. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-14 10:49 |  |  | 130 | INR | 130 | ENM HOME DISTRIBUTION
WO-11245343 | 103952116 | 2023-09-12 10:21 | 2023-09-12 | MCb Dolly free | 2023-09-12 09:59 | A9N4P63C | A9N4P63C | A9N4P63C |  | 4 pole 63c curve mcb tripping issue Purchased July 2023 , Shre Sai Electrical | 2023-09-12 | 2023-09-12 11:01 | No | Warranty | Amol pathangane | 6 B, parvathy industrial estate , opposite adinath society near bansali metals | Pune | 411009 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Amit Patil_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the MCB found dolly free. this problem observed during testing. we On The MCB then MCB not goes to On. it's dolly free. this MCb is not repairable. So MCB needs to be replaced. Required material : A9KF71463BQ- 01 nos | Repair |  | 9- Service Validated | 2023-09-13 10:22 | =S= Consig Fill up 226041544 |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11245579 | 103952811 | 2023-09-12 13:52 | 2023-09-12 |  | 2023-09-12 10:39 | EZ9R35263 | EZ9R35263 | EZ9R35263 |  | 2 no RCCB purchased from Flipkart in OCt2022 , RCCb - 63 amps 30 ma , 2 pole | 2023-09-12 | 2023-09-12 13:15 | No | Warranty | Deepak Saranagi | B 9 , Krishna Vihar , kolathia, near laxmi mandap . | Bhubaneswar | 751030 | Odisha | India FS ED&I CSP East Team UNIVERSAL ELECTRIC POWER SOLUTION BHUBANESWAR | RAMESH PRABHAT_UNIVERSAL ELECTRIC POWER SOLUTION BHUBANESWAR | Universal Electric Power Solution(500012032) | material to be booked | Repair |  | 9- Service Validated | 2023-09-16 13:25 |  |  | 11 | INR | 11 | ENM HOME DISTRIBUTION
WO-11246017 | 103953021 | 2023-09-12 11:17 | 2023-09-12 |  | 2023-09-12 10:49 | EZ9F56463 | EZ9F56463 | EZ9F56463 |  | EZ9F56463 Sr No : D2310 DOM March 2023 P: Knob Free / Not switched ON Metalink Engineers 3636, Sector 32 A Chandigarh Road Ludhiana 145526 Mr Ashwani 6284763485,9023506414 Mail Id : aakash@nmaindia.com | 2023-09-12 | 2023-09-12 11:19 | No | Warranty | Metalink Engineers | Sector 32-A ,3636 Chandigarh Road | Ludhiana | 141010 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the MCB-(EZ9F56463 ) found not getting on due to dolly free and (EZ9F71240) found phase missing & dolly free and contactor found phase missing. Hence faulty replaced. EZ9F71463 - 1 No - 1 Nos. LC1E1210M7 - 2 Nos. EZ9F71240 - 2 Nos. email : aakash@nmaindia.com | Repair |  | 9- Service Validated | 2023-09-12 15:12 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11246736 | 103952007 | 2023-09-12 15:19 | 2023-09-12 |  | 2023-09-12 11:00 | IN8486/20(BZ) | IN8486/20(BZ) | IN8486/20(BZ) |  | DOP: 28/10/2022 IN8481/16 IN8486/20 P: Not Working Muhammed Alfan Landmark maple, Flat 6E Kunnathpalam Calicut - 673019 Muhammed Alfan 8281555626 | 2023-09-12 | 2023-09-15 13:15 | No | Warranty | Muhammed Alfan Muhammed Alfan |  | Kozhikode | 673019 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Rejilesh APSMarketingCompany Calicut | APS Marketing Company | visited this site found zencelo 16ax & 20dp switchs cracked IN8486/16 2NOS IN8486/20 1NOS replaced problem solved | Repair |  | 9- Service Validated | 2023-09-15 13:18 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11246817 | 103952060 | 2023-09-12 17:26 | 2023-09-12 |  | 2023-09-12 11:20 | IH14000100 | IH14000100 | IH14000100 |  | DOP: 15/6/2022 IH14000100 4 Channel Relay Qty:1 P: Not working 124, Vijaya Springwoods, Manipal County Road, Singasandra, Near Star Market, Bangalore - 560068, Contact Person: Harsha Kodnad Contact Number: 9980824605 | 2023-09-12 | 2023-09-13 18:44 | No | Warranty | Harsha Harsha | #124, Vijaya Springwoods, Manipal County Road, Singasandra Bangalore - 68 Near Star Market | Bangalore | 560068 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Mohammad Riyaz_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported wiser 4 channel relay the problem found was R4 channel load continuous ON. we resetted the relay then checked same load is On not getting off. So we replaced new relay and checked found working ok. The same shown to the customer. | Repair |  | 9- Service Validated | 2023-09-13 18:59 |  |  | 28 | INR | 28 | ENM HOME DISTRIBUTION
WO-11246974 | 103952822 | 2023-09-12 13:56 | 2023-09-12 |  | 2023-09-12 12:34 | UNS61SW1M_GY | UNS61SW1M_GY | UNS61SW1M_GY |  | DOP: 30/7/2022 EZ9ETND06 : 1 Pcs UNS61SW1M_GY - 2 Pcs UNS62SW1M_GY : 2 Pcs UNSCP16M_GY : 1Pcs P: Db door knob issue, switch not working, plate broken. BAPU SHAKEEL MP KODIYATHUR P.O SUNSET LANE HOUSE, CHATHAPARAMBA PIN - 673602 MUKKAM, CALICUT BAPU SHAKEEL MP 9048838978 | 2023-09-12 | 2023-09-14 21:10 | No | Warranty | BAPU SHAKEEL MP BAPU SHAKEEL MP | KODIYATHUR P.O SUNSET LANE HOUSE, CHATHAPARAMBA | Kozhikode | 673602 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Rejilesh APSMarketingCompany Calicut | APS Marketing Company | visited this customer place found unica switchs alighnment issue, switchs serviced problem solved. 16md plate serviced and 6way tpn db lock action missing , db door lock replaced problem solved | Repair |  | 9- Service Validated | 2023-09-14 21:15 |  |  | 40 | INR | 40 | ENM HOME DISTRIBUTION
WO-11247206 | 103956830 | 2023-09-12 17:05 | 2023-09-12 |  | 2023-09-12 14:29 | IH101ZWIFI | IH101ZWIFI | IH101ZWIFI |  | DOP: 5/12/2022 IH101ZWIFI Gateway Qty:1 P: Gateway offline Mr. Prasun Patra MO -8971067788 Electronica Shop No 1 Rajdeep Enclave 8/1 Baisnab Ghata road Garia Kolkata ? 700084 | 2023-09-12 | 2023-09-13 13:57 | No | Warranty | Electronica | Ground Floor, Shop No. 1, Rajdeep Enclave, | Kolkata | 700084 | West Bengal | India FS ED&I CSP East Team SREYAM SERVICES BHATPARA | AMIT BHATTACHARYA_SREYAM SERVICES BHATPARA | Sreyam Services(8513) | AS PER CUSTOMER CONFIRMATION PROBLEM WASC RESOLVED. SO WE CLOSED THE COMPLAIN. | Repair |  | 9- Service Validated | 2023-09-13 13:57 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11247223 | 103961368 | 2023-09-14 11:56 | 2023-09-12 |  | 2023-09-12 14:38 | A9N2P32C | A9N2P32C | A9N2P32C |  | A9N2P32C DD2023-W04-611 Qty:1 P: Not Working | 2023-09-12 | 2023-09-14 14:16 | No | Warranty | Kapoor Electro World Pvt Ltd | Shop 1107 Near Division 3 Samrala rd null | Ludhiana | 141008 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | checked the mcb found not giving output. Hence faulty, replaced. A9N2P32C - 1 Nos. Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-14 17:07 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11247260 | 103957212 | 2023-09-12 15:04 | 2023-09-12 |  | 2023-09-12 14:42 | UNS5STFAN2M_WE | UNS5STFAN2M_WE | UNS5STFAN2M_WE |  | DOP: 7/8/2023 UNS5STFAN2M_WE Qty : 6 PCS P: Not working ISSUDHEEN ANSARI KIZHOKKOTH (PO) KODUVALLY KOZHIKODE - 673572 ISSUDHEEN 9947420586 | 2023-09-12 | 2023-09-13 11:17 | No | Warranty | ISSUDHEEN ISSUDHEEN | ANSARI HOUSE KIZHAKOTH KODUVALLY CALICUT | Kozhikode | 673572 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found unica 5st fan regulator speed always same unica 5stfan regulator replaced 1nos | Repair |  | 9- Service Validated | 2023-09-13 11:21 |  |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11247865 | 103961244 | 2023-09-19 20:14 | 2023-09-12 |  | 2023-09-12 16:02 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | IH100WFVDP Smart Doorbell Qty:1 P: Installation Kindly check invoice at site Aijaz Hassan, C4 Smart Neighbourhood near Thindlu Gate Sarjapura Chikka Tirupati Road BENGALURU, Karnataka, 562125 Phone: 9591502591 | 2023-09-12 | 2023-09-19 15:27 | No | Commercial Action - Sales | Aijaz Aijaz | C4 Smart Neighbourhood near Thindlu Gate Sarjapura Chikka Tirupati Road | Bangalore | 562125 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | C Gunasekaran_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | As per customer request, we had visited the site and resolved customer facing login issue and voice issue. and checked live and video call found working ok. | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-19 21:32 |  |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11247891 | 103964854 | 2023-09-13 14:01 | 2023-09-12 |  | 2023-09-12 16:16 | SAE_UE_MS_CSAWE | SAE_UE_MS_CSAWE | SAE_UE_MS_CSAWE |  | DOP: 10/9/2023 SAE_UE_MS_CSAWE Qty:1 P: Not Working Kindly check invoice at site | 2023-09-12 | 2023-09-14 15:10 | No | Warranty | Manas Manas | B 213 CR Park | Delhi | 110019 | Delhi | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the sensor and found sensor have output issue, We replace the faulty sensor with new. | Repair |  | 9- Service Validated | 2023-09-14 18:03 |  |  | 26 | INR | 26 | ENM HOME DISTRIBUTION
WO-11248016 | 103964634 | 2023-09-12 18:36 | 2023-09-12 |  | 2023-09-12 16:55 | A9N4P63D | A9N4P63D | A9N4P63D |  | DOP: 21/6/2022 A9N4P63D A9N4P32C P: Not Working 4TH FLOOR,187, HIFLY CAPITAL,VAISHALI NAGAR ROAD HAFEEZPET, RANGAREDDY HYDERABAD,500049 Telangana Jyothi 8340021693 | 2023-09-12 | 2023-09-17 12:00 | No | Warranty | Jyothi Jyothi | 4TH FLOOR,187, HIFLY CAPITAL,VAISHALI NAGAR ROAD HAFEEZPET, RANGAREDDY | Hyderabad | 500049 | Telangana | India FS ED&I CSP South Team Sumanth Electrical Services Hyderabad | Venkata Prasad_SUMANTH ELECTRICAL SERVICES HYDERABAD | Sumanth Electrical Services | Visited the Site and Inspected the Schneider Electric- A9N4P63D-01 No's and A9N4P32C-01 No's. Here in our observation we found that the MCB is not working. So,we have replaced with New MCB A9N4P63D-01 No's and A9N4P32C-01 No's and we have checked the ON/OFF operations which found OK. Complaint is closed. | Repair |  | 9- Service Validated | 2023-09-18 14:54 |  |  | 10 | INR | 10 | ENM HOME DISTRIBUTION
WO-11251236 | 103969168 | 2023-09-13 10:58 | 2023-09-13 | NA | 2023-09-13 09:49 | E3034H1EBGS | E3034H1EBGS | E3034H1EBGS |  | ear Sir / Ma'am Please arrange to send the service personnel at the following site : Pankaj seksaria 12,Ballygunge park road Kolkata 700019 M.9007430380 Thanks & Regards -- BIBEK DAS (TOSHNIWAL ELECTRICALS) 5/1, CLIVE ROW KOLKATA-700001 MOBILE & WHATSAPP- 9903762242 | 2023-09-13 | 2023-09-16 14:00 | No | Warranty | Pankaj seksaria | 12,Ballygunge park road | Kolkata | 700019 | West Bengal | India FS ED&I CSP East Team B.D Electroservices Kolkata | KOUSHIK MONDAL_B.D Electroservices Kolkata | B.D Electroservices(500017330) | On received of ZVO material will delivered to customer. | Repair |  | 9- Service Validated | 2023-09-16 14:00 | =S= Free Order 226055325 has been saved |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-11251251 | 103973654 | 2023-09-13 11:04 | 2023-09-13 | NA | 2023-09-13 10:06 | 5502DAL2PS | 5502DAL2PS | 5502DAL2PS |  | Client Name :Mr.Pritam Beria Trade Name : Oversure Developers Pvt Ltd. Site Address : 19A, Sarat Bose Road 5th Floor, Flat no :5B Kolkata- 700020 Contact Person : Mr.Koushick Sarkar Contact No: 9038783902 | 2023-09-13 | 2023-09-16 15:15 | No | Warranty | Pritam Beria | Oversure Developers Pvt Ltd.19A, Sarat Bose Road 5th Floor, Flat no :5B | Kolkata | 700020 | West Bengal | India FS ED&I CSP East Team B.D Electroservices Kolkata | RAHUL RAY_B.D Electroservices Kolkata | B.D Electroservices(500017330) | On received of ZVO material will delivered to customer. | Repair |  | 9- Service Validated | 2023-09-16 14:40 |  |  | 18 | INR | 18 | ENM HOME DISTRIBUTION
WO-11252991 | 103967655 | 2023-09-13 12:40 | 2023-09-13 |  | 2023-09-13 11:44 | P3100_DG | P3100_DG | P3100_DG |  | DOP: 22/5/2023 P3100 Livia Swicthes Qty : 1 P: Not Working Sabu 9656228576 Kanniyattukudiyil house valayampady choondi puthankurish pin 682308 | 2023-09-13 | 2023-09-14 15:21 | No | Warranty | Sabu Sabu | Kanniyattukudiyil house valayampady choondi puthankurish | Ernakulam | 682308 | Kerala | India FS South2 ED&I CSP PrinterPeople Cochin | Renjith PR PrinterPeople Cochin | PRINTER PEOPLE-COCHIN | 2018 batch.. invoice provided. p3100 1 no speed adjustment issue P3100 1 nos replaced | Repair |  | 9- Service Validated | 2023-09-15 15:22 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11253007 | 103991032 | 2023-09-14 18:00 | 2023-09-13 |  | 2023-09-13 11:54 | E8334L1_WE_G8 | E8334L1_WE_G8 | E8334L1_WE_G8 |  | sidhi 18(3) mariamman kovil street kottai thottam ,shastri nager east behind new bus stand tirupur-641602 9443741401 | 2023-09-13 | 2023-09-16 15:52 | No | Warranty | sidhi sidhi | 18(3) mariamman kovil street kottai thottam ,shastri nager east behind new bus stand | Tiruppur | 641602 | Tamil Nadu | India FS South2 ED&I CSP GRControlSystems Coimbatore | Mani kandan GRControlSystems Coimbatore | GR Control Systems-Coimbatore | Site Visit done. Customer didn't purchase Inner model cover there is no product issue. Informed the customer to purchase the same. | Repair |  | 8- Service Completed | 2023-09-16 16:08 |  |  | 62 | INR | 62 | ENM HOME DISTRIBUTION
WO-11253419 | 103995769 | 2023-09-14 06:03 | 2023-09-13 |  | 2023-09-13 14:31 | P3200_DG | P3200_DG | P3200_DG |  | DOP: 6/5/2023 P3200 P: Not Working SAMAS HOME CONCEPTS LLP OOTY ROAD CHERANI MALAPPURAM-KERALA PIN: 676123 SAMAS HOME CONCEPTS LLP 7907427001 | 2023-09-13 | 2023-09-20 17:42 | No | Warranty | SAMAS SAMAS | SAMAS HOME CONCEPT LLP OOTY ROAD, CHERANI CHERANI | Malappuram | 676123 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Rejilesh APSMarketingCompany Calicut | APS Marketing Company | visited this site found livia switchs dolly crack issue P1001 10NOS P1002 3NOS P3200 1NOS replaced | Repair |  | 9- Service Validated | 2023-09-20 17:53 | Hi Team, Below material booked zfre Zvo : 226060770 |  | 60 | INR | 60 | ENM HOME DISTRIBUTION
WO-11254095 | 104002359 | 2023-09-14 05:42 | 2023-09-13 |  | 2023-09-13 18:25 | UNS32DP2M_GY | UNS32DP2M_GY | UNS32DP2M_GY |  | DOP: 2/6/2022 UNS32DP2M_GY Qty: 2 PCS P: Not Working SADHIQUE KAPPALAM KAPPALAM HOUSE VALATHAI PALAM MUKKAM (PO), MUKKAM KOZHIKODE - 673602 SADHIQUE KAPPALAM 9645147844 | 2023-09-13 | 2023-09-14 20:58 | No | Warranty | SADHIQUE KAPPALAM SADHIQUE KAPPALAM | KAPPALAM HOUSE VALATHAI PALAM MUKKAM (PO), MUKKAM | KOZHIKODE | 673602 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found unica 32dp switch action missing. UNS32DP2M_GY replaced 1nos problem solved | Repair |  | 9- Service Validated | 2023-09-14 21:01 |  |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11254713 | 104005403 | 2023-09-14 05:48 | 2023-09-13 |  | 2023-09-13 18:46 | P1001_6_DG_N | P1001_6_DG_N | P1001_6_DG_N |  | DOP: 13/7/2022 P1132 Qty: 2 PCS P: Not working PEETHAM BARAN POYIL HOUSE PALLIKKARA (PO) NEAR PALLIKKARA VAYANSHALA, PAYYOLI KOZHIKODE - 673522 PEETHAM BARAN 9847197094 | 2023-09-13 | 2023-09-14 15:25 | No | Warranty | Mr PEETHAMBARAN | POYIL HOUSE PALLIKKARA POST PAYYOLY, NEAR PALLIKKARA POST OFFICE, | Kozhikode | 673522 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found livia 32dp switch crack issue p1132 replaced 1nos problem solved | Repair |  | 9- Service Validated | 2023-09-14 15:30 |  |  | 45 | INR | 45 | ENM HOME DISTRIBUTION
WO-11256833 | 104004531 | 2023-09-14 09:58 | 2023-09-13 | Hence , This product is needed to be replaced XB5AW34M2N 01Nos | 2023-09-14 09:45 | XB5AW34M2N | XB5AW34M2N | XB5AW34M2N |  | DOM: 2023-W30 XB5AW34M2N Qty:1 P: Lamp not working Trimasys Control Solution Pvt .Ltd T Block,W-36 , MIDC , Bhosari, Pune- 411026 India Mr. Vishal Ambre 9637486051 | 2023-09-14 | 2023-09-16 15:23 | No | Warranty | Trimasys Control Solutions Pvt. Ltd | W-36, MIDC, | pune | 411026 | Maharashtra | India FS ED&I CSP West Team Alliance Controls Pvt Ltd Pune | Rohit Srivastav_Alliance Controls Pvt. Ltd | Alliance Controls Pvt. Ltd. (7966) | 1) Visited to site & discuss with customer and checked 01 Nos XB5AW34M2N with Sr no . 2023-W30 (2) Given 226VAC supply to the illumination lamp and observed lamp not glowing inside panel other 03Nos illumation lamp working proper.(3) Hence , This product is needed to be replaced XB5AW34M2N 01Nos | Repair |  | 9- Service Validated | 2023-09-16 15:23 | =S= Consig Fill up 226053101 |  | 1 | INR | 1 | ENM HOME DISTRIBUTION
WO-11258513 | 104025638 | 2023-09-16 16:30 | 2023-09-14 |  | 2023-09-14 11:07 | A9N4P40C | A9N4P40C | A9N4P40C |  | 2 pole continuity not coming purchased on Feb 2023 agarwal electrical | 2023-09-14 | 2023-09-22 17:09 | No | Warranty | Viswanath Viswanath | plaot no 138 , Sector 24 | Faridabad | 121005 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mcb found phase missing, Hence faulty replaced. A9N4P40C - 1 nos A9N4P63C - 1 nos Email : id not provided by customer . | Repair |  | 8- Service Completed | 2023-09-22 17:15 |  |  | 52 | INR | 52 | ENM HOME DISTRIBUTION
WO-11258795 | 104028019 | 2023-09-15 11:37 | 2023-09-14 |  | 2023-09-14 12:38 | A9N4P63C | A9N4P63C | A9N4P63C |  | 63 aap 4 pole , make and break issue Supplied mAy 2023 | 2023-09-14 | 2023-09-18 14:38 | No | Warranty | JP Enterprises | SCF 18, Shop No 5, DLF Industrial Area, Phase 1 | Faridabad | 121003 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | checked the mcb found phase missing, Hence faulty, replaced. A9N4P63C - 1 Nos. Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-19 14:40 |  |  | 45 | INR | 45 | ENM HOME DISTRIBUTION
WO-11258931 | 104029727 | 2023-09-15 11:21 | 2023-09-14 |  | 2023-09-14 13:29 | A9N4P63C | A9N4P63C | A9N4P63C |  | A9N4P63C D2320 Qty:1 P: Dolly free | 2023-09-14 | 2023-09-15 14:40 | No | Warranty | New Ankur Confessionary Work | A7/120 Electrosteel compound Southside of GT rd Industrial Area null | Ghaziabad | 201009 | Uttar Pradesh | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mcb found phase missing, Hence faulty replaced. A9N4P63C - 1 nos Email : id not provided by customer . | Repair |  | 8- Service Completed | 2023-09-15 14:43 |  |  | 52 | INR | 52 | ENM HOME DISTRIBUTION
WO-11258944 | 104028341 | 2023-09-14 17:55 | 2023-09-14 |  | 2023-09-14 13:39 | U202SPM/1>B00-OS | U202SPM/1>B00-OS | U202SPM/1>B00-OS |  | DOP: 6/6/2023 U202SPM/1>B00-OS Qty -1 no P: Not Working Rahul,NO-12 AD BLOCK,5TH STREET,ANNA NAHAR,CHENNAI-40 CHANRA SEKAR-7358071485 payments@techmechelectrify.com | 2023-09-14 | 2023-09-19 18:47 | No | Warranty | CHANRA SEKAR CHANRA SEKAR | NO-12 AD BLOCK 5TH STREET ANNA NAHAR | Chennai | 600040 | Tamil Nadu | India FS South2 ED&I CSP UpservePowerSystems Chennai | HARI PRASATH UpservePowerSystems Chennai | Upserve Power Systems | U202SPM/1>B00-OS 01 NO. replacement is given to the customer. | Repair |  | 9- Service Validated | 2023-09-19 18:49 |  |  | 18 | INR | 18 | ENM HOME DISTRIBUTION
WO-11259270 | 104031507 | 2023-09-15 12:23 | 2023-09-14 |  | 2023-09-14 15:58 | X1001WH_M3M_N | X1001WH_M3M_N | X1001WH_M3M_N |  | DOP: 2/12/2022 X1181WH -10, X2106- 10 P: Not working Asset Lineage Flat no.3b, Sasthamangalam Trivandrum 695010 Kerala Shreyan 9895118317 | 2023-09-14 | 2023-09-15 12:42 | No | Warranty | In charge Shreyan | Asset Lineage Flat 3B Shasthamangalam Pippinmoodu | Thiruvananthapuram | 695010 | Kerala | India FS ED&I CSP South Team Connect Plus Technologies Cochin | Azif J_Connectplus Technologies Cochin | Connect Plus Technologies | replaced all the faulty switches. | Repair |  | 8- Service Completed | 2023-09-21 15:59 | Hi Team, Material booked zfre Zvo : 226058806 |  | 1 | INR | 1 | ENM HOME DISTRIBUTION
WO-11259380 | 104036324 | 2023-09-15 15:11 | 2023-09-14 |  | 2023-09-14 16:54 | IN8401_16_BZ | IN8401_16_BZ | IN8401_16_BZ |  | 6 nos 20 amp dp switch not working Consumer Account Mrs. Chinki tambi 78 , new rajdhani enclave , vikash marg , New Delhi 110092 Delhi India Purchased on Feb 2023 | 2023-09-14 | 2023-09-16 15:12 | No | Warranty | Chinki tambi | 78 , new rajdhani enclave , vikash marg , | New Delhi | 110092 | Delhi | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the switches and socket and found switches and socket have damage condition and POP available on the switches . We ask to customer how to damage the switches, customer have no idea. We suggest to customer we not consider the damage condition switches in warranty and not provide the replacement. So we close the complete. | Repair |  | 8- Service Completed | 2023-09-16 15:14 | 226053413 Cancelled as per verbal communication from karamveer. |  | 14 | INR | 14 | ENM HOME DISTRIBUTION
WO-11259437 | 104037291 | 2023-09-15 11:29 | 2023-09-14 |  | 2023-09-14 17:26 | A9N4P63C | A9N4P63C | A9N4P63C |  | c63 A 4 pole - MCB doll false January 2023 | 2023-09-14 | 2023-09-18 16:40 | No | Warranty | A S Industries | S 45 , Bulandshahar Road Industrial Area | Ghaziabad | 201001 | Uttar Pradesh | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | checked the mcv found dolly free, hence faulty, replaced. A9N4P63C - 1 Nos. Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-19 16:42 |  |  | 52 | INR | 52 | ENM HOME DISTRIBUTION
WO-11262612 | 104039151 | 2023-09-15 11:30 | 2023-09-15 | Switch not operating | 2023-09-15 09:44 | EZ9F21225 | EZ9F21225 | EZ9F21225 | D 1721 | Dear Sir, Please find below product details: 1. Name of Customer: Shrikrishna Mahavir Electrical Works, KHED-SHIVAPUR 2. Site Address: - Elegance,Gat No.780/1,2, Near Toll Plaza,Khed Shivapur, Tal: Haveli,Dist:Pune - 412205 3. Name of contact person at site :- Mr. Amit Sangali 4. Contact Phone / Mob. No: 9168888194 5. Defective product details:- EZ9F21225 6. Product Make:-Schneider Electric 7. Nature of Defect: - Product Defective 8. Shutdown availability if applicable - yes 9. Serial No: or DOM of the product- D1721 10. Dealer Name /OA no. /Invoice Details: - Shrikrishna Mahavir Electrical Works 11. Commissioned / Installed date:- 12. Name & phone No: of the person registering the complaint: Mr. Amit Sangali (Shrikrishna Mahavir Electrical Works, KHED-SHIVAPUR) Phone number. 9168888194 | 2023-09-15 | 2023-09-18 11:21 | No | Warranty | Shrikrishna Mahavir Electrical Works | Ground Floor, Shop No.3 and 4, | Pune | 412205 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Samadhan S_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the Switches found that the Switch not operating. but we taken on/off operation it's working found ok. there is no problem observed in switch. it's found ok. | Repair |  | 9- Service Validated | 2023-09-18 11:24 |  |  | 55 | INR | 55 | ENM HOME DISTRIBUTION
WO-11262627 | 104040994 | 2023-09-15 11:32 | 2023-09-15 | Switch not working | 2023-09-15 10:04 | X1001WH_N | X1001WH_N | X1001WH_N |  | Name of Customer: Bhushan Sonar 2. Site Address: - Greens society 3. Name of contact person at site :- 4. Contact Phone / Mob. No: - 9766690909 5. Defective product details:- door bell switch 6. Product Make:- Opale 7. Nature of Defect: Switch not working 8. Shutdown availability if applicable :nil 9. Serial No: or DOM of - 10. Dealer Name /OA no. /Invoice Details: - 10 years warranty 11. Commissioned / Installed date:- NIL 12. Name & phone No: of person registering the complaint: Mr. Bhushan Sonar 9766690909 | 2023-09-15 | 2023-09-16 15:43 | No | Warranty | Sonar Bhushan | Bhushan Suresh Shiva laxmi Plot no13 3 | Nashik | 422010 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Kunal jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the Switch not working . we observed this Switch is working properly.switch found ok. on/off operation found ok. | Repair |  | 9- Service Validated | 2023-09-16 15:47 |  |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11263180 | 104042758 | 2023-09-15 11:34 | 2023-09-15 | Switch not operating | 2023-09-15 10:44 | X1001WH_N | X1001WH_N | X1001WH_N |  | Dear Team, Need to replace a few electrical opale switches - home appliances under the warranty policy. Kindly find the attached warranty invoice for reference (also attached snapshot, if attachment is not accessible) . Site Address, K702 - Nana Anada Gaikwad. Pudumjee G-Corp, Greens. K & L Building, Aditya Birla Hospital Marg, Thrgaon Phata, Chinchwad, Pune (Pin 411033). Mahesh Nana Gaikwad. 09403696341. | 2023-09-15 | 2023-09-16 15:49 | No | Warranty | Mahesh Nana Gaikwad | Pudumjee G-Corp Greens K & L Building Aditya Birla Hospital Marg Thrgaon Phata Chinchwad | Pune | 411033 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Kunal jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the switch found that the Switch is not working it's found broken from inside the board . so this problem is not repairable.So switch Needs to be replaced, Required Material : X1001WH - 01 nos. we arranged the material from our stock and replaced it. | Repair |  | 9- Service Validated | 2023-09-18 10:42 | =S= Consig Fill up 226061082 |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11264271 | 104042017 | 2023-09-15 15:28 | 2023-09-15 |  | 2023-09-15 11:07 | L5508D1A | L5508D1A | L5508D1A |  | nd the attached invoice copy for regarding complaint of C-Bus Dimmer (L5508D1A) kindly register the complain Site Address Mr Deepak Address- H N B-292 Paschim Vihar, New Delhi 110063 Cont Per - Mr Ravinder - 8802160388 | 2023-09-15 | 2023-09-16 18:11 | No | Warranty | Deepak Deepak | H N B-292 Paschim Vihar, | New Delhi | 110063 | Delhi | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Visited the site and as per customer schedule and confirmation we reach the site, but customer have no idea any dimmer complaint. We suggest to customer please available the material for testing then re- login the complaint. We close the complaint. | Repair |  | 8- Service Completed | 2023-09-16 18:13 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11265266 | 104065217 | 2023-09-16 15:55 | 2023-09-15 |  | 2023-09-15 17:41 | UNS32DP2M_GY | UNS32DP2M_GY | UNS32DP2M_GY |  | NISAR MANIKYAKUNNE ANNASSERY (PO) ANNASSERY KOZHIKODE - 673317 NISAR 9846768289 UNS32DP2M_GY : 2 PCS UNS61SW1M_GY : 3 PCS UNS6BPL1M_GY : 2 PCS Not working Yes Under Warranty Before Three Months LAN Marketing 8075581561 | 2023-09-15 | 2023-09-18 12:26 | No | Warranty | NISAR NISAR | MANIKYAKUNNE ANNASSERY (PO) ANNASSERY | KOZHIKODE | 673317 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found unica 32dp switch dolly struck issue UNS32DP2M_GY : 1nos replaced | Repair |  | 9- Service Validated | 2023-09-19 12:29 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11269376 | 104076896 | 2023-09-16 12:57 | 2023-09-16 |  | 2023-09-16 12:01 | UNS5STFAN2M_GY | UNS5STFAN2M_GY | UNS5STFAN2M_GY |  | Unicapure 5 Steps 360 Deg Fan Regulator, 2M UNS5STFAN2M_GY I look forward to your reply and a resolution to this problem Joby jose Chelangara house Vellangallur Pin 680662 Ph. 9895141857 | 2023-09-16 | 2023-09-20 17:10 | No | Warranty | Joby jose | Chelangara house | Vellangallur | 680662 | Kerala | India FS South2 ED&I CSP PrinterPeople Cochin | Renjith PR PrinterPeople Cochin | PRINTER PEOPLE-COCHIN | regulator send to location eng for onsite replacement. replacemnt will be scheduled on delivery and customer down time schedule | Repair |  | 8- Service Completed | 2023-09-20 17:12 |  |  | 55 | INR | 55 | ENM HOME DISTRIBUTION
WO-11269392 | 104076916 | 2023-09-21 16:08 | 2023-09-25 |  | 2023-09-16 12:56 | P1001_N | P1001_N | P1001_N | P1001 | AMBILIKUTTAN AADISSERIL KARUNAGAPPALLY 690519 AMBILIKUTTAN 9809787374, '9526082492 "SCHNEIDER LIVIA 1WAY SWITCH 10AMP WH (P1001)" 2 nos SCHNEIDER LIVIA 10/16A 3 PIN SOCKET(P2106) 2 nos not working hhys inframart Joseph ouseph 9526082492 | 2023-09-16 | 2023-09-30 09:07 | No | Warranty | AMBILIKUTTAN AMBILIKUTTAN | AADISSERIL KARUNAGAPPALLY | KARUNAGAPPALLY | 690519 | Kerala | India FS South2 ED&I CSP PrinterPeople Cochin | Renjith PR PrinterPeople Cochin | PRINTER PEOPLE-COCHIN | P1181 P2106 replaced | Repair |  | 8- Service Completed | 2023-09-30 14:08 |  |  | 140 | INR | 140 | ENM HOME DISTRIBUTION
WO-10992934 | 102507699 | 2023-07-14 09:38 | 2023-07-14 |  | 2023-07-14 09:27 | ATS480C59Y | ATS480C59Y | ATS480C59Y | 8822316AA232001 | Fuse Continuous blown issue for ATS480C59Y Dear Sir/Madam., Good Morning, Part Number - ATS480C59Y & Qty - 1 No. Serial Number - 8822316AA232001 Issue : Fuse continuously blown during start the Motor. 8 Nos same rating soft starter provided the same site and rest of the feeders working fine. Site Details : Sail, Bokaro Bokaro Steel City, Jharkhand, India - 827001. Contact details : Mr. Rakesh - 7856028890 / 9801615535 Because of Government site and critical operation kindly depute the service engineer to above mentioned site asap. | 2023-07-14 | 2023-09-02 14:52 | No | Warranty | Bokaro Steel Plant | DGM (C&IT), Bokaro Steel Plant Bokaro Steel City | Bokaro | 827001 | Jharkhand | India FS ED&I CSP East Team UNIVERSAL ELECTRIC POWER SOLUTION BHUBANESWAR | Banty Kumar_UNIVERSAL ELECTRIC POWER SOLUTION BHUBANESWAR | Universal Electric Power Solution(500012032) | material booked | Repair |  | 9- Service Validated | 2023-09-14 14:57 | =S= Free Order 225906641 |  | 182 | INR | 182 | Industrial Automation Ops
WO-11269416 | 104077015 | 2023-09-19 16:25 | 2023-09-16 |  | 2023-09-16 13:46 | A9N4P63C | A9N4P63C | A9N4P63C |  | Dear sir, I would like to inform you that we are facing problem 1 no. MCB. Which is one pole not working. So I request you to please resolve/ replace it on immediate basis. Also find the attached photo for your reference? Item detail: Item: MCB Rating: 63A, 10KA, 4P Make: SCHNEIDER Qty: 1 no. | 2023-09-16 | 2023-09-22 17:17 | No | Warranty | Ambit Switchgears | C - 50, Phase- II | Noida | 201305 | Uttar Pradesh | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mcb found phase missing, Hence faulty replaced. A9N4P63C - 1 nos Email : id not provided by customer | Repair |  | 8- Service Completed | 2023-09-22 17:19 |  |  | 65 | INR | 65 | ENM HOME DISTRIBUTION
WO-11275086 | 104083047 | 2023-09-18 10:34 | 2023-09-19 |  | 2023-09-18 09:54 | EZ9F76440 | EZ9F76440 | EZ9F76440 |  | easy 9 -EZ9F76440 1 no on off issue Purchased on 8 month back | 2023-09-18 | 2023-09-19 10:42 | No | Warranty | Hussain Hussain | near SR petrol pump , trajpar chakri | Morbi | 363642 | Gujarat | India FS ED&I CSP West Team JKS ENGINEERING CO Rajkot | Jayesh J_JKS Rajkot | JKS Engineering Co. | We visited at site check mcb on/off not working check mcb terminal and body side not any problem.ourobservation mcb side sticker open in side dusting clean dusting mcb on/off working ok. | Repair |  | 9- Service Validated | 2023-09-19 11:30 |  |  | 80 | INR | 80 | ENM HOME DISTRIBUTION
WO-11275100 | 104077836 | 2023-09-18 12:07 | 2023-09-18 |  | 2023-09-18 10:17 | UNS61SW1M_WE | UNS61SW1M_WE | UNS61SW1M_WE |  | Abdul salam Maata house Vadakkummuri house , oorngateeri , areekode Malappuram dt , pin : 673639 Kerala. Abdul salam 9,847,623,459 Unica pure switches Switches complaint yes Under Warranty 4 months Muhammed Ali - 8606739993 | 2023-09-18 | 2023-09-20 18:11 | No | Warranty | AbdulSalman Abdul | Veluvangadan house Vadakkumuri areekode | Malappuram | 673639 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found unica one way switch and 32dp switch contact issue unica 1way 1nos unica 32dp switch 1nos replaced | Repair |  | 9- Service Validated | 2023-09-20 18:14 |  |  | 45 | INR | 45 | ENM HOME DISTRIBUTION
WO-11276721 | 104081922 | 2023-09-18 11:47 | 2023-09-18 |  | 2023-09-18 11:09 | IN8401_16 | IN8401_16 | IN8401_16 |  | Subramanian Good Earth Melange-2B Menon Parambu Road,Changampuzha Nagar Edapally, Kochi-682024 Subbu 9945274374 IN8401-15 NOS Complaint 9008316501 | 2023-09-18 | 2023-09-21 09:37 | No | Warranty | Subramanian Subramanian | Good Earth Melange-2B Menon Parambu Road,Changampuzha Nagar Edapally | Kochi | 682024 | Kerala | India FS South2 ED&I CSP PrinterPeople Cochin | Renjith PrinterPeople Cochin | PRINTER PEOPLE-COCHIN | IN848/16 2 nos.. 2018 batch approved by se. onsite replacement re scheduled to 23/9/23 as per customer request | Repair |  | 9- Service Validated | 2023-09-21 16:42 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11276727 | 104077676 | 2023-09-18 12:53 | 2023-09-18 |  | 2023-09-18 11:15 | EZ9ETND04 | EZ9ETND04 | EZ9ETND04 |  | Shahzadha Hot View Sweets , The square Building ,Fort Road Kasaragod (P O ) Kasaragod Kasaragod , PIN : 671121 Shahzadha 7400337333 Easy9 DB DB IS NOT WORKING Under Warranty One month Mohammed Jebrood- 9743182896 | 2023-09-18 | 2023-09-19 21:32 | No | Warranty | Shahzadha Shahzadha | Hot View Sweets , The square Building ,Fort Road Kasaragod (P O ) Kasaragod | Kasaragod | 671121 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found Easy9 - TPN DB - double door ( EZ9ETND04) batch no.S-07/2021 base unit rust issue, this is not a product compalint customer fault. INFORM TO CUSTOMER | Repair |  | 9- Service Validated | 2023-09-19 21:41 |  |  | 180 | INR | 180 | ENM HOME DISTRIBUTION
WO-11279299 | 104094466 | 2023-09-19 15:12 | 2023-09-19 |  | 2023-09-19 09:50 | A9N4P63C | A9N4P63C | A9N4P63C |  | Dear sir My address is 397 L/A model town Parkash nagar road, jalandhar | 2023-09-19 | 2023-09-19 15:14 | No | Warranty | Bharat Bharat | 397 L/A model town Parkash nagar road | Jalandhar | 144003 |  | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | checked the isolator found phase missing. hence faulty, replaced. A9S4P063 - 1 Nos. Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-19 17:22 |  |  | 65 | INR | 65 | ENM HOME DISTRIBUTION
WO-11280370 | 104097690 | 2023-09-19 16:29 | 2023-09-19 |  | 2023-09-19 13:01 | UNS5STFAN2M_WE | UNS5STFAN2M_WE | UNS5STFAN2M_WE |  | DOP: 17/8/2022 UNS5STFAN2M_WE : 2 PCS UNS4STFAN1M_WE : 1 PCS P: Not working AHMED A C LULU BAKERY PAYYOLI ANGADI (PO) PAYYOLI ANGADI KOZHIKODE - 673523 AHMED A C 9946190001, 7519888887 | 2023-09-19 | 2023-09-20 15:46 | No | Warranty | AHMED A C | LULU BAKERY PAYYOLI ANGADI (PO) PAYYOLI ANGADI | KOZHIKODE | 673523 |  | India FS South2 ED&I CSP APSMarketingCompany Calicut | Rejilesh APSMarketingCompany Calicut | APS Marketing Company | visited this site found unica 5st fan regulator speed out of control UNS5STFAN2M_WE replaced problem solved | Repair |  | 9- Service Validated | 2023-09-20 15:52 | case registered in parent territory |  | 45 | INR | 45 | ENM HOME DISTRIBUTION
WO-11281003 | 104122096 | 2023-09-19 17:27 | 2023-09-19 |  | 2023-09-19 17:10 | P1002 | P1002 | P1002 |  | DOP: 10/12/2022 P1002 : 4 PCS P1001 : 3 PCS P1132 : 2 PCS P: Not working JITHIN POTHUVAL KANDI HOUSE OORATH (PO) OORATH, KUTTIADY KOZHIKODE - 673508 JITHIN 9605688686 | 2023-09-19 | 2023-09-22 17:26 | No | Warranty | Jithin Jithin | POTHUVAM KANDI HOUSE OORATH (PO) OORATH, KUTTIADY | Kozhikode | 673508 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found livia switchs contact issue and dolly crack P1001 2NOS P1132 1NOS P1001 17NOS P1002 10 nos replaced | Repair |  | 9- Service Validated | 2023-09-22 17:30 |  |  | 55 | INR | 55 | ENM HOME DISTRIBUTION
WO-11281024 | 104122973 | 2023-09-19 17:32 | 2023-09-19 |  | 2023-09-19 17:14 | EZ9EPVD08N | EZ9EPVD08N | EZ9EPVD08N |  | DOP: 1/9/2022 EZ9EPVD08N Qty : 1 PCS P: Db inner parts damage ANLARSHA K K KUTTIYIL ULLIYERI ULLIYERI (PO) KOZHIKODE - 673315 ANLARSHA K K 9846617266 | 2023-09-19 | 2023-09-21 21:15 | No | Warranty | ANLARSHA ANLARSHA | KUTTIYIL ULLIYERI ULLIYERI (PO) | Kozhikode | 673315 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found Vertical phase selector DB, Easy9 earth bar broken, earth bar replaced earthbar will be arranged by dealer | Repair |  | 9- Service Validated | 2023-09-21 21:16 |  |  | 40 | INR | 40 | ENM HOME DISTRIBUTION
WO-11281031 | 104123122 | 2023-09-19 17:38 | 2023-09-19 |  | 2023-09-19 17:18 | EZ9ETND04 | EZ9ETND04 | EZ9ETND04 |  | DOP: 24/7/2022 EZ9ETND04 Qty : 1 PCS P: Db Door Knob issue IQBAL PARAMBATH HOUSE PERAMBRA (PO) PERAMBRA KOZHIKODE - 673525 IQBAL 9846482005 | 2023-09-19 | 2023-09-21 11:54 | No | Warranty | IQBAL IQBAL | PARAMBATH HOUSE PERAMBRA (PO) PERAMBRA | Kozhikode | 673525 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found Easy9 - SPN DB - double door lock spring action missing replaced new lock problem solved. | Repair |  | 9- Service Validated | 2023-09-21 11:59 |  |  | 45 | INR | 45 | ENM HOME DISTRIBUTION
WO-11284039 | 104124672 | 2023-09-20 11:10 | 2023-09-20 | As per sr. no product in warranty raise ZVO for replacement. | 2023-09-20 10:46 | US15/6U000 | US15/6U000 | US15/6U000 |  | DOP: 24/7/2022 US15/6U000 QTY - 01 P: NOT WORKING PROPERLY (ON / OFF PROBLEM) M/S SHAH ELECTRIC CO. G-401 Cellestial Dreams Near Rajhans Zion Canal Road Vesu -Surat 9428148117 ASHIMA KEJARIWAL | 2023-09-20 | 2023-09-20 14:01 | No | Warranty | M/S SHAH ELECTRIC CO. | G-401 Cellestial Dreams Near Rajhans Zion Canal Road Vesu null | Surat | 395007 | Gujarat | India FS ED&I CSP West Team VARDHAMAN ELECTROSOFT Vadodara | MAHENDRA SINGH VARDHAMAN ELECTROSOFT Vadodara | VARDHAMAN ELECTROSOFT | we visited the site and check the product is physically ok. check the ultiimpress model G A switch out let ON/OFF operation issue. | Repair |  | 9- Service Validated | 2023-09-26 14:02 | 226057155 |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11284845 | 104144351 | 2023-09-20 12:14 | 2023-09-20 |  | 2023-09-20 10:58 | A9N4P63C | A9N4P63C | A9N4P63C |  | Product : A9KF71125 MCB Sr No. D2244 , DOM NOV 2022 Within Warranty Yes Phase Miss / Not Passing Current Mr Inder H. no. 1321,Gali no. 8 Hall Bazar Amritsar 143006 Mr Inder 9592901500 | 2023-09-20 | 2023-09-20 12:16 | No | Warranty | Inder Inder | H. no. 1321, Gali no. 8 Hall Bazar | Amritsar | 143001 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the MCB found Phase Missing / Not Passing Current and Isolator found not giving output and phase phase missing problem and fan regulator found speed variation issue and switch found stuck of issue and socket switch found burnt & melt. Hence faulty replaced. A9N1P25C - 1 Nos. EZ9S66263 - 4 Nos. IN84SFR - 2 Nos. IN8486/32 - 2 Nos. IN8426/16 - 2 Nos. email : id not provided by the customer. | Repair |  | 8- Service Completed | 2023-09-20 17:29 |  |  | 151 | INR | 151 | ENM HOME DISTRIBUTION
WO-11285084 | 104144750 | 2023-09-20 15:18 | 2023-09-20 | We found the meter booting up, not turning to ON mode. suspecting firmware related things | 2023-09-20 12:24 | EM7230 | EM7230 | EM7230 |  | DOP: 18/4/2023 EM7230 Qty:1 P: DISPLAY NOT WORKING (the controller power on off position display shows only schneider logo forther no action) Vasista Marines customer no ;-9966532578 Address ;- kodavalli,Palakoderu Mandal,near Bhimavaram West Godavari district ,534210 | 2023-09-20 | 2023-09-26 08:44 | No | Warranty | Vasista Marines Vasista Marines | kodavalli Palakoderu Mandal near Bhimavaram | West Godavari | 534210 | Andhra Pradesh | India FS ED&I CSP South Team ENERPRO ENGINEERING SOLUTIONS Vijayawada | SK SIRAJUDDIN_ENERPRO ENGINEERING SOLUTIONS VIJAYAWADA | Enerpro Engineering Solutions - 500012682 | METER NOT WORKING | Repair |  | 8- Service Completed | 2023-09-27 08:47 |  |  | 134 | INR | 134 | ENM HOME DISTRIBUTION
WO-11285409 | 104144418 | 2023-09-20 15:26 | 2023-09-20 |  | 2023-09-20 13:46 | IN8401_16_SP | IN8401_16_SP | IN8401_16_SP |  | DOP: 6/6/2022 Zencelo sqitches P: Not Working Zainudheen ck Pakadapuraya house Vengara Malappuram dt , pin : 676304 Kerala. Zainudheen ck 9746354238 | 2023-09-20 | 2023-09-23 16:49 | No | Warranty | Zainudheen Zainudheen | Pakadapuraya house Vengara | Malappuram | 676304 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found zencelo switchs struck issue IN8401 REPLACED 2NOS | Repair |  | 9- Service Validated | 2023-09-23 16:54 |  |  | 45 | INR | 45 | ENM HOME DISTRIBUTION
WO-11285418 | 104144822 | 2023-09-20 15:25 | 2023-09-20 |  | 2023-09-20 13:52 | UNS5STFAN2M_WE | UNS5STFAN2M_WE | UNS5STFAN2M_WE |  | DOP: 26/7/2023 Unica Pure 5 Steps 360 degree Fan regulator P: Customer is facing issues with Unica Pure 6ax 1WAY SWITCH Reena Indah Desa Seva up school kottichal road ,Kannadiparamba (p o )Kannadiparamba ,pincode -670604 Kannur Reena 8547396676 | 2023-09-20 | 2023-09-22 14:19 | No | Warranty | Reena Reena | Indah Desa Seva up school kottichal road ,Kannadiparamba (p o )Kannadiparamba | Kannur | 670604 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found unica 5st fan regulator knob broken unica 5st fan replaced problem solved | Repair |  | 9- Service Validated | 2023-09-22 14:26 |  |  | 100 | INR | 100 | ENM HOME DISTRIBUTION
WO-11285422 | 104150043 | 2023-09-20 15:17 | 2023-09-20 | Validated By Prashant | 2023-09-20 13:55 | IN8401_N | IN8401_N | IN8401_N |  | Zencelo switch not working purchased on June 2023 from Ashna Electrical mumbai | 2023-09-20 | 2023-09-21 10:39 | No | Warranty | ROMIL K | 502, rudra hights sarojini road vilay parle west | Mumbai | 400056 | Maharashtra | India FS ED&I CSP West Team S K SERVICES Mumbai | Ganesh Tati_S K SERVICES Mumbai | S.K. Services (10237) | We visited the site Product Ref - IN8401(BZ)-2Nos Serial No:-23193,23192 We check the product 6A 1Way switch is properly not operating The 1Nos is stuck issue and another 1Nos is Locking issue We replace the both switch and solve the problem. | Repair |  | 9- Service Validated | 2023-09-25 10:43 | =S= Consig Fill up 226068239 |  | 20 | INR | 20 | ENM HOME DISTRIBUTION
WO-11285425 | 104145331 | 2023-09-20 14:45 | 2023-09-20 |  | 2023-09-20 13:57 | A9N4P63C | A9N4P63C | A9N4P63C |  | DOP: 19/7/2023 A9N4P63C Qty:1 P: Dolly free NIDHI CONTROLS, NO. 14, FIRST FLOOR, SIR M VISHWESHWARAIAH LAYOUT, AVALAHALLI VILLAGE, UTTARAHALLI HOBLI, ANJANAPURA POST, BANGALORE - 560062. Contact No : 9845824770. | 2023-09-20 | 2023-09-21 09:41 | No | Warranty | NIDHI CONTROLS | NIDHI CONTROLS No.14, 1st floor, Sir M. Vishweshwaraiah industrial Layout, Avalahalli Village, Uttarahalli Hobli, Anjanapura Post, - . | Bangalore | 560062 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Nagaraja G_P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | Inspected and found below mentioned 1)Ref: A9N4P63C S/N:D2328 = 01 No, MCB dolly free issue. Hence we will give same new MCB warranty replacement. So we have replaced new one MCB from our PSK stock. | Repair |  | 9- Service Validated | 2023-09-21 09:42 |  |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-11285930 | 104127215 | 2023-09-22 14:44 | 2023-09-20 |  | 2023-09-20 16:06 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | DOP: 6/5/2023 IH14000100 4 Channel Relay IH12001010 Dimmer + Fan Control IH11000200 Curtain Controller IH101ZWIFI Automation Gateway IH100WFVDP Smart Doorbell P: Installation Le Meridien Coimbatore 762 Avinashi Rd Cexus Nagar Neelambur Tamil Nadu 641062 Vishwajeet Singh Sengar 9453005292 | 2023-09-20 | 2023-09-22 18:27 | No | Commercial Action - Sales | Vishwajeet Singh Sengar | Le Meridien Coimbatore 762 Avinashi Rd Cexus Nagar Neelambur | Coimbatore | 641062 | Tamil Nadu | India FS South2 ED&I CSP GRControlSystems Coimbatore | Mani kandan GRControlSystems Coimbatore | GR Control Systems-Coimbatore | IH14000100 4 Channel Relay - 1No IH12001010 Dimmer + Fan Control - 1No IH11000200 Curtain Controller - 1No IH101ZWIFI Automation Gateway - 1No IH100WFVDP Smart Doorbell - 1No Installation done | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-22 18:32 |  |  | 24 | INR | 24 | ENM HOME DISTRIBUTION
WO-11285956 | 104152627 | 2023-09-21 11:50 | 2023-09-20 |  | 2023-09-20 16:21 | P1086_DG | P1086_DG | P1086_DG |  | DOP: 16/6/2022 P1086 : 3 PCS P2005 : 3 PCS P2106 : 1 PCS P2010 : 4 PCS P1001 : 11 PCS P1002 : 6 PCS P5001 : 7 PCS P1132 : 6 PCS P: Not Working ABDULLA INDORA ASSOCIATES KALLACHI (PO) KALLACHI, NADAPURAM KOZHIKODE - 673506 ABDULLA 8086456098 | 2023-09-20 | 2023-09-25 16:16 | No | Warranty | Mr ABDULLA | 19/440A-A13, PUNATHUMMAL COMPLEX KALLACHI NADAPURAM CLICUT - | Kozhikode | 673506 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found livia switchs dolly crack and struck issue P2106 : 1 PCS P1001 : 11 PCS P1002 : 6 PCS P5001 : 1 PCS P1132 : 5 PCS replaced problem solved | Repair |  | 9- Service Validated | 2023-09-25 16:27 |  |  | 65 | INR | 65 | ENM HOME DISTRIBUTION
WO-11285970 | 104154744 | 2023-09-20 17:41 | 2023-09-20 |  | 2023-09-20 16:27 | A9KF71463 | A9KF71463 | A9KF71463 |  | 1)EZC250H4125 : 125A 4P MCCB : 25KA: 1 NO : Spreader didn't tighten to this mccb. SL NO : 60947-2 ,JIS C8201-2- 2) MCB : 63A 4P MCB : A9KF71463 : 2 NO : TRIPPING SL NO : DD-2023-W20-4-4 SL NO : DD-2023-W21-7-5 3) MCB : 16A 2P MCB: A9KF71216 : 2 NOS : TRIPPING SL NO : DD-2023-W20-5-8 SL NO : DD-2023-W09-4-2 4) MCB : 32A 2P MCB ; A9KF71232 1 NO : SCREW DOESN'T TIGHT SL NO: DD-2023-W12-2-11 5) MCB 40A 2P MCB : A9KF71240 : 1 NO : TRIPPING SL NO : DD-2023-W18-3-8 6) 32A 4P MCB : A9KF71432 : 1 NO : TRIPPING DD-2023-W19-5-8 7)10A SP MCB: A9KF71110 : 1 NO : TRIPPING DD-2023-W07-2-2 8) OLR LRE21:1 NO : Not working in condition SL NO : 8C 23086 9) SHUNT : EZESHT200AC :1 NO : Not working in condition SL NO : 8ADL-2022-W49-3 Check invoice at site Karavali Switchgears C-42 Industrial Estate Baikampady Mangalore-575011 Prathiksha 7892528314 | 2023-09-20 | 2023-09-25 16:03 | No | Warranty | Karaavali Switchgears | C42, Industrial Estate, Baikampady, | Mangalore | 575011 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | MANOJ GANESAN SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | - EZC250H4125 -Spreader didn't tighten to this mccb. - A9KF71110- revet came out from the mcb. - LRE21- stop button not working - EZESHT200AC -Not working - XB5AW33G1N - 10nos while unboxing found integral led not available in the push button. So we had arranged for the replacement and sent thru courier. Replacement done by alpha electricals. - A9KF71463- 2nos- found dolly free we rectified the same and found working ok - A9KF71232- found working ok - A9KF71240- found working ok - A9KF71432- found working ok | Repair |  | 9- Service Validated | 2023-09-25 22:37 |  |  | 250 | INR | 250 | ENM HOME DISTRIBUTION
WO-11285994 | 104152485 | 2023-09-20 17:43 | 2023-09-20 |  | 2023-09-20 16:40 | A9KR11463 | A9KR11463 | A9KR11463 |  | RCCB : 63A 4P 30MA :A9KR11463 : 1 NO: TRIPPING SL NO : DD-2023-W26-2-1 RCCB : 40A 2P 30MA : A9KR11240 : 1 NO : 1 POLE NOT WORKING DD-2022-W05-7-2 Plant-Tech Industrial Services Ltd Plot No- 245, Baikampady New Mangalore State Name : Karnataka, Code : 29 : 575011 Prathiksha 7892528314 | 2023-09-20 | 2023-09-25 16:06 | No | Warranty | Plant-Tech Industrial Services Ltd | Plot No- 245, Baikampady null | Mangalore | 575011 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | MANOJ GANESAN SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | we had requested to send defective to our office, after checking the problem found was rccb not getting ON intermittently. so we had arranged for the replacement. replacement done by alpha electricals. | Repair |  | 9- Service Validated | 2023-09-25 21:00 |  |  | 250 | INR | 250 | ENM HOME DISTRIBUTION
WO-11289200 | 104154992 | 2023-09-21 12:12 | 2023-09-21 | Fan Regulator not working | 2023-09-21 09:54 | IN84SFR_N | IN84SFR_N | IN84SFR_N |  | 1. Name of Customer =gautam jethwani 2. Site Address: = Gautam Jethwani satyam shivam society B-2 Building Flat no 605 NEAR hOTEL RAJWADA SOMESHWARWADI PASHAN PUNE 411008 3. Name of contact person at site := GAUTAM SIR 4. Contact Phone / Mob. No: = 9822095914 | 2023-09-21 | 2023-09-22 11:45 | No | Warranty | Gautam Jethwani | B-2 Building Flat no 605 NEAR hOTEL RAJWADA SOMESHWARWADI PASHAN | Pune | 411008 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Swamesh S_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the Fan Regulator not working in all steps, so we removed regulator observed capacitor found burn. that's why Fan Regulator not working. as per serial number this product is out of warranty. so we reject the warranty of product. | Repair |  | 9- Service Validated | 2023-09-22 11:59 |  |  | 45 | INR | 45 | ENM HOME DISTRIBUTION
WO-11289218 | 104174103 | 2023-09-21 12:54 | 2023-09-21 |  | 2023-09-21 10:12 | A9KF71463 | A9KF71463 | A9KF71463 |  | Product A9KF71463, 4 pole 63 Amps MCB Sr No. D 2148, DD2021-W48-3-3 DoM Dec 2021 MCB - Not Working Not Passing Current Product is in Warranty Please replace No. 2016, Rakhrajpur Bari Brahmana, Jammu PIN 181133 Jammu and Kashmir J&K Mr Ramesh 8899162899 | 2023-09-21 | 2023-09-21 12:57 | No | Warranty | Ramesh Kumar | No. 2016 Rakhrajpur Baribrahmna | Jammu | 180010 | Jammu and Kashmir | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Ram Ashish Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the Not Working Not Passing Current due to phase missing and contactor found not giving output. Hence faulty replaced. A9N4P63C - 1 Nos. LC1D80AM7 - 1 Nos. email : id not provided by the customer. | Repair |  | 8- Service Completed | 2023-09-21 14:17 |  |  | 355 | INR | 355 | ENM HOME DISTRIBUTION
WO-11289829 | 104174503 | 2023-09-21 17:27 | 2023-09-21 |  | 2023-09-21 10:41 | CPX4STFAN1M_WE | CPX4STFAN1M_WE | CPX4STFAN1M_WE |  | CUSTOMER REQUESTCustomer Request is visible on the customer portal, ensure clarity Livia 4 step regulator not working Purchased in the month , | 2023-09-21 | 2023-09-25 16:24 | No | Warranty | Ankur bardia | tower B , Flat 1204 , EMAR , emerald estate sector 65 , | Gurgaon | 122018 | Haryana | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the fan regulator and found fan regulator have output issue, We replace the faulty fan regulator with new. | Repair |  | 8- Service Completed | 2023-09-25 17:49 |  |  | 56 | INR | 56 | ENM HOME DISTRIBUTION
WO-11290466 | 104177694 | 2023-09-21 16:25 | 2023-09-21 |  | 2023-09-21 14:40 | A9N3P10C | A9N3P10C | A9N3P10C |  | M/S Maa Vaishno Engineering Vill. Khambi, Tehsil- hodal,palwal, Faridabad Mr. Tekchand 9988825190 Product : A9N3P10C , LC1E2510M7 Serial no.: DD-2023-W23-1 , 1021463 Phase missing / No output | 2023-09-21 | 2023-09-25 14:54 | No | Warranty | Maa Vaishno Engineering | Vill. Khambi, Tehsil- hodal,palwal, null | Faridabad | 121004 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mcb and contactor found phase missing, Hence faulty need replacement. A9N3P10C - 1 nos LC1E2510M7 - 1 nos Email : | Repair |  | 8- Service Completed | 2023-09-26 14:56 |  |  | 52 | INR | 52 | ENM HOME DISTRIBUTION
WO-11290496 | 104177643 | 2023-09-22 12:08 | 2023-09-21 |  | 2023-09-21 14:45 | A9N16258 | A9N16258 | A9N16258 |  | Ahluwalia Contract India Ltd Puri The Aravallis Sec-61, Nr Ullawas Village Gurgaon Mr.Shailendra 9716444759 Product : A9N16258 Serial Number : DD-2021-W45-5-1 | 2023-09-21 | 2023-09-22 12:15 | No | Warranty | Aluwalia Contract India Ltd | Puri The Aravallis Sec-61, Nr Ullawas Village | Gurgaon | 122011 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Delhi | Kamal Kumar_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the Rccb found working ok. Email : id not provided by customer . | Repair |  | 8- Service Completed | 2023-09-22 14:39 |  |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11290500 | 104182049 | 2023-09-22 16:16 | 2023-09-21 |  | 2023-09-21 14:48 | A9N4P63C | A9N4P63C | A9N4P63C |  | CUSTOMER REQUESTCustomer Request is visible on the customer portal, ensure clarity 4 pole 63 amps MCB not working supply last month only | 2023-09-21 | 2023-09-22 16:19 | No | Warranty | Shiva Electrical & Hardware Store | Bawana Pooth Khrud, Near Valmiki Hospital, Vijay market | Bawana | 110039 | Delhi | India FS ED&I CSP North Team Sharma Electric Works Delhi | Pradeep Sharma_Sharma Electric Delhi | Sharma Electric Works (16295) | Checked the mcb found not giving output, Hence faulty replaced. A9N4P63C - 1 nos Email : id not provided by customer | Repair |  | 8- Service Completed | 2023-09-22 17:22 |  |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11293845 | 104204623 | 2023-09-22 11:33 | 2023-09-22 |  | 2023-09-22 09:38 | IN8401_16_SP | IN8401_16_SP | IN8401_16_SP |  | DOP: 23/12/2022 IN8401(BZ) Qty? 10 Nos Approx. P: Not Working 13 Basant Bahar 3 Opp. Kabir Enclave Ghuma Bopal ? 380058 Ahmedabad Contact No. 7600031760 Name. Kushan Shah | 2023-09-22 | 2023-09-25 16:45 | No | Warranty | Kushan Shah | 13 Basant Bahar 3, Opp. Kabir Enclave, Ghuma, Bopal | Ahmedabad | 380058 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Mistri Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physically obsrved ok. in8402(bz) install properly and working ok. so close t he case. | Repair |  | 8- Service Completed | 2023-09-25 16:45 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11293857 | 104184913 | 2023-09-22 14:19 | 2023-09-22 |  | 2023-09-22 09:44 | IH101ZW2IR | IH101ZW2IR | IH101ZW2IR |  | Dear sir , Please arrange to issue work order for following Mr. PK Khare, 602, Mecon Apartment , C-58/10, Sector 62,NOIDA-201301 Phone: 9717429134 Thanks and regards, sk jain | 2023-09-22 | 2023-09-23 03:04 | No | Warranty | PK Khare | 602, Mecon Apartment , C-58/10, Sector 62, | Noida | 201301 | Uttar Pradesh | India FS ED&I CSP North Team Seamtek International Pvt. Ltd. GHAZIABAD | Satish Raika Seamtek International Pvt. Ltd. GHAZIABAD | Seamtek International Pvt. Ltd. | following wiser components has been installed ssmart doorbell: 1 qty | Repair |  | 8- Service Completed | 2023-09-23 03:04 |  |  | 0 | INR | 0 | ENM HOME DISTRIBUTION
WO-11293923 | 104186576 | 2023-09-23 10:05 | 2023-09-22 |  | 2023-09-22 10:25 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Please raise the wiser installation call for below customer QDB Amaranthine, Chitrapuri colony high tower rd, Opp to Chitrapuri MIG building, Manikonda Jagir, Telangana- 500089. Contact person : Mr. Lakahan/Lucky ? +91 90599 00599 | 2023-09-22 | 2023-09-23 10:13 | No | Commercial Action - Sales | QDB Amaranthine, | hitrapuri colony high tower rd,Opp to Chitrapuri MIG building, null | Manikonda Jagir | 500089 | Telangana | India FS ED&I CSP South Team Master Electrical Solutions Hyderabad | DEBANGSHU BOSE Master Electrical Solutions SECUNDERABAD | Master Electrical Solutions | visited the site and carried out out following job.as per our discussion customer said they have all the required material for installation.so we went and there is nothing is ready to installation. And customer don't know how many material are to be install.so we have waited almost 1.5 hours and after all the things are available then we installed the relay . | Commissioning & Installation | Start-up | 8- Service Completed | 2023-09-23 10:19 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11293938 | 104185330 | 2023-09-23 11:59 | 2023-09-22 | Switches not operating | 2023-09-22 10:30 | IN8401_16_SP | IN8401_16_SP | IN8401_16_SP |  | DOP: 21-06-2022 IN8401 Qty=3 NOS P: Not Working Pratik electricals shop no 1 gajnayan building sominath nagar nr. somnath mandir vadgaon sheri pune 411014 Pratik 9822052150/ 8983052150 | 2023-09-22 | 2023-09-23 12:54 | No | Warranty | pratik electricals | Suprabhat Society Road No 2 Vadagaon Sheri | Pune | 411014 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Kunal jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the Switches not working. it;s found stuck not changing contact. switches stuck again & again. this problem is not repairable. So Switches needs to be replaced. Required Material : IN8401- 03 nos | Repair |  | 9- Service Validated | 2023-09-25 12:14 |  |  | 20 | INR | 20 | ENM HOME DISTRIBUTION
WO-11294131 | 104186095 | 2023-09-22 16:38 | 2023-09-22 | DP switch is not working & fan Regulator problem | 2023-09-22 10:34 | UNS32DP2M_WE | UNS32DP2M_WE | UNS32DP2M_WE |  | REPLACMENT Dear Sir 1. Name of Customer =NEW INDIA CABLES TRADING PVT LTD 2. Site Address: = NEW INDIA CABLES TRADING PVT LTD 741/2 BUDHWAR PETH PUNE 411002 3. Name of contact person at site := DASTGIR 4. Contact Phone / Mob. No: = 9823637253 5. Defective product details:- UNS32DP2M-WE =1 NOS 21-06-2022 X 3200 WH =3 NOS 1-08-2022 6. Product Make:-Schneider Electric 7. Nature of Defect: = NOT WORKING 8. Shutdown availability if applicable :nil 9. Serial No: or DOM of the product = UNS32DP2M-WE =1 NOS 21-06-2022 X 3200 WH =3 NOS 1-08-2022 ? | 2023-09-22 | 2023-09-22 16:42 | No | Warranty | New India Cables Trading Pvt Ltd | 741/2, shop no.6, near Kasardevi Temple, Tapkir Galli, | Pune | 411011 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Swamesh S_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked DP switch is not working & fan Regulator problem. this contact strip observed removed condition. customer not accepted this material. and fan regulator is not working 1 & 2 step. So it's needs to be replaced. Required Material : UNS32DP2M_WE - 01 nos, X3200 - 01 nos | Repair |  | 9- Service Validated | 2023-09-23 11:26 | =S= Consig Fill up 226071077 |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11294319 | 104205519 | 2023-09-22 12:25 | 2023-09-22 |  | 2023-09-22 10:37 | A9N4P63C | A9N4P63C | A9N4P63C |  | A9N4P63C 63Amps MCB Sr No. D2142 ( Nov 2021 ) Phase Not passing / Pole open MES, ( Military Engineering services) MAMUNN CANTT,INDUSTRIAL GROWTH CENTER, PATHANKOT, Punjab. 145001 Mr. SANJAY PANDEY 9417877008 spcontractor24@gmail.com | 2023-09-22 | 2023-09-22 13:45 | No | Warranty | MES, ( Military Engineering services) | MAMUNN CANTT, INDUSTRIAL GROWTH CENTER | PATHANKOT | 145001 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the mcb found phase missing and power supply found not power up and extended rotary handle found mechanism not working so mccb nut on / off due to rotary handle faulty. Hence faulty replaced. A9N4P63C - 1 Nos. LV432598 - 1 Nos. ABL2REM24100K - 1 Nos. email : spcontractor24@gmail.com | Repair |  | 8- Service Completed | 2023-09-22 15:33 |  |  | 175 | INR | 175 | ENM HOME DISTRIBUTION
WO-11294526 | 104205580 | 2023-09-22 11:23 | 2023-09-22 |  | 2023-09-22 10:41 | E8334L1_DG_G8 | E8334L1_DG_G8 | E8334L1_DG_G8 |  | DOP: 25/4/2023 E8334L1_DG_G8 E8315_6_DG E8333L1_DG_G8 P: Not Working Ar. Shahbas Ahamed "Sidra House" Behind Star Care Hospital, Nr. Chunas Club, Thondayad , Calicut - 673016 Ar. Shahbas Ahamed 9972123629 | 2023-09-22 | 2023-09-28 13:35 | No | Warranty | Shahbas Ahamed Shahbas Ahamed | "Sidra House" Behind Star Care Hospital, Nr. Chunas Club, Thondayad , Calicut | Kozhikode | 673016 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found avator on socket action missing and not working E8315_16_DG 1NOS E8315_6_DG 5NOS replaced, sockets working fine | Repair |  | 8- Service Completed | 2023-09-28 13:39 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11295171 | 104203250 | 2023-09-22 14:17 | 2023-09-22 |  | 2023-09-22 11:20 | EZ9EPS63S | EZ9EPS63S | EZ9EPS63S |  | Nedumkundan house Thrikkalangode post , karakkunnu , manjeri Malappuram dt. Pin : 676123 Kerala. Shanavas nk 9,895,315,348 Easy9 63 a rotary switches (EZ9EPS63S) Rotary complaint Yes Under Warranty 6 months | 2023-09-22 | 2023-09-29 17:10 | No | Warranty | ShanavasS Shanavas | Nedimkundan house Thrikkalangode post , karakkunnu , manjeri | Malappuram | 676123 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Rejilesh APSMarketingCompany Calicut | APS Marketing Company | visit this site found Easy9 - 40A pre-assembled selector switch , blue phase short EZ9EPS40S replaced problem solved | Repair |  | 8- Service Completed | 2023-09-29 17:18 |  |  | 55 | INR | 55 | ENM HOME DISTRIBUTION
WO-11295211 | 104206785 | 2023-09-25 11:18 | 2023-09-22 |  | 2023-09-22 11:37 | UNS5STFAN2M_WE | UNS5STFAN2M_WE | UNS5STFAN2M_WE |  | DOP: 23/2/2022 UNS32BP2M Qty: 1 P: Not Working Kindly check invoice at site | 2023-09-22 | 2023-09-25 12:11 | No | Warranty | Kush Kush | House 3 Contactors Area Rd 3 Bistupur | Jamshedpur | 831001 | Jharkhand | India FS ED&I CSP East Team UNIVERSAL ELECTRIC POWER SOLUTION BHUBANESWAR | Banty Kumar_UNIVERSAL ELECTRIC POWER SOLUTION BHUBANESWAR | Universal Electric Power Solution(500012032) | material to be booked | Repair |  | 8- Service Completed | 2023-09-28 12:15 |  |  | 14 | INR | 14 | ENM HOME DISTRIBUTION
WO-11295260 | 104207333 | 2023-09-22 13:27 | 2023-09-22 | NA | 2023-09-22 11:58 | E8331FR350_WD_G8 | E8331FR350_WD_G8 | E8331FR350_WD_G8 |  | E8331FR350_WD_G8 not working CJ 33 , 1st Floor , salt lake city Sector 2 opposite tank no 9 Kolkata 700091 West Benga Purchased details - EA Sales - 22nd feb 2023 | 2023-09-22 | 2023-09-26 13:45 | No | Warranty | Nikuj Jhunjhunwala | CJ 33 , 1st Floor , salt lake city Sector 2 opposite tank no 9 | Kolkata | 700091 | West Bengal | India FS ED&I CSP East Team B.D Electroservices Kolkata | KOUSHIK MONDAL_B.D Electroservices Kolkata | B.D Electroservices(500017330) | On received of ZVO material will delivered to customer. | Repair |  | 8- Service Completed | 2023-09-26 17:48 |  |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-11309302 | 104267742 | 2023-09-26 14:44 | 2023-09-26 |  | 2023-09-26 10:44 | UNS32DP2M_GY | UNS32DP2M_GY | UNS32DP2M_GY |  | 6 0CT 2022 Perfect homes creation PVT LTD Model unica 20mpr Adress 474 Sector 4, Urban estat Gurgoun 122001 Haryana 9999996776 Gagan | 2023-09-26 | 2023-09-28 16:24 | No | Warranty | Gagan Gagan | 474 Sector 4, Urban estat | Gurgaon | 122001 | Haryana | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the switch and found found switch have dolly free issue. We replace the faulty switch with new. | Repair |  | 8- Service Completed | 2023-09-28 16:28 |  |  | 1 | INR | 1 | ENM HOME DISTRIBUTION
WO-11310426 | 104270201 | 2023-09-27 13:30 | 2023-09-26 |  | 2023-09-26 12:44 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | IH100WFVDPNot working Kumra electric work 1 month back Installation was done on 23 aug Regd mobile no 9878100060 Kindly raise a visit request | 2023-09-26 | 2023-09-27 13:33 | No | Warranty | Varun Arora | 95 tagore nagar opp shehnai palace | Jalandhar | 144001 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | checked the vdp found gateway offline due to customer changed the password. Set right the same, now working ok. Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-27 13:35 |  |  | 65 | INR | 65 | ENM HOME DISTRIBUTION
WO-11310888 | 104276792 | 2023-09-29 13:09 | 2023-09-26 |  | 2023-09-26 15:28 | EZ9F76340 | EZ9F76340 | EZ9F76340 |  | Superlac Paints Pvt Ltd Plot No.99 & 100 B.S Road Industrial Area Ghaziabad - 201001 Contact Person : Mr.Tribhuvan Singh Mob - 9971225751 EZ9F76340---not working inv attached | 2023-09-26 | 2023-09-29 13:11 | No | Warranty | Superlac Paints Pvt Ltd | Plot No.99 & 100 B.S Road Industrial Area null | Ghaziabad | 201001 | Uttar Pradesh | India FS ED&I CSP North Team Sharma Electric Works Delhi | Ravinder Singh_Sharma Electric Delhi | Sharma Electric Works (16295) | checked the mcb found ok. Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-29 13:14 |  |  | 52 | INR | 52 | ENM HOME DISTRIBUTION
WO-11310976 | 104275626 | 2023-09-26 16:44 | 2023-09-26 |  | 2023-09-26 15:56 | P2005_N | P2005_N | P2005_N |  | 10A 3 PIN SOCKET Dear sir/mam I would like to inform you that, regarding 1nos.Socket 10A 3 pin with shutter Model no-P2005N not properly working. ADDRESS-FLAT NO- B6-401 UNINAV BLISS,RAJ NAGAR EXTENSION,GHAZIABAD UTTAR PRADESH 201017 Thanks & Regards Rakesh Yadav Mob.no.9450964662 | 2023-09-26 | 2023-09-28 16:35 | No | Warranty | Rakesh Yadav | FLAT NO- B6-401 UNINAV BLISS,RAJ NAGAR EXTENSION,GHAZIABAD UTTAR PRADESH 201017 null | GHAZIABAD | 201017 | Uttar Pradesh | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the socket and found socket have output issue. We replace the faulty socket with new. Mail id. rakeshy527@gmail.com | Repair |  | 8- Service Completed | 2023-09-28 16:38 |  |  | 22 | INR | 22 | ENM HOME DISTRIBUTION
WO-11310985 | 104277604 | 2023-09-26 16:42 | 2023-09-26 |  | 2023-09-26 15:59 | A9N3P63C | A9N3P63C | A9N3P63C |  | MCB 3POL Invoice Details Radhika Electricals July 2023 XC60C63A Mod JY63C D2022 KR Foods Ltd. B-16 Bulandshar road, Gaziabad 201009 Balram Singh 8285173417 | 2023-09-26 | 2023-09-28 17:26 | No | Warranty | KR Foods Ltd. | B-16 Bulandshar road null | GHAZIABAD | 201009 | Uttar Pradesh | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the MCB and found MCB have dolly free issue. Remove the side sticker and clean with air. And check the again MCB working is ok. Now resolve the issue. Mail Id. instt.balramsingh@gmail.com | Repair |  | 8- Service Completed | 2023-09-28 17:32 |  |  | 24 | INR | 24 | ENM HOME DISTRIBUTION
WO-11311030 | 104274426 | 2023-09-28 12:43 | 2023-09-26 |  | 2023-09-26 16:16 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Wiser smart door bell not working: Mr. Rajiv Yadav, Shushma Urban Views, zirakpur Wiser Smart Door Bell installed at customer residence is not working properly. He is getting error message while re installing the software. Please arrange a technician visit at site today 26 sept 2023 if possible or tomorrow positively I.e. 27 sept 2023. The details of customer and copy of bill is attached below 1. Customer Name : Rajiv Yadav 2. Customer Address : G802, Shushma Urban Views, Shushma Square, Old Ambala Road, Village Gazipur, Dhakauli, SAS Nagar Mohali, 160104 3. Installation Type : NEW 4. Product : Smart Door Bell 5. Contact Number : +91 +91 88222 22224 6. Email Id: rajiv111111@aol.com | 2023-09-26 | 2023-09-28 12:48 | No | Warranty | Rajiv Yadav | G802, Shushma Urban Views, Shushma Square, Old Ambala Road, Village Gazipur, Dhakauli, | Mohali | 160104 | Punjab | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Ram Ashish Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the vedio door bell found working ok. email : id not provided by the customer. | Repair |  | 8- Service Completed | 2023-09-28 13:00 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11311074 | 104279177 | 2023-09-27 13:04 | 2023-09-26 |  | 2023-09-26 16:37 | X1001WH_N | X1001WH_N | X1001WH_N |  | Fw: PROBLEM- ON/OFF ISSUE MODEL - X1001WH SERIAL NO. - 23121L PROBLEM- ON/OFF ISSUE I HAVE MY COMPLAIN BOOKED ON DATED.15.09.23 BUT NOT ANY ACTION IN MY COMPLAIN & NOT SOLVE THE PROBLEM AS ON DATE, SO RESOLVE THE ISSUE AS SOON AS POSSIBLE COUSTMER NAME - DARSHI RASTOGI CONTACT PERSON - DARSHI RASTOGI CONTACT NO. - 9984094777 ADDRESS - 3/110 A, VISHNUPURI, KANPUR 208002 | 2023-09-26 | 2023-09-27 15:24 | No | Warranty | Darshil Rastogi | 3/110, A Vishnupuri , | Kanpur | 208002 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Aman Khare_Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found switches having wiring issue. now working fine. | Repair |  | 8- Service Completed | 2023-09-27 15:27 |  |  | 115 | INR | 115 | ENM HOME DISTRIBUTION
WO-11314520 | 104290626 | 2023-09-27 11:10 | 2023-09-27 | Switch not working | 2023-09-27 09:28 | X1001WH_N | X1001WH_N | X1001WH_N |  | Dear Sir, Pl issue complaint no. 1. Name of Customer: chandan munot 2. Site Address: - L-1002 greens society thergaon 411033 3. Name of contact person at site :- 4. Contact Phone / Mob. No: - 98810 66975 5. Defective product details:-X1001WH 6. Product Make:- Opale 7. Nature of Defect: switch not working 8. Shutdown availability if applicable :nil 9. Serial No: or DOM of -14096 10. Dealer Name /OA no. /Invoice Details: - 10 years warranty 11. Commissioned / Installed date:- NIL 12. Name & phone No: of person registering the complaint: Ms. | 2023-09-27 | 2023-09-27 12:29 | No | Warranty | Chandan Munot | L-1002 greens society thergaon | Pune | 411033 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Kunal jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the switch found that the Switch is not working it's found broken from inside the board . so this problem is not repairable.So switch Needs to be replaced, Required Material : X1001WH - 05 nos. we arranged the material from our stock and replaced it. | Repair |  | 9- Service Validated | 2023-09-27 16:02 | =S= Consig Fill up 226086356 |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11314546 | 104281798 | 2023-09-27 16:27 | 2023-09-27 |  | 2023-09-27 09:58 | EZ9F76340 | EZ9F76340 | EZ9F76340 |  | EZ9F76340 MCB 3 POLE 40A DEFECT -SCREW FREE CODE D2041 INVOICE ATTACHED EZ9F76432 MCB 4POLE 32A DEFECT PHASE MISSING CODE D2242 THESE 2 PRODECTS WITH US FROM DELAER With RegardsPrashant MattaNaman Enterprisesshop no-33 ground floorkalawati paliwal marketGumanpura, KotaRajasthanMob:09829863933 | 2023-09-27 | 2023-09-27 16:32 | No | Warranty | Naman Enterprises | Shop no. 33, kalawati Paliwal Marke | kota | 324007 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | Checked the mcb found screw free, Hence faulty replaced. EZ9F76340 - 1 nos EZ9F76432 - 1 nos Email : | Repair |  | 8- Service Completed | 2023-09-28 14:28 |  |  | 250 | INR | 250 | ENM HOME DISTRIBUTION
WO-11314592 | 104299408 | 2023-09-28 12:40 | 2023-09-27 |  | 2023-09-27 10:29 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Defected Products: 1.Smart Doorbell : IH100WFVDP 2.4 channel realy 3.Automation Gate way Invoice Details: goyal electricals 28 october 2022 Address House number 385 Sector 79 Mohali 140308 Contact Person Abhay Sood 8968844922 | 2023-09-27 | 2023-09-28 13:21 | No | Warranty | Abhay Sood | House number 385 Sector 79 | Mohali | 140308 | Punjab | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Ram Ashish Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the 4 chennel relay found not getting off(fix on) due to S3 wire and S4 wire short set the right now working is properly. IH100WFVDP - srn:-SDC036220221256 Checked the found not working properly due to WIFI Speed issue and vdp is working healthy. Hence case is closed. WIFI Signal - 24% to 48% dbm-89 down load speed - 1.0 Mbp5 Up load speed - 2.0 Mbp5 email : id not provided by the customer. | Repair |  | 8- Service Completed | 2023-09-28 15:59 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11315387 | 104299683 | 2023-09-27 12:19 | 2023-09-27 |  | 2023-09-27 10:43 | EZ9F71463 | EZ9F71463 | EZ9F71463 |  | Your request is: Product : EZ9F71463 63 Amps (63 Amps ) MCB Sr No. D2143 , Nov 21 Warranty Status :Yes with in warranty Problem: Not getting ON Please replace Bala Shree Industries E-607-608, E.P.I.P. BORANADA,JODHPUR 342004 Mr. RAM 7888606910 saielecthouse@gmail.com | 2023-09-27 | 2023-09-27 12:21 | No | Warranty | Bala Shree Industries | E-607-608, E.P.I.P. BORANADA | JODHPUR | 342004 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Amarjeet Singh Sharma Electric Jaipur | Sharma Electric Works | Checked the mcb found phase missing problem and UV coil found not working, Hence faulty replaced. EZ9F71463 - 2 nos LV429407 - 1 nos EZ9F76240 - 4 nos Email : | Repair |  | 8- Service Completed | 2023-09-27 16:19 |  |  | 338 | INR | 338 | ENM HOME DISTRIBUTION
WO-11315492 | 104299833 | 2023-09-27 12:31 | 2023-09-27 |  | 2023-09-27 10:45 | A9N3P02C | A9N3P02C | A9N3P02C |  | MCB Complaint Product: A9N3P02C MCB C Curve 2 Amps SR No.D 2221 May 2022 Yes In warranty Problem : Not passing Curren in One Pole | 2023-09-27 | 2023-09-27 12:33 | No | Warranty | IL&FS Transport Limited | Chenani Nashri Tunnel project Lower Mada Village Gugard Tehsil- chenani ,District - Udhampur | Udhampur | 182142 | Jammu and Kashmir | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Ram Ashish Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the mcb found dolly free and phase missing. Hence faulty replaced. A9N3P02C - 1 Nos. A9N1P16C - 2 Nos. A9N4P16C - 2 Nos. email : sonukrjk@rediffmail.com | Repair |  | 8- Service Completed | 2023-09-27 15:52 |  |  | 395 | INR | 395 | ENM HOME DISTRIBUTION
WO-11316218 | 104299785 | 2023-09-27 12:59 | 2023-09-27 |  | 2023-09-27 11:05 | A9N4P63C | A9N4P63C | A9N4P63C |  | MCB Complaint Model:- MCB A9n4p63c Sr: D2313 Fault:- One pole no conitu Shakti Electrical & Trading Co Vasant Road Maliwara Ghaziabad 7310952882---Varun Email : shaktielectrictrading@gmail.com | 2023-09-27 | 2023-09-29 15:03 | No | Warranty | Shakti Electrical & Trading Co | Vasant Road Maliwara | Ghaziabad | 201001 | Uttar Pradesh | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the MCB and found MCB have output issue, We replace the faulty MCB with new. | Repair |  | 8- Service Completed | 2023-09-29 15:14 |  |  | 24 | INR | 24 | ENM HOME DISTRIBUTION
WO-11316228 | 104300058 | 2023-09-27 12:04 | 2023-09-27 |  | 2023-09-27 11:14 | A9N1P10C | A9N1P10C | A9N1P10C |  | Product : A9N1P10C 1Pole 10 Amps Sr No. D2149 DOM Dec 2021 Warranty Status Yes in Warranty Knob Loose / Free Unable to switch on Check-List for Complaint Regn. Mr Mehul H.no no.25 Keshavpura, Rangbari, Kota Rajasthan Pin 324005 Mr Mehul 8905814890 | 2023-09-27 | 2023-09-27 12:06 | No | Warranty | Mehul Mehul | H.no no.25 Keshavpura, Rangbari, kota Rajasthan | KOTA | 324002 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | Checked the mcb found phase missing , Hence faulty replaced. A9N1P10C - 1 nos EZ9F71263 - 4 nos A9N4P63C - 2 nos Email : | Repair |  | 8- Service Completed | 2023-09-27 16:14 |  |  | 250 | INR | 250 | ENM HOME DISTRIBUTION
WO-11316338 | 104299642 | 2023-09-27 16:38 | 2023-09-27 |  | 2023-09-27 11:59 | UNS4STFAN1M_WE | UNS4STFAN1M_WE | UNS4STFAN1M_WE |  | Mr.Rajesh bhargava Hno 69/1 Khedli phatak Station Road Kota Pin 324005RegardsPrashant MattaNaman Enterprises kota, Rajasthan Mob-9829863933 On Wed, 27 Sept 2023 at 9:56 am, Mail2Case India <customercare.in@schneider-electric.com> wrote: Hello Sir/Mam.Greetings of the day.We have received your complain request , We would like to tell you that the details which you have sheared with us is not sufficient for filing the complain .So we request you that please share the mentioned details:. Complete site address of customer with pin-codeThank You--------------- Original Message ---------------From: [namankota@yahoo.com]Sent: 26/9/2023 5:50 pmTo: customercare.in@schneider-electric.comSubject: CUSTOMER COMPLAINT DEAR TEAM FAN REGULATOR NOT WORKING- 2PCS UNS4STFAN1M_WE CUSTOMER -MR.BHARGAVA STATION ROAD MOB-9468735331 With RegardsPrashant MattaNaman Enterprisesshop no-33 ground floorkalawati paliwal marketGumanpura, KotaRajasthan Following attachments are linked to this email:1.WhatsApp Image 2023-09-26 at 5.46.26 PM.jpegthread::R5vddxULcfGbOQZEw0pG8z4:: | 2023-09-27 | 2023-09-27 14:31 | No | Warranty | Rajesh Bhargava | Hno 69/1 Khedli phatak Station Road | Kota | 324005 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | Checked the fan regulator found not working, Hence faulty replaced UNS4STFAN1M_WE - 2 nos Email : id not provided by customer . | Repair |  | 8- Service Completed | 2023-09-28 14:33 |  |  | 250 | INR | 250 | ENM HOME DISTRIBUTION
WO-11316363 | 104299740 | 2023-09-27 12:52 | 2023-09-27 | Switch not working | 2023-09-27 12:06 | X1001WH_N | X1001WH_N | X1001WH_N |  | Complaint for Switch not Working Please issue complaint no as details given below. 1. Name of Customer: Shivraj Bhosale 2. Site Address: - L-104, Greens Society, Thergaon, Chinchwad, Pune -411033 3. Name of contact person at site :- Shivraj Bhosale 4. Contact Phone / Mob. No: - 90042 33339 5. Defective product details:-X1001WH 6. Product Make:- Opale 7. Nature of Defect: Switch not working 8. Shutdown availability if applicable :nil 9. Serial No: or DOM of -14224 10. Dealer Name /OA no. /Invoice Details: - 10 years warranty 11. Commissioned / Installed date:- NIL 12. Name & phone No: of person registering the complaint: Mr. Shivraj Bhosale Please do the needful. Thanks & regards, Shivraj | 2023-09-27 | 2023-09-27 15:58 | No | Warranty | Shivraj Bhosale | L-104, Greens Society, Thergaon, Chinchwad, | Pune | 411033 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Kunal jadhav_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the switch found that the Switch is not working it's found broken from inside the board . so this problem is not repairable.So switch Needs to be replaced, Required Material : X1001WH - 02 nos. we arranged the material from our stock and replaced it. | Repair |  | 9- Service Validated | 2023-09-27 16:01 |  |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11316781 | 104304515 | 2023-09-27 15:22 | 2023-09-27 |  | 2023-09-27 14:58 | IH12000020 | IH12000020 | IH12000020 |  | Register a complain for wiser(not working) With due to kind attention Red light in gateway, wise is not taking any command but Wi-Fi is available working properly in all device. Attached file for your reference. Client details: BA-11, Salt lake city sec-1, between PNB Bank I Land & 2 no tank Mr Vijay Jha -9831729224 Best Regards, Rohit Poddar M: 9830806331 | 2023-09-27 | 2023-09-28 16:00 | No | Warranty | Vijay Jha | BA-11 Salt Lake City sector-1 between PNB Bank IN Land & 2 no tank | kolkata | 700064 | West Bengal | India FS ED&I CSP East Team SREYAM SERVICES BHATPARA | AMIT BHATTACHARYA_SREYAM SERVICES BHATPARA | Sreyam Services(8513) | AFTER SITE VISIT FOUND GATEWAY CHECK ITS RJ45 CONNECTION CONNECTION ARE CUTTING, THIS CABLE REPLACE BY NET WORK ENGINEER. GATEWAY CHECK FOUND OK. | Repair |  | 8- Service Completed | 2023-09-28 16:03 |  |  | 12 | INR | 12 | ENM HOME DISTRIBUTION
WO-11316981 | 104305426 | 2023-09-30 11:59 | 2023-09-27 |  | 2023-09-27 15:58 | MTN684064 | MTN684064 | MTN684064 |  | Dear Sir, "Greeting From Eco Power Solution" Please Attend the following complaint. Name :- SUI DHAAGA SEWING MACHINES LIMITED Address :- MALERKOTLA ROAD, BACK SIDE RANIA PETROL PUMP, V.P.O. GILL, Punjab, 141116 Contact number :- 85688 02030 Complaint :- MTN684064 - 1 pcs Invoice Date : 25 -01-2023 Problem :- This item is not working properly. Kindly attend the complaint on priority basis. Attached sale invoice Thanks & Regards ASHISH KUMAR ECO POWER SOLUTIONS (Sister Concern of M/s Automation Systems Ludhiana) Cabin No. 1, 90-C, Shakti Enclave Near Toor Complex, Dugri Road Ludhiana-141002 PUNJAB Virus-free.www.avast.com | 2023-09-27 | 2023-09-30 15:16 | No | Warranty | SUI DHAAGA SEWING MACHINES LIMITED | MALERKOTLA ROAD, BACK SIDE RANIA PETROL PUMP, V.P.O. GILL null | Ludhiana | 141116 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | checked the MTN found not power up. Hence faulty, replaced Material replaced by dealer. MTN684064 - 1 Nos. Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-30 15:25 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11317305 | 104310534 | 2023-09-28 11:56 | 2023-09-28 | Validated By Prashat | 2023-09-27 18:16 | E8315USB_WG_G8 | E8315USB_WG_G8 | E8315USB_WG_G8 |  | Faulty Switches Mr Sahil K 2147, The Atla, Sab TV lane, Nr Laxmi Industrial Estate, Link Road, Andheri West. Mumbai. M: 9920717107 Ref found faulty : E8315USB_WG_G8 purchase from nylon electric corporation Dated 10th August 2022. | 2023-09-27 | 2023-09-28 14:00 | No | Warranty | Sahil K | 2147, The Atla, Sab TV lane, Nr Laxmi Industrial Estate, Link Road, Andheri West | Mumbai | 400001 | Maharashtra | India FS ED&I CSP West Team S K SERVICES Mumbai | Ganesh Tati_S K SERVICES Mumbai | S.K. Services (10237) | We Visited Site Avatar ON USB Charger Is Not Operating So Totally Off Or Not Powering On We Replace The Product Closed The Complant | Repair |  | 9- Service Validated | 2023-09-28 19:33 |  |  | 15 | INR | 15 | ENM HOME DISTRIBUTION
WO-11321833 | 104330177 | 2023-09-28 11:29 | 2023-09-28 |  | 2023-09-28 11:09 | A9N3P10C | A9N3P10C | A9N3P10C |  | MCB Complaint MCB A9N3P10C, 10Amps Sr no D 2144 DOM NOV 2021 Warranty Status : YES Problem : Not passing Voltage Phase missing Please arrange to replace the product | 2023-09-28 | 2023-09-28 11:30 | No | Warranty | Hitesh Electrical | Shop no--3 ajanta chowk bhiwadi district Alwar | Bhiwadi | 301019 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | Checked the mcb found not working due to phase missing, Hence faulty replaced. A9N3P10C - 1 nos EZ9F76332 - 1 nos EZ9F76325 - 1 nos EZ9F76316 - 1 nos Email : | Repair |  | 8- Service Completed | 2023-09-28 16:01 |  |  | 175 | INR | 175 | ENM HOME DISTRIBUTION
WO-11322109 | 104332159 | 2023-09-28 16:58 | 2023-09-28 |  | 2023-09-28 13:14 | P6005 | P6005 | P6005 | NA | case id 104303764 work order creation for ITC Hotel Complaint Key guards having problems at ITC- Kakatiya- Somajiguda. Ask Master Electricals to attend this site and check, meanwhile will generate the WO and give it to them. Thanks & Regards Saikumar.Kona DGM-Field Service Operations- TS & AP Mobile -9849075853 Please find the attached complaint form Request you to register the same. Checklist for Complaint Registration 1 Name of Customer RH Power Sistem 2 Site Address Shanti Nagar ITC Hotel Hyderabad. 3 Name of contact person at site Yeshwanth Reddy 4 Contact Phone / Mob. No: 9502319628 & 9550346688 5 Defective product details P6004 10 Nos 6 Nature of Defect Key Guard 7 Shutdown availability if applicable 8 Warranty status yes 9 Commissioned / Installed date Sep-23 10 Serial No: or DOM of the product D2023 Regards, Rajendra Prasad Mekala Manager- Sales Retail Division Schneider Electric M 8008933200 E rajendra.kumarp@se.com Skype rajendra.kumarp@se.com Schneider Electric India Pvt. Ltd. 401 - 404A,4th Floor, Ashoka Bhoopal Chambers, SP Road, Secunderabad-500003 Telangana | 2023-09-28 | 2023-09-30 19:14 | No | Warranty | ITC Kakatiya | 6-3-1187, Srinivasa Towers, Begumpet, | Hyderabad | 500003 | Telangana | India FS ED&I CSP South Team Master Electrical Solutions Hyderabad | VEERESH KUMAR Master Electrical Solutions SECUNDERABAD | Master Electrical Solutions | As per complaint visited the site carried out the following job Check the operation of power key card switches or not working properly inside pressing nob was not pressed when put in the key card so adjusted then it will work after that again one more operation we facing same issue we need to replace the switches Material Quantity P6005 20.NO's Hand over to the customer and taken back defective material | Repair |  | 8- Service Completed | 2023-09-30 19:47 |  |  | 10 | INR | 10 | ENM HOME DISTRIBUTION
WO-11322477 | 104335412 | 2023-09-29 15:03 | 2023-09-28 |  | 2023-09-28 16:04 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | New installation of wiser smart door bell: Mr. Gaurav Mehta, Mohali Pls install a smart door bell at the below address. Copy of invoice is attached. Product Name: WISER Smart Door Bell Qty: 01 No Contact Details: Gaurav Mehta Address: House Number : House Number 743, Sector 94, Mohali, Pin code: 140301 Contact number : +91 70609 67435, 8360361651 Installation : NEW Broadband with wifi Available: Yes Special Note:- Please intimate before visiting at the customer site. Regards Pardeep kumar Sr. Sales Executive Schneider Electric Mohali 8360361651 | 2023-09-28 | 2023-09-29 15:06 | No | Commercial Action - Sales | Gaurav Mehta | House Number 743, Sector 94, | Mohali | 140301 | Punjab | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Ram Ashish Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the vdp found not power up. Hence faulty replaced. IH100WFVDP - 1 Nos. email : id not provided by the customer. | Commissioning & Installation | Start-up | 8- Service Completed | 2023-09-29 17:41 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11322585 | 104337475 | 2023-09-28 17:17 | 2023-09-28 | Part order request validated by Mr. Chandrakant Panchal Sir | 2023-09-28 16:58 | X1001WH_N | X1001WH_N | X1001WH_N |  | Hi Team, Please register a complaint Product reference - X1001WH 4 nos & X2007WH 1 nos & X3200wh 2 nos & x1025wh 1 nos & X2106wh 2 nos & X1005wh 1 nos Products are not working, Invoice copy is attached here & take action for better service Site Address- Site ? MIG 2/3B Saket Nagar Bhopla Name ? Harbhajan Piplode Number -9425457747 Pin code ? 462026 Email- harbhajanpiplode12@gmail.com Sachin MishraSenior Sales Executive Power BusinessSchneider Electric M 7566612425 E Sachin.mishra@non.se.comCustomer Care Customercare.in@schneider-electric.com E7/31,Arera colony Flat no.G3, G. Floor Vinay Apartment, Bhopal 462016 Internal | 2023-09-28 | 2023-09-29 23:43 | No | Warranty | Harbhajan Piplode | MIG 2/3B Saket Nagar | Bhopla | 462024 | Madhya Pradesh | India FS ED&I CSP West Team ABR Technical Service Indore | Mayank Patidar_ABR Technical Services Indore | ABR Technical Services (9574) | Checked and found following faulty products details are given below:- 1) X1001WH - 4 Nos. - 16225L, 16283L - Broken 2) X1005WH - 1 Nos. - 16320L - Mech. Stuck 3) X1025WH - 1 Nos. - 16224L - Mech. Stuck 4) X3200WH - 2 Nos. - 16252L - Steps not working 5) X2106WH - 2 Nos. - 16433L - Shutter not working 6) X2007WH - 1 Nos. - 16433L - Shutter not working As per DOM product are out of warranty but customer provided Invoice Dated - 28/06/2023. So for customer satisfaction we recommend to replace all above faulty products. Replaced from distributor stock and now we are closing this case. | Repair |  | 8- Service Completed | 2023-09-30 11:44 | =S= Consig Fill up 226097876 |  | 215 | INR | 215 | ENM HOME DISTRIBUTION
WO-11322632 | 104341056 | 2023-09-28 18:25 | 2023-09-28 |  | 2023-09-28 17:27 | IN8486_BZ | IN8486_BZ | IN8486_BZ |  | Zencelo Complaint Zencelo switch 32 DP switch ---2 nos 16 amp switch --1 no Purchased on 11th Aug 2023 Site :- Flat no 51 Sai charan Apartment Behind. ICICI bank Green glen Layout Bellandur Bangalore 560103 Tarkesh 9986562462 | 2023-09-28 | 2023-09-30 21:29 | No | Warranty | Tarkesh Tarkesh | Sai charan Apartment Behind. ICICI bank Green glen Layout Bellandur | Bangalore | 560103 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | MANOJ GANESAN SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported zencelo switch. found struck up issue and led indicator not glow.so we replaced and checked working ok. | Repair |  | 8- Service Completed | 2023-09-30 21:32 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11322645 | 104341108 | 2023-09-29 10:55 | 2023-09-28 |  | 2023-09-28 17:28 | IH101ZWIFI | IH101ZWIFI | IH101ZWIFI | GW040216220634067 | Dear sir , 2 months back we have installed a home automation of schnieder . This time 2 relay showing inactive . We having facing a problem to on and off the lights Old case no. Is - 97109980 Part reference - IH101ZWIFI Serial no. - GW040216220634067 Adress - B-43 ,sec-H , Aliganj lucknow, uttar pradesh PIN code - 226024 Contact person - sarthak gulati Contact no.7607471078 | 2023-09-28 | 2023-09-29 16:04 | No | Warranty | Sarthak Gulati | B 43 sector H Aliganj | Lucknow | 226024 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Abhishek Patel Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found RELAY having setting issue, we resolve now relay working fine | Repair |  | 8- Service Completed | 2023-09-29 16:09 |  |  | 10 | INR | 10 | ENM HOME DISTRIBUTION
WO-11326241 | 104358388 | 2023-09-29 14:58 | 2023-09-29 | MCb fitting yellow Clip missing | 2023-09-29 10:40 | EZ9F76116 | EZ9F76116 | EZ9F76116 |  | PRODUCT DEFECTIVE - EZ9F76116 [ thread::bh3NjYGufBG4iJQsuvK7lD4:: ] Please find below product details: 1. Name of Customer: Shrikrishna Mahavir Electrical Works, KHED-SHIVAPUR 2. Site Address: - Elegance,Gat No.780/3,4, Near Toll Plaza,Khed Shivapur, Tal: Haveli,Dist:Pune - 412205 3. Name of contact person at site :- Mr. Amit Sangali 4. Contact Phone / Mob. No: 9168888194 5. Defective product details:- EZ9F76116 , QTY: 2 6. Product Make:-Schneider Electric 7. Nature of Defect: - Product Defective | 2023-09-29 | 2023-09-30 16:44 | No | Warranty | Shrikrishna Mahavir Electrical Works | Ground Floor, Shop No.3 and 4, | Pune | 412205 | Maharashtra | India FS ED&I CSP West Team SUPER ELECTRICALS ENGINEERING SERVICES Pune | Samadhan S_Super electricals Pune | Super Electricals Engineering Services(500017125) | Checked the MCb fitting yellow Clip missing. mounting clip not comes in MCb. so we arrange 2 nos of mounting of MCb and fitted it. then problem is resolved. this is new one product. | Repair |  | 8- Service Completed | 2023-09-30 16:49 |  |  | 60 | INR | 60 | ENM HOME DISTRIBUTION
WO-11327119 | 104359994 | 2023-09-29 13:15 | 2023-09-29 |  | 2023-09-29 12:14 | EZ9R55263 | EZ9R55263 | EZ9R55263 |  | Product : EZ9R55263 RCCB Sr No. DD 2021 W46-2-1 Yes With in Warranty Problem : Dolly Free / Not getting ON Automation & Control Unit -II ( Panal Manufacturing ) Industrial Area ,SIDCUL Pantnagar, 263153 Udham Singh Nagar, Uttarakhand. Mr. Surinder Kumar 8847413880 Ganesh7471@rediffmail.com | 2023-09-29 | 2023-09-29 13:16 | No | Warranty | Automation & Control pvt ltd. | Unit -II ( Panal Manufacturing ) Industrial Area ,SIDCUL Pantnagar | Udham Singh Nagar | 263153 | Uttarakhand | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Amandeep Singh_Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the meter found display not power up and rccb found not getting on due phase missing, Hence faulty replaced. METSEEM6436HCL10RS - 2 nos EZ9R55263 - 1 nos Email : ganesh7471@rediffmail.com | Repair |  | 8- Service Completed | 2023-09-29 16:55 |  |  | 5 | INR | 5 | ENM HOME DISTRIBUTION
WO-11327237 | 104361023 | 2023-09-29 18:19 | 2023-09-29 |  | 2023-09-29 13:04 | IN8401_16_SP | IN8401_16_SP | IN8401_16_SP |  | RE: 104299494 - Seetharaman Hi Team, Please refer trialing mail and share one more Repair Wo on priority 104299494 In Customer Site Switches also issue. Our Engineer discussed with Pramoth sir & Venkatesh sir for switches issue. Kindly discuss the Pramod sir & Venkatesh Sir & log the Thermostat call. Thanks & Regards Vidya.J | 2023-09-29 | 2023-09-30 17:42 | No | Warranty | Seetharaman Seetharaman |  | Coimbatore | 641018 | Tamil Nadu | India FS South2 ED&I CSP GRControlSystems Coimbatore | Mani kandan GRControlSystems Coimbatore | GR Control Systems-Coimbatore | Thermostat - 4Nos Reset & Configuration done | Repair |  | 8- Service Completed | 2023-09-30 17:46 |  |  | 18 | INR | 18 | ENM HOME DISTRIBUTION
WO-11195369 | 103729145 | 2023-09-01 22:10 | 2023-09-01 |  | 2023-09-01 18:38 | A9N4P32D | A9N4P32D | A9N4P32D | 2023-W28-3-6 | Re: requested for details, Case: 103442675, [ thread::M3eZ8TicfsC9pz_fs4DTfT4:: ] DOP:02/08/2023 A9N4P32D 2023-W28-3-6 ITEM :32A 4POLE MCB D CURVE MODEL NO.A9N4P32D NOT WORKING SITE ADDRESS NAME:SHIVAKUMAR B MOB:9980011776 ss ADDRESS :DELL R & D CENTRE 7TH FLOOR BAGMANE TECH PARK 65/2 BAIRASANDRA MAIN ROAD CAUVERI COLONY BYRASANDRA CV RAMAN NAGAR BANGALORE - 560093 | 2023-09-01 | 2023-09-03 10:00 | No | Warranty | Dell | Dell India R&D centre #65/2 Bagmane Parin Bagmane Tech Park,Bairasandra Main Road C V Raman | Bangalore | 560093 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | C Gunasekaran_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported mcb found not getting ON, due to burr or dust at mcb sticker side. We removed and checked the on,off operations found working ok. The same shown to the customer. | Repair |  | 9- Service Validated | 2023-09-03 20:53 |  |  | 12 | INR | 12 | ENM HOME DISTRIBUTION
WO-11199302 | 103740941 | 2023-09-02 10:53 | 2023-09-02 |  | 2023-09-02 10:42 | A9N19667 | A9N19667 | A9N19667 | 225674606 | FW: WO Re-Assign Request : WO-11183306 , Infosys Limited RCBO nuisance tripping issue of 25A 2pole 30mA in Infosys Chennai As I have told we have supplied 25A 2pole 30mA RCBO ( A9N19667 ) to Infosys Chennai Project from Shankar electricals Now Customer is facing nuisance tripping issue of 25A 2pole 30mA So Kindly arrange to send Schneider Service person to check and resolve the issue Mr Naresh ? 9094237422 Note : Before going to site Plz call him SO : 225674606 Item : A9N19667 - 1No Issue : facing nuisance Within warranty | 2023-09-02 | 2023-09-02 19:00 | No | Warranty | Infosys Limited | IL Chennai Shols SEZ Dev No 138 Infosys limited Sez developer old rd Kanchipuram Chennai Tamilnadu 600119 India | SHOLINGANALLUR | 600119 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Site Visit Done | Repair |  | 9- Service Validated | 2023-09-05 19:43 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 29 | INR | 29 | ENM HOME DISTRIBUTION
WO-11229420 | 103883922 | 2023-09-08 15:05 | 2023-09-08 |  | 2023-09-08 13:07 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | Installation request Hotel Novotel Plot 181, 3B, industrial area, Phase 1, Chandigarh Kindly arrange a technician visit tomorrow morning positively at this place for installation of the below product. 1 smart door bell-IH100WFVDP 1 gateway-IH101ZWIFI 1 relay 4 channel-IH14000100 1 curtain controller -IH11000200 - Pardeep kumar /8360361651/engineerpardeepkumar@yahoo.com | 2023-09-08 | 2023-09-09 10:23 | No | Commercial Action - Sales | Hotel Novotel | Plot 181, 3B, industrial area Phase 1 null | Chandigarh | 160002 | Chandigarh | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Karnail Singh Sharma Electric Chandigarh | Sharma Electric works(1003) | visited the site and install the bell , 4 channel relay and curtain controller and gateway now working ok , IH140000100 - 1 , Srn:4R2302302511916 IH1000200 - 1 , Srn:CC440214050543 IH101ZWIFI - 1 ,Srn:02/23 IH100WFVDP -1 , Srn:05/23 > Checked the curtain controller relay found no communication issue.Hence faulty replaced. > IH11000200 - 1 Nos. email : engineerpardeepkumar@yahoo.com | Commissioning & Installation | Start-up | 9- Service Validated | 2023-09-09 12:46 |  |  | 25 | INR | 25 | ENM HOME DISTRIBUTION
WO-11234312 | 103909920 | 2023-09-09 13:41 | 2023-09-09 |  | 2023-09-09 13:13 | A9N18367 | A9N18367 | A9N18367 |  | Act9 100A 3p Mccb properly is not working QQ-2022-w22-8 Convert JN Sea Port Ship Yard Visakhapatnam 530020 Andhra Pradesh India Contact Kingshuk Jena ?916302939352 | 2023-09-09 | 2023-09-15 12:40 | No | Warranty | Sadhav Offshore engineering PVT LTD | Convert JN Sea Port Ship Yard | Visakhapatnam | 530020 | Andhra Pradesh | India FS ED&I CSP South Team Voltamp Electrical Works Visakhapatnam | Chinni SaiKumar_VOLT AMP ELECTRICAL WORKS Visakhapatnam | Voltamp Electrical Works | Visited the site and found above the Act 100 A 3P MCB is not working so today we have observed the problem of 100 A 3P MCB Dolby issue so zvo material replaced | Repair |  | 9- Service Validated | 2023-09-15 12:41 |  |  | 20 | INR | 20 | ENM HOME DISTRIBUTION
WO-11301101 | 104192718 | 2023-09-23 14:14 | 2023-09-23 |  | 2023-09-23 11:31 | CSS54E_WE | CSS54E_WE | CSS54E_WE |  | CSS54E_WE - not functioning | 2023-09-23 | 2023-09-26 18:20 | No | Warranty | Paras Agarwal | House No.6 Pushpanjali Colony, Kanth Road, | Moradabad | 244001 | Uttar Pradesh | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Visit the site and found faulty material not available at site. We suggest to customer please available the faulty material at site then again login the complaint. Now we close the complaint. | Repair |  | 8- Service Completed | 2023-09-27 11:33 |  |  | 168 | INR | 168 | ENM HOME DISTRIBUTION
WO-11295473 | 104209893 | 2023-09-23 00:38 | 2023-09-22 | Validated By Prashant | 2023-09-22 13:11 | IN8401_16_SP | IN8401_16_SP | IN8401_16_SP |  | DOP: 3 March 2023 Zencelo Switches Qty: 1 P: Not Working Kindly check invoice at site | 2023-09-22 | 2023-09-27 18:00 | No | Warranty | Bhagus Vani | 71B Tower Jolly Maker Apt 1 Opp to Maker Chamber Cup parade Kulaba | Mumbai | 400005 | Maharashtra | India FS ED&I CSP West Team S K SERVICES Mumbai | Ganesh Tati_S K SERVICES Mumbai | S.K. Services (10237) | We visited the site Product Ref No:-IN8431USB -BZ-1nos. Serial no:-22173L We check the material Zencelo USB charger is totally off We will replace the product book ZVO. We Replace The Product Closed The Complaint | Repair |  | 9- Service Validated | 2023-09-27 20:36 | 226079520 |  | 20 | INR | 20 | ENM HOME DISTRIBUTION
WO-11299970 | 104219049 | 2023-09-25 23:30 | 2023-09-23 | NA | 2023-09-23 09:49 | C40H32D400 | C40H32D400 | C40H32D400 |  | ARROW ELECTRICALS INDIA PVT. LTD Arrow House, 11A/11B, K.T. Industrial Park, Goraipada, Vasai, Dist. Palghar, Maharashtra 401208. Rahul Kumar (7488332189) 7488332189 arrowsales@arrowelectricals.in C40H32D400 - 1 DOLLY FREE INVOICE NO.9008670694 (DATE- 07 Aug 2023) JAYESH MHATRE | 2023-09-23 | 2023-09-26 16:05 | No | Warranty | Arrow Electricals India Pvt. Ltd. | Arrow House (11A/11B), K.T. Industrial Park, Goraipada,, Vasai E, Dist. Palghar | Vasai | 401208 | Maharashtra | India FS ED&I CSP West Team Kanekar Consulting Engineers Pvt Ltd Thane | Nitin Arote_Kanekar Consulting Mumbai | Kanekar Consulting Engineers Pvt. Ltd. | Material is not available on site, already solved the problem by customer, material dispatch to end user closed this case. | Repair |  | 9- Service Validated | 2023-09-26 16:06 |  |  | 27 | INR | 27 | ENM HOME DISTRIBUTION
WO-11301219 | 104229964 | 2023-09-25 10:03 | 2023-09-23 |  | 2023-09-23 15:01 | P1001_6_DG_N | P1001_6_DG_N | P1001_6_DG_N |  | DOP: 31/5/2022 Livia switches P: Not Working Safwan Alungal house Anvar nagar , kuniyil , areekode Malappuram dt. Pin : 673639 Kerala. Safwan 7994561760 | 2023-09-23 | 2023-09-25 15:21 | No | Warranty | Safwan Safwan | Alungal house Anvar nagar , kuniyil , areekode | Malappuram | 673639 | Kerala | India FS South2 ED&I CSP APSMarketingCompany Calicut | Roshid APSMarketingCompany Calicut | APS Marketing Company | visited this site found livia switchs indicator not working P1181 1NOS P1086 1NOS replaced problem solved | Repair |  | 9- Service Validated | 2023-09-25 15:22 |  |  | 40 | INR | 40 | ENM HOME DISTRIBUTION
WO-11301267 | 104230147 | 2023-09-25 11:04 | 2023-09-25 |  | 2023-09-23 16:41 | A9N4P63C | A9N4P63C | A9N4P63C |  | DOP: 8/9/2023 A9N4P63C Qty:1 P: Tripping issue VOLT-ON Engineering, No.60, Gramani Street, Station Road (South), Korattur, Chennai-600080 Contact: 07358768311/312 | 2023-09-23 | 2023-09-27 18:00 | No | Warranty | VOLT-ON Engineering | No.60, Gramani Street, Station Road (South), Korattur, null | Chennai | 600080 | Tamil Nadu | India FS ED&I CSP South Team Omicon Engineering Madurai | Dinesh Kumar_Omicon Engineering Madurai | Omicon Engineering | Site Visit Done | Repair |  | 8- Service Completed | 2023-09-27 19:08 | Hi Team, Material booked zfre Zvo : 226067873 |  | 18 | INR | 18 | ENM HOME DISTRIBUTION
WO-11304201 | 104235429 | 2023-09-25 10:35 | 2023-09-25 |  | 2023-09-25 09:44 | A9N3P10C | A9N3P10C | A9N3P10C |  | Product : A9N3P10C MCB 10Amps , 3Pole Sr No D2217,DOM April 2022 Warranty : YES Not Powering ON / Phase Miss New Age Electricals Plot no. 985, industrial area, Dehradun Road, Paonta Sahib, Himachal Pradesh. PIN 173025 Mr.Nitesh Dhiman 8725051128 Email : nge_nitesh@rediffmail.com | 2023-09-25 | 2023-09-25 12:07 | No | Warranty | New Age Electricals | plot no. 985 , industrial area,Dedradun Road | Paonta Sahib | 173025 | Himachal Pradesh | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Karnail Singh Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the mcb found not giving output due to phase missing and contactor found not getting on due to phase missing. chaecked the LADN11 contact block found not giving output, Hence faulty replaced. A9N3P10C - 1 nos LC1DFKM7 - 1 nos LC1D18M7 - 1 nos LADN11 - 1 nos Email : nge_nitesh@rediffmail.com | Repair |  | 8- Service Completed | 2023-09-25 13:35 |  |  | 120 | INR | 120 | ENM HOME DISTRIBUTION
WO-11304224 | 104230686 | 2023-09-25 11:32 | 2023-09-25 |  | 2023-09-25 09:56 | UNS61SW1M_GY | UNS61SW1M_GY | UNS61SW1M_GY |  | NAME- MR SUNIL SAMDANI ADDRESS-Merlin 5th avenue Tower 1, Flat 24C Mohisbatan Kolkata - 700102 CONTACT PERSON-Mr Sunil Samdani NUMBER-97023 69666 PROBLEM- UNS61SW1M_GY 6AMP SWITCH UNICA-10nos PRODUCT-NOTWORKING STATUS-WARRANTY | 2023-09-25 | 2023-09-27 15:10 | No | Warranty | SUNIL SAMDANI | erlin 5th avenue Tower 1, Flat 24C Mohisbatan | Kolkata | 700102 | West Bengal | India FS ED&I CSP East Team SREYAM SERVICES BHATPARA | AMIT BHATTACHARYA_SREYAM SERVICES BHATPARA | Sreyam Services(8513) | AFTER SITE VISIT FOUND SWITCH REPLACED BY NEW ONE AND DEFFECTIVE MATERIAL IS COLLECTED. | Repair |  | 8- Service Completed | 2023-09-27 15:11 |  |  | 18 | INR | 18 | ENM HOME DISTRIBUTION
WO-11304250 | 104235762 | 2023-09-25 14:13 | 2023-09-25 |  | 2023-09-25 10:12 | A9N4P63C | A9N4P63C | A9N4P63C |  | A9N4P63C D2230 A9N3P32C D2230 A9N4P63C D2230 Qty:3 P: Dolly free Kindly check invoice at site | 2023-09-25 | 2023-09-28 16:56 | No | Warranty | Anupam Electrical Control | K-370, Site-V Kasna Industrial Area UPSIDC distt- Gautambudh nagar | Greater Noida | 201308 | Uttar Pradesh | India FS ED&I CSP North Team Saffron Automation Delhi | Banne Singh_Saffron Automation Delhi | Saffron Automation(18001) | Check the MCB and found MCB have dolly free issue and output issue and screw loss issue. We replace the faulty MCB with new. | Repair |  | 8- Service Completed | 2023-09-28 17:59 |  |  | 52 | INR | 52 | ENM HOME DISTRIBUTION
WO-11069748 | 102988954 | 2023-08-03 11:16 | 2023-08-03 |  | 2023-08-03 10:49 | ATV340D37N4E | ATV340D37N4E | ATV340D37N4E | 2.1405e+19 | We are facing problem in AC Drive Model no : ATV340D37N4E Serial No : 21405040088213080032 Site Address - Crescent Foundry Co. Pvt. Ltd. (Unit - 2)N. H. 6, Srirampore Kulgachia, P. O. Sumda, Uluberia, Howrah - 711303 Cont. Person - Mr. Suvas Pakhira (06290901657) Fault- SAFF error | 2023-08-03 | 2023-09-07 16:22 | No | Warranty | Crescent Foundry Co Pvt. Ltd. | Barunda, Madhya Para, Bagnan, Near Ananda Nikatan High School null | Howrah | 711303 | West Bengal | India FS ED&I CSP East Team SREYAM SERVICES BHATPARA | AMIT BHATTACHARYA_SREYAM SERVICES BHATPARA | Sreyam Services(8513) | FOUND DEFFECTIVE DRIVE REPLACED BY NEW ONE, DEFFECTIVE DRIVE DIRECT ORDER BY CUSTOMER SITE. | Repair |  | 9- Service Validated | 2023-09-07 16:39 |  |  | 60 | INR | 60 | Industrial Automation Ops
WO-11304293 | 104230428 | 2023-09-25 11:14 | 2023-09-25 |  | 2023-09-25 10:39 | CCT551023 | CCT551023 | CCT551023 |  | DOP: 20/6/2023 CCT551023- HIGH BAY SENSOR Qty:1 P: THIS SENSOR IS INTERMEDIATELY NOT WORKING, SOMETIMES NOT GETTING ON, OUTPUT IS NOT WORKING. M/S CHAITRA CIVIL VENTURES LLP SY.N 13, NEXT TO BMTC BUS DEPOT CHALLAGHATTA VILLAGE,KENGERI HOBLI BENGALURU-560074 KRISHNA PRASAD M 9900030357 | 2023-09-25 | 2023-09-30 11:15 | No | Warranty | M/S CHAITRA CIVIL VENTURES LLP | SY.N 13, NEXT TO BMTC BUS DEPOT CHALLAGHATTA VILLAGE,KENGERI HOBLI null | Bangalore | 560074 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Swamy HJ_P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | Inspected and found below mentioned 1)Ref: CCT551023 S/N: 1909 = 1 Sensor, sensor not working properly. Purchase invoice No: 112316870603901 Purchase Date: 20/07/2023 Hence we will give new same warranty replacement ASAP | Repair |  | 8- Service Completed | 2023-09-30 11:16 |  |  | 5 | INR | 5 | ENM HOME DISTRIBUTION
WO-11304308 | 104230432 | 2023-09-25 18:44 | 2023-09-25 |  | 2023-09-25 10:49 | LSS100100 | LSS100100 | LSS100100 |  | DOP: 23/2/2023 LSS100100-WISER FOR KNX Qty:1 P: THIS CONTROLLER IS NOT POWERING ON M/S CONSULATE GENERAL OF SWIZERLAND 26,3RD AND 4TH FLOOR CRESCENT PARK APTS REST HOUSE, CRESCENT ROAD BENGALURU-560001 Consulate 9900030357 | 2023-09-25 | 2023-09-30 15:00 | No | Warranty | M/S CONSULATE GENERAL OF SWIZERLAND | 26,3RD AND 4TH FLOOR CRESCENT PARK APTS REST HOUSE, CRESCENT ROAD null | Bangalore | 560001 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Mohammad Riyaz_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported LSS100100-1nos found the problem was this controller is not powering on, so we had arranged for the replacement and zvo directly booked to techmech engineers. | Repair |  | 8- Service Completed | 2023-09-30 20:33 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11304321 | 104231406 | 2023-09-26 14:20 | 2023-09-25 |  | 2023-09-25 10:54 | IH100WFVDP | IH100WFVDP | IH100WFVDP |  | roduct Name: WISER Smart Door Bell Qty: 01 Nos Contact Details: Dr. Amardeep singh Address: House Number : House Number 218, Sector 119, Gateway city, Near naryan e school. Mohali, Pin code: 140301 Contact number : +91 98768 77421, 8360361651 Installation : NEW Broadband with wifi Available: Yes | 2023-09-25 | 2023-09-30 14:44 | No | Commercial Action - Sales | Amardeep singh | House Number 218, Sector 119, Gateway city, Near naryan e school | Mohali | 140301 | Punjab | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Karnail Singh Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the vdp found not configure and unable to reset and program. Hence faulty replaced. IH100WFVDP - 1 Nos. email : id not provided by the customer. | Commissioning & Installation | Start-up | 8- Service Completed | 2023-09-30 14:47 |  |  | 30 | INR | 30 | ENM HOME DISTRIBUTION
WO-11304376 | 104230434 | 2023-09-25 18:46 | 2023-09-25 |  | 2023-09-25 11:20 | LSS100100 | LSS100100 | LSS100100 |  | DOP: 17/5/2023 LSS100100-WISER FOR KNX Qty:1 P: THIS CONTROLLER IS POWERING ON BUT WE CANNOT ABLE TO CONFIGURE THE CONTROLLER. MYLAR ELECTRICALS NO 24, 1ST CROSS L B SHASTRY NAGAR BENGALURU-560017 Maylar 9900030357 | 2023-09-25 | 2023-09-27 16:30 | No | Warranty | MYLAR ELECTRICALS | NO 24. 1ST CROSS L B SHASTRY NAGAR | Bangalore | 560017 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | MANOJ GANESAN SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported LSS100100- 1 nos found it was getting ON, but not able to configure the controller. So we had arranged for the replacement and zvo directly booked to techmech engineers. | Repair |  | 8- Service Completed | 2023-09-28 13:10 |  |  | 27 | INR | 27 | ENM HOME DISTRIBUTION
WO-11304565 | 104238107 | 2023-09-25 12:48 | 2023-09-25 |  | 2023-09-25 12:10 | IN8401_16_SP | IN8401_16_SP | IN8401_16_SP |  | DOP: 19/01/2023 Zencelo Switches Qty:3 P: Not Working Kindly check invoice copy at site | 2023-09-25 | 2023-09-26 10:12 | No | Warranty | Deepak Deepak | B 601 Shanthinikunj bliss Near Haridarshan Avenue Sola shine city road | Ahmedabad | 380060 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Mistri Anik Engineering Ahmedabad | Anik Engineering (554) | Visited t he site and checked the produc found physially observed ok. IN8401 SR NO : 23012 L switching problem 1 Nos IN8481/16 SR NO : 23022L switching problem . so free replacment.. | Repair |  | 9- Service Validated | 2023-09-26 10:13 | =S= Consig Fill up 226085140 |  | 35 | INR | 35 | ENM HOME DISTRIBUTION
WO-11304895 | 104242021 | 2023-09-25 17:47 | 2023-09-25 |  | 2023-09-25 14:04 | UNS5STFAN2M_WE | UNS5STFAN2M_WE | UNS5STFAN2M_WE |  | UNS5STFAN2M regulatore Speed problem Purchased on 25th feb 2023 from yahs Marketing raipur | 2023-09-25 | 2023-09-30 12:00 | No | Warranty | Hansraj Yadav | swarnabhumi , R3 , 144, amashivni , vidhan sabha road | Raipur | 492007 |  | India FS ED&I CSP East Team SOMDEV & COMPANY RAIPUR | SOUMYA BEHERA_SOMDEV & COMPANY RAIPUR | Somdev & Company | the switches are defective so we replace the same. | Repair |  | 8- Service Completed | 2023-09-30 17:30 |  |  | 18 | INR | 18 | ENM HOME DISTRIBUTION
WO-11098326 | 103148239 | 2023-08-10 12:38 | 2023-08-10 |  | 2023-08-10 10:32 | TM3AQ4 | TM3AQ4 | TM3AQ4 | IB2305S12569 | Product issue PLC coutput card TM3AQ4 IB2305S12569 | 2023-08-10 | 2023-09-12 10:28 | No | Warranty | Technocrat mouldings pvt Ltd | 967 MIE, Part A | Bahadurgarh | 124507 | Haryana | India FS ED&I CSP North Team Saffron Automation Delhi | Ashok Bhati_Saffron Automation Delhi | Saffron Automation(18001) | Check the Analog output card and found card have output issue, We replace the faulty analog output card with new. | Repair |  | 9- Service Validated | 2023-09-12 18:22 |  |  | 52 | INR | 52 | Industrial Automation Ops
WO-11102683 | 103200466 | 2023-08-11 11:11 | 2023-08-11 |  | 2023-08-11 10:48 | TM3XTRA1 | TM3XTRA1 | TM3XTRA1 | 8B22120014354 | PLC AND MODULE FAULTY TM3XTRA1 S/N:- 8B22120014354 | 2023-08-11 | 2023-09-18 13:10 | No | Warranty | JWIL INFRA LTD. | Near Satdharu Dam,Jhapan Road,Village,Hardua Post,RajaPatna | Damoh | 470880 | Madhya Pradesh | India FS ED&I CSP West Team ABR Technical Service Indore | Lalu Sen_ABR Tecneical Services Indore | ABR Technical Services (9574) | Reached at site site and checked PLC and modules and found details are given below Then we checked PLC /DI /DG /AI modules not communicating with PLC also found some modules components damage so after discussion with product expert and we will revert back Please find attached Find enclosed Site incidental report. and we are close this case. | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-18 13:12 |  |  | 650 | INR | 650 | Industrial Automation Ops
WO-11125505 | 103258924 | 2023-08-16 11:47 | 2023-08-16 | softstarter is need to be replaced. ATS22C11Q- 01Nos | 2023-08-16 10:54 | ATS22C11Q | ATS22C11Q | ATS22C11Q | 8B2323396104 | Accuon Project Solutions Bhumkar Estate Sr.No.14/7, Behind Swami ?Narayan Temple & Krushna Kunj Phase 2, Near JSPM College Narhe, Pune-411041. Contact person-Ms.Mrunali Waghmare(9604267501) | 2023-08-16 | 2023-09-18 10:49 | No | Warranty | Accuon Project Solutions | Bhumkar Estate Sr.No.14/7, Behind Swami ?Narayan Temple & Krushna Kunj Phase 2, Near JSPM College Narhe | Pune | 411041 | Maharashtra | India FS ED&I CSP West Team Alliance Controls Pvt Ltd Pune | Shmabhu Bone_Alliance Controls Pvt. Ltd | Alliance Controls Pvt. Ltd. (7966) | (1) Visited on site and checked softstarter, when applied power and control voltage, it's getting in ready status. But 24VDC not getting only 7VDC measured on 24VDC Terminal. That cause softstarter can't be taking run command. (2) This problem has occurred to the customer while in testing. (3) Opened the softstarter and checked control card, found that component burn on control card. (4) As per telephonic discussion with Mr. Kiran Borse sir, this softstarter is need to be replaced. ATS22C11Q- 01Nos | Repair |  | 9- Service Validated | 2023-09-18 10:50 | =S= Consig Fill up 225975895 |  | 34 | INR | 34 | Industrial Automation Ops
WO-11126019 | 103306245 | 2023-08-17 12:36 | 2023-08-16 |  | 2023-08-16 14:50 | PFXGP4401TAD | PFXGP4401TAD | PFXGP4401TAD |  | DOM: 3/22 PFXGP4401TAD 138710C045181 P: Screen issue Alstrut India Pvt. Ltd 63, Thattankulam Rd J Garden Madhavaram Chennai, Tamil Nadu 600060 Mr.venkatesan 7358810891 | 2023-08-16 | 2023-09-22 10:39 | No | Warranty | Alstrut India Pvt. Ltd | 63, Thattankulam Rd J Garden Madhavaram null | Chennai | 600060 | Tamil Nadu | India FS ED&I CSP South Team Star Automations Chennai | Nobin Balaiah_Star Automations Chennai | Star Automations | Problem Reported by Customer : Point mark in display. Visited the site and checked the Proface - HMI physically it was good condition. On the device we found the point mark in the display. Discussed with schneider regarding this issue as special case we replace the Proface HMI ( PFXGP4401TAD ) in under warranty. We replace 1 no in under warranty. | Repair |  | 9- Service Validated | 2023-09-22 10:46 |  |  | 90 | INR | 90 | Industrial Automation Ops
WO-11145774 | 103404733 | 2023-08-21 17:35 | 2023-08-21 |  | 2023-08-21 15:53 | TM200C24R | TM200C24R | TM200C24R | WX35999223160431 | Complaint 08-09 TM200C24R Serial No. WX35999223160431 | 2023-08-21 | 2023-09-05 17:00 | No | Warranty | Friendsco Engineering Works | Plot No.-18, Phase-1, Industrial Area, Kundli | Sonipat | 131001 | Haryana | India FS ED&I CSP North Team Saffron Automation Delhi | Yavnish Tyagi Saffron Automation Delhi | Saffron Automation(18001) | Check the PLC and found PLC is power up, but PLC not showing any program and PLC also malfunctioning. So PLC is faulty. We replace the faulty PLC with new. | Repair |  | 9- Service Validated | 2023-09-05 22:25 | 225990541 ZFRE BOOKED. |  | 56 | INR | 56 | Industrial Automation Ops
WO-11146031 | 103411066 | 2023-08-23 15:48 | 2023-08-21 |  | 2023-08-21 17:33 | ATV610D45N4 | ATV610D45N4 | ATV610D45N4 | 4.0013e+17 | Complaint 08-11 | 2023-08-21 | 2023-09-19 16:40 | No | Warranty | ETH Biofuel | Lauhka Patti Railway Station Tarantaran null | AMRITSAR | 143415 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the vfd found show signal output -phase loss and control card found inter change but same problem observe, power board, control card,& DC bus board. Hence faulty, replaced. VX4DCPD45N4 - 1 Nos. VX4P610D45N4 - 1 Nos. VX4B610100 - 1 Nos. email : id not provided by the customer. | Assessment/ Inspection | Data Collection | 8- Service Completed | 2023-09-19 16:44 |  |  | 151 | INR | 151 | Industrial Automation Ops
WO-11150125 | 103442483 | 2023-08-24 16:39 | 2023-08-22 | As per discussion with mrs. Sandhya Mam product needed to be replaced . | 2023-08-22 13:32 | HMIPSPS752D1X01 | HMIPSPS752D1X01 | HMIPSPS752D1X01 | 8APSPS752221150009 | Issue:Not working Warranty HMIPSPS752D1X01 8APSPS752221150009 Issue:Not working Site Address: TATA MOTORS LIMITED DHARWAD BELUR INDUSTRIAL AREA, GARAG ROAD, MUMMIGATTI POST, DHARWAD. KARNATAKA -580011 Raghvendra hugar - 7795151519 raghvendra.hugar@tatamotors.com | 2023-08-22 | 2023-09-20 15:48 | No | Warranty | Tata Motors Limited | Beside High court, NH-4 Road, Belur Industrial Area, Mummigatti Post- , Dharwad | Dharwad | 580011 | Karnataka | India FS ED&I CSP West Team Alliance Controls Pvt Ltd Pune | Rohit Srivastav_Alliance Controls Pvt. Ltd | Alliance Controls Pvt. Ltd. (7966) | We visited at site & done as per below following points:- 1)Power up IPC by 24VDC supply & found IPC power led glowes in green and after sometime display gets blank and after 5 to 10 min found home page and we try to touch but not getting any response.2) In input side used SMPS 230VAC UPS power & O/P 24VDC , 10A and checked voltage and found I/P N-L= 229.1VAC , N-E = 0.67VAC & O/P +VE/-VE = 24VDC -VE/E =0.7VDC.3)We have attached photographs & videos.4) IPC installed 5 to 6 months before as per Verbally said by customers.5)We open IPC and checked for any burnt mark as damaged part but not observed any.6) As per observation for 40 to 45 min we found touch response is delay . touch calibration done found ok.7) But in actual functional checked that time touch response found delay . | Repair |  | 9- Service Validated | 2023-09-20 15:55 | =S= Consig Fill up 226002039 | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 433 | INR | 433 | Industrial Automation Ops
WO-11150580 | 103447959 | 2023-08-24 15:04 | 2023-08-22 |  | 2023-08-22 17:02 | ATV340D11N4E | ATV340D11N4E | ATV340D11N4E | HL204396030 | Complaint 08-13ATV340D11N4E Serial No. HL232023018 | 2023-08-22 | 2023-09-21 15:03 | No | Warranty | Square ?A? Controls & Automation(500053187) | STREET NO. - 3, BACHITTAR NAGAR, OPPOSITE GNE COLLEGE, GILL ROAD, | Ludhiana | 141002 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the vfd found IGBT short circuit. Hence faulty , replaced. ATV340D11N4E - 1 Nos. email : harmeet136@gmail.com | Repair |  | 8- Service Completed | 2023-09-23 14:07 |  |  | 25 | INR | 25 | Industrial Automation Ops
WO-11153147 | 103475080 | 2023-08-23 09:53 | 2023-08-23 | As per disccusion with mr. Kiran Borse sir above product needed to be replaced . | 2023-08-23 09:24 | XPSBAC14AC | XPSBAC14AC | XPSBAC14AC | 8B2307105676 / 8B-2023-W07 | Pl. provide complaint number Warranty 1) XB5AD912R4K7 HEAD AND POTENTIOMETER sr.no. 3L-2023-03-25 Nature of defect: C-TERMINAL SCREW NOT GETTING TIGHTNESS AND A & B-TERMINAL SCREW FOUND OK, GETTING TIGHTNING. 2) M9F43330 MULTI 9 30A D-CURVE 3 POLE MCB Sr.No AA-2022-W43-2 Nature of defect: Y-PHASE POLE OPEN. 3) XPSBAC14AC HARMONY SAFETY AUTOMATION SAFETY MODULE Sr.No. 8B2307105676 / 8B-2023-W07 Nature of defect: RELAY NOT WORKING 4) ATV340U40N4 Sr,No 4048000HL231363100 Nature of defect : DRIVE NOT GETTING ON For sr.no 1 to 4 pl. create WO and provide complaint number, 5) ATV320U15N4C Sr.No. HL2215571062 Nature of defect: SAFF FAULT ON DISPLAY For sr.No. 5 create separate WO and provide complaint number. 6) ATV320U07N4C Sr.No. HL2306966128 Nature of defect: GROUND SHORT CIRCUIT FAULT ON DISPLAY For sr.. No. 6 create separate WO and provide complaint number. Pl provide complaint number as per given above details immediately and assign it to me for 22.08.2023 schedule date to me, BOBST INDIA PVT LTD, Plot no.82,126-132, village kasar Amboli,Post Ambadvet, Ghotawade Road,Taluka Mulshi, Contact person: Mr. Parasaram Kolekar Mob. No. 8378985861 | 2023-08-23 | 2023-09-01 12:40 | No | Warranty | BOBST India Pvt. Ltd. | Plot No. 82, 126-132, Village Kasar Amboli, Po. Ambadvet Ghotawade Road, Tal: Mulshi | Pune | 411042 | Maharashtra | India FS ED&I CSP West Team Alliance Controls Pvt Ltd Pune | Rohit Srivastav_Alliance Controls Pvt. Ltd | Alliance Controls Pvt. Ltd. (7966) | We visited at site and checked products as per below:1) XB5AD912R4K7: Head and potencialmeters with S/N: 32-2023-03-25 we haved checked and found c-terminal screw tightness issue 2)M9F43330: Multi9 , 30A D-curve 3pole MCB with S/N :AA-2022-w43-2 we have checked and found 4- phasepole open issue . ON/OFF operation found ok. screw tightness found ok.3) XPSBAC14AC:Harmony safety atomation safety module with s/N : 8B2307105676 and D.O.M.8B2023W07 we have checked and relay not opearating polarity not change. | Repair |  | 9- Service Validated | 2023-09-04 12:46 | VIP FSR= No 3. FSR Request: Unavailability of the preferred FSR, need to depute Non VIP FSR(Requester Name). =S= Consig Fill up 225994553 |  | 27 | INR | 27 | Industrial Automation Ops
WO-11158906 | 103512826 | 2023-08-25 10:55 | 2023-08-24 |  | 2023-08-24 16:27 | ATS22C41 | ATS22C41 | ATS22C41 | 882238226003 | ATS22 SSCR issue | 2023-08-24 | 2023-09-01 17:23 | No | Warranty | Geo Miller & Co. Pvt. Ltd. | C/o The Project Manager, Payjal-II Aish Bagh Water Works Campus Water Works RD null | Lucknow | 226001 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Aman Khare_Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found Soft starter having bypass contactor issue so we replaced. now soft starter working fine. | Repair |  | 9- Service Validated | 2023-09-01 17:27 |  |  | 12 | INR | 12 | Industrial Automation Ops
WO-11178233 | 103618750 | 2023-08-29 15:03 | 2023-08-29 |  | 2023-08-29 11:22 | ATV310HU15N4E | ATV310HU15N4E | ATV310HU15N4E | HL2241066301 | ATV320HU15N4E HL2241066301 NOT GETTING ON customer told wrong reference number earlier now updated in reasons | 2023-08-29 | 2023-09-02 12:28 | No | Warranty | Disposafe Health And Life Care Ltd | Sector - 59, Phase - II | Faridabad | 121004 | Haryana | India FS ED&I CSP North Team Saffron Automation Delhi | Yavnish Tyagi Saffron Automation Delhi | Saffron Automation(18001) | Check the drive and found drive physical condition is ok. Check the drive static test and found static test is not ok. So drive is faulty. We replace the faulty drive with new. E+N- 0.35V. Mail Id. utility@disposaser.com | Repair |  | 9- Service Validated | 2023-09-02 14:47 |  |  | 53 | INR | 53 | Industrial Automation Ops
WO-11178360 | 103618244 | 2023-08-30 14:25 | 2023-08-29 |  | 2023-08-29 12:04 | ATV310H075N4E | ATV310H075N4E | ATV310H075N4E | 8B2232609181 | Complaint for ATV310H075N4E 8B2232609181 | 2023-08-29 | 2023-09-04 16:04 | No | Warranty | Ratna Machines Pvt. Ltd | 235, Village, Koyla Faizullah Nagar, Rehpura Road | Rampur | 244927 | Uttar Pradesh | India FS ED&I CSP North Team Saffron Automation Delhi | Yavnish Tyagi Saffron Automation Delhi | Saffron Automation(18001) | Check the drive and found drive physical condition is ok. Give the input supply and found drive show F020 Fault. We replace the faulty drive with new. | Repair |  | 9- Service Validated | 2023-09-04 16:08 |  |  | 204 | INR | 204 | Industrial Automation Ops
WO-11178696 | 103619278 | 2023-08-29 15:43 | 2023-08-29 |  | 2023-08-29 13:59 | XB5AW33B1N | XB5AW33B1N | XB5AW33B1N |  | XB5AW33B1N 37 222312913 02-02-2023 Switching & Illuminated Issue XB5AW34B1N 16 222312913 02-02-2023 Switching & Illuminated Issue XB5AW34B2N 28 222312913 02-02-2023 Switching & Illuminated Issue XB5AW31B1N 12 222312913 02-02-2023 Switching & Illuminated Issue XB5AG21N 9 222312913 02-02-2023 Switching & Illuminated Issue XB5AS542N 4 222312913 02-02-2023 Switching & Illuminated Issue XB5AW35B1N 1 232402365 24-05-2023 Switching & Illuminated Issue XB5AA21N 9 222312913 02-02-2023 Switching & Illuminated Issue XB5AA31N 2 222312913 02-02-2023 Switching & Illuminated Issue ZBE101N 27 202109042 16-02-2023 Switching & Illuminated Issue ZBE102N 13 202109042 16-02-2023 Switching & Illuminated Issue XB5AD21N 1 222312913 02-02-2023 Switching & Illuminated Issue YSL Electronics No. 42, KHB Indl. Area Yelahanka Bangalore- 560064 Mr.Balappa Ph :8884169612 | 2023-08-29 | 2023-09-06 17:06 | No | Warranty | YSL Electronics | No 42, KHB Industrial Area Yelahanka New Town | Bangalore | 560064 | Karnataka | India FS ED&I CSP South Team PSK Power Controls Bangalore | Chethan SC P.S.K. POWER CONTROLS Bangalore | PSK Power Controls | Inspected and found below mentioned 1)Ref: XB5AW34B1N S/N: 1022503, 1022484 = 50 No'S, light not getting on, struckking issue and screw threading issue(Screw not opening). 2)Ref: XB5AW33B1N S/N:1023174, 1022476 = 48 No'S, caps are opened, some marks in the caps and button is very hard. 3) Ref: ZBV-B3N S/N:1022505 = 1 No's, not getting on 4) Ref: XB5AW3501N S/N:1022365 = 1 No, strucking issue. 5) Ref: XB5AW31B1N S/N:1022486 = 8 No'S, push button is very hard and not getting ON. 6) Ref: ZBV-B1N, S/N:1022365 = 1 No, not getting ON 7)Ref: XB5AG21N S/N:1022484 = 10 No'S, key's are comming out in on position instead in OFF position. 8)Ref: XB5AS542N = 6 No'S, emergency push button not operating 9)Ref:XB5AA21N = 9 No'S , push button is very hard. We took the photos and details of the products and we have given the warranty replacement for above mentioned after the confirmation from the Schneider FSE. | Repair |  | 9- Service Validated | 2023-09-06 17:07 | Material reference is in blocked in status ZBVB1N Rest all booked zfre in this work order Zvo : 226018431 |  | 30 | INR | 30 | Industrial Automation Ops
WO-11178711 | 103594253 | 2023-08-29 17:31 | 2023-08-29 |  | 2023-08-29 14:07 | ATV320U40N4C | ATV320U40N4C | ATV320U40N4C | HL2247840283 | Address AN-6, M.G.ROAD, PHASE-3, INDUSTRIAL AREA, DASNA, MASOORI 201001, GHAZIABAD Uttar Pradesh, India Attend Customer Complaint Urgently- SERVOKON SYSTEMS LIMITED (ATV320U40N4C- Serial no.- HL2247840283) | 2023-08-29 | 2023-09-01 18:18 | No | Warranty | SERVOKON SYSTEMS | AN-6, M.G.ROAD, PHASE-3, INDUSTRIAL AREA, DASNA, MASOORI null | GHAZIABAD | 201001 | Uttar Pradesh | India FS ED&I CSP North Team Saffron Automation Delhi | Deepak Pal_Saffron Automation Delhi | Saffron Automation(18001) | Check the drive and found drive static test is ok. After providing the input supply drive not show display. Drive is faulty. We replace the faulty drive with new. Mail Id. measales@maxgroup.co.in | Repair |  | 9- Service Validated | 2023-09-02 13:11 |  |  | 56 | INR | 56 | Industrial Automation Ops
WO-11181327 | 103629900 | 2023-08-31 12:15 | 2023-08-30 | We required panel wiring diagram & output connected Motor details + Breaking transister value from customer. | 2023-08-30 10:04 | ATV320U15N4C | ATV320U15N4C | ATV320U15N4C | HL2239735009 | DISPLAY NOT WORKING-1.5KW VFD ATV320U15N4C drive serial no. ? HL2303539047 | 2023-08-30 | 2023-09-05 15:20 | No | Warranty | Endurance MATERIAL Handlers Pvt. Ltd. | Endurance Material Handlers Pvt. Ltd., Gat No. 391, Dehu Alandi Road, Talawade Near Talawade Software Park, Pune | Pune | 411062 | Maharashtra | India FS ED&I CSP West Team Alliance Controls Pvt Ltd Pune | Shmabhu Bone_Alliance Controls Pvt. Ltd | Alliance Controls Pvt. Ltd. (7966) | 1) Visited on site & checked VFD in cold Test found in Reetifier section L1 , L2 , L3 is getting open with Respected to PA/+ Terminal & L1 & L2 is open with PC/- IGBT section OK wrt. PA/+ & PC/-.2) opened the drive & checked inside , found that IPM section in burnt condition .3)This VFD is used for LT Application . After 2 month of commissioning drive has been failed.4)We will be share all the data & Backup of drive , VFD's photoghraph's to schneider , for next action . | Repair |  | 9- Service Validated | 2023-09-05 15:21 | =S= Consig Fill up 226018996 |  | 13 | INR | 13 | Industrial Automation Ops
WO-11181369 | 103621520 | 2023-08-30 10:40 | 2023-08-30 | we have observed VFD display getting off in the running configuration, suspecting internal issue. customer having spare VFD and replaced new one. system is working ok. | 2023-08-30 10:29 | ATV12H037M2 | ATV12H037M2 | ATV12H037M2 | 8B220867073 | Service call ATV12H037M2 8B220867073 | 2023-08-30 | 2023-09-01 13:03 | No | Warranty | L & T DECCAN TOLLWAY LTD | C/O ARYA OMNITALK WIRELESS SOL TP - 02, NH-65, KAMKOLE MUNIPALLY | MEDAK | 502345 | Telangana | India FS ED&I CSP South Team ENERPRO ENGINEERING SOLUTIONS Vijayawada | Makineni Jayashankar ENERPRO ENGINEERING SOLUTIONS VIJAYAWADA | Enerpro Engineering Solutions - 500012682 | VFD Display not working. | Repair |  | 9- Service Validated | 2023-09-02 13:04 |  |  | 267 | INR | 267 | Industrial Automation Ops
WO-11182875 | 103631495 | 2023-08-30 12:52 | 2023-08-30 | we have inspected the VFD. VFD and related the DBR got failed. suspecting due to external issue it got failed. VFD in the store. Customer using all the Schneider switchgear and Automation. considering long view goodwill basis here we are providing replacement. | 2023-08-30 11:00 | ATV320U40N4C | ATV320U40N4C | ATV320U40N4C | 21HL2210702 | Complaint - ATV320U40N4C Serial No - 21HL2210702268 | 2023-08-30 | 2023-09-04 15:49 | No | Warranty | Pokarna Engineered Stone Limited | Survey No.910,Mekaguda Gram Panchayat,Nandigam Revenue Village and Mandal,Ranga Reddy District | Hyderabad | 509223 | Telangana | India FS ED&I CSP South Team ENERPRO ENGINEERING SOLUTIONS Vijayawada | ES Chowdary_ENERPRO ENGINEERING SOLUTIONS VIJAYAWADA | Enerpro Engineering Solutions - 500012682 | VFD Not working | Repair |  | 9- Service Validated | 2023-09-04 15:51 |  |  | 265 | INR | 265 | Industrial Automation Ops
WO-11183544 | 103653729 | 2023-08-30 19:49 | 2023-08-30 |  | 2023-08-30 15:37 | ABL8RPM24200 | ABL8RPM24200 | ABL8RPM24200 | W372022 | RE: Issue - Battery module, Case: 103513548, [ thread::c9Rg0DeAcdeHhNVtdzuiND4:: ] W372022 ABL8BPK24A12 | 2023-08-30 | 2023-09-19 16:06 | No | Warranty | CLIMAVENETA | No. 1105, Keerthi Pradhan Logistics Park, Belluru (V) Narasapur Hobli, | Kolar | 563133 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | MANOJ GANESAN SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | We had visied the site and checked the customer reported Battery module,Found customer returned from mumbai site to panel manufacturer,There is no option to charge battery in builder place,Measured voltage was 11 VDC out of 24 VDC.So we booked ZVO directly to customer because no option and no provision to check charging. | Repair |  | 9- Service Validated | 2023-09-19 22:14 |  |  | 52 | INR | 52 | Industrial Automation Ops
WO-11188312 | 103693095 | 2023-08-31 17:12 | 2023-08-31 |  | 2023-08-31 16:42 | ATV340D22N4 | ATV340D22N4 | ATV340D22N4 | 40 48600HL220379059 | Product : ATV340D22N4 Ser. No. : 4048600HL220379059 Problem : No display Customer : Cranetech Equipments, Plot no. : 1110/B, GIDC, Phase ? 3, Vatva, Near Kalupur bank, Ahmedabad-382445, GUJARAT, INDIA. Contact Person : Mr. Nitin Solanki - 9925002119 | 2023-08-31 | 2023-09-01 15:14 | No | Warranty | cranetech equipments | Plot no. 1110/B, phase-III, Near Kalupur bank, GIDC, Vatva | Ahmedabad | 383445 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Mohammad Aasif Anik Engineering Ahmedabad | Anik Engineering (554) | check the above drive physically observed ok. check the igbt and rectifier l1 and l3 open with pc . check the runtime 8030858 ontime 31277441 acc=3.0 sec, dcc = 3.0sec, fault undervoltage inf7, please give enduser detils for furher action. open the drive for primary inspection but flashing observed at dc bus sheet. ATV310HU22N4E SR NO 8B2248198278 V1.5IE02 physcially osberved ok. check the igbt and rectifer but input open with pa+ and output open with pa+. check the runtime 0.25, ontime 1.17 So doubt of benefit free replacement for customer satisfaction. | Repair |  | 9- Service Validated | 2023-09-01 15:14 | =S= Consig Fill up 226022731 |  | 10 | INR | 10 | Industrial Automation Ops
WO-11194723 | 103724026 | 2023-09-02 13:06 | 2023-09-01 |  | 2023-09-01 14:39 | BMXP342020H | BMXP342020H | BMXP342020H | 21224900779 | BMXP342020H 21224900779 DALIP VERMA: 9917464026 dalip1.verma@gmail.com | 2023-09-01 | 2023-09-14 11:59 | No | Warranty | D.S.G. PAPER PVT. LTD. | 7957/5, Ranbir Marg, Model Town GSTIN: 03AACCD1450A1ZN | Patiala | 147001 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the plc processor found not communicate with ethernet and try to reset but not working. Hence faulty replaced. BMXP342020H - 1 Nos. email : dalip1.verma@rediffmail.com | Repair |  | 9- Service Validated | 2023-09-14 12:12 |  |  | 110 | INR | 110 | Industrial Automation Ops
WO-11195226 | 103721399 | 2023-09-02 12:11 | 2023-09-01 | As per discussion with Mr.kiran borse sir this drive is needed to be replaced . | 2023-09-01 17:06 | ATV320D11N4C | ATV320D11N4C | ATV320D11N4C | HL2325588060 | Complaint for ATV320D11N4C Sr No-(21) HL2325588060 | 2023-09-01 | 2023-09-05 15:08 | No | Warranty | SHRINIVAS NANDKISHOR PUROHIT HUF | SECTOR D, PLOT NO-24, PHASE II, SHRI LAXMI SAHAKARI AUDYOGIK VASAHAT, HATKANANGALE null | Kolhapur | 416115 | Maharashtra | India FS ED&I CSP West Team Alliance Controls Pvt Ltd Pune | Shmabhu Bone_Alliance Controls Pvt. Ltd | Alliance Controls Pvt. Ltd. (7966) | (1) Visited on site and as per reported problem by customer checked VFD in cold test found it's rectifier and IGBT section found OK with respected to PA+ and PC-. (2) Applied 415VAC to drive input and checked drive display to show the SCF3 fault. (3) We applied somove software and backup to the drive. (4) We get factory reset on drive & drive display show SCF3 fault . (5) We off the drive power source and open the drive & checked burnt mark in drive , therefore no any burnt mark show in drive parts.(6)Problem occured during testing . Replacement booked at brisk Electronics Pune. product - ATV320D11N4C , Qty - 01 Drive Dispatched by Flexi- 17188 | Repair |  | 9- Service Validated | 2023-09-05 15:09 | =S= Consig Fill up 226023043 |  | 302 | INR | 302 | Industrial Automation Ops
WO-11195285 | 103728668 | 2023-09-02 11:02 | 2023-09-01 |  | 2023-09-01 17:45 | ATS22D75Q | ATS22D75Q | ATS22D75Q | 8B230682208 | ATS22D75Q 606480167225 8B2306822081 TRIPPING ISSUE GANGA WATER SIDHARTH VIHAR SEC 8 CWR AWAS VIKASH 9891841131 RAM PRAKASH ajaydhama67@gmail.com | 2023-09-01 | 2023-09-02 13:10 | No | Warranty | Ganga water plant | siddartha vihar , nearby vijay nagar | Ghaziabad | 201009 | Uttar Pradesh | India FS ED&I CSP North Team Saffron Automation Delhi | Deepak Pal_Saffron Automation Delhi | Saffron Automation(18001) | Check the soft starter and found after input supply starter power up and ready. Give run command found starter trip or SCF fault. Check the parameter and found customer didn't program. We program the starter and run successfully. We suggest to customer for program support please co-ordinate with panel builder. | Repair |  | 9- Service Validated | 2023-09-02 17:29 |  |  | 38 | INR | 38 | Industrial Automation Ops
WO-11200505 | 103621890 | 2023-09-02 12:00 | 2023-09-02 |  | 2023-09-02 11:30 | ABL2REM24045K | ABL2REM24045K | ABL2REM24045K | 8a2022w166161b00687904332 | genuine (r m panel) ABL2REM24045K 8a2022w166161b00687904332 | 2023-09-02 | 2023-09-02 14:40 | No | Warranty | Genuine X-Ray & Radiological Equipment Private Limited | Tin Number Radhe industrial Estate 497 Tajpur Road Sakhej Bavla High way changodar | Changodar | 382213 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Mistri Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physically observed ok. ABL2REM24045K SR NO : 8A22W16461 , 8A2022W16461 , -3 Nos smps observed box are damaged due to moisture and observed corrosion on smps body. customer give supply and spark obseved on smps terminal we open the smps and checked the pcb corrosion only metalic pant. we give supply voltage 220 vac and checked the output voltage 24.17vdc observed ok. according to customer afte sometime smps getting on off and led light glow. so avoid the warranty. | Repair |  | 9- Service Validated | 2023-09-02 14:40 |  |  | 40 | INR | 40 | Industrial Automation Ops
WO-11200655 | 103727886 | 2023-09-02 14:44 | 2023-09-02 |  | 2023-09-02 14:10 | ATV610D55N4 | ATV610D55N4 | ATV610D55N4 | 4001400JM230705 | COMPLAINT BOOK FOR -ATV610D55N4- 4001400JM230705846SERVILINK SYSTEM LTD | 2023-09-02 | 2023-09-04 12:04 | No | Warranty | Servilink Systems Ltd. | PLOT NO.151A & B, Ratnakar Park, New GIDC POR, Ramangamdi, N.H.8 null | Vadodara | 391243 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Mistri Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physically osberved ok,. check the igbt and rectifier section ok. but l1 phase terminal burnt observed customer use pin type lug for input and output . open the drive for primary inspection but only l1 phase burnt obsered. check the runtime 5.6h, ontime 29.5h, no of starts 140 times. l1 phase burnt due to local heating so avoid the warranty so no free replacement. no any product problem observed. | Repair |  | 9- Service Validated | 2023-09-04 12:05 |  |  | 125 | INR | 125 | Industrial Automation Ops
WO-11200707 | 103742474 | 2023-09-02 17:13 | 2023-09-02 | We have collected the Servo drive details and observed the drive display not coming. we have provided the replacment. | 2023-09-02 15:49 | LXM26DU15M3X | LXM26DU15M3X | LXM26DU15M3X | P158AF391700583 | RE: Complaint -SVP Ganesh Food Products LXM26DU15M3X P158AF391700583 [ thread::OLNxx610eoudm5DGBCl5AT4:: ] | 2023-09-02 | 2023-09-06 17:02 | No | Warranty | SRI GANESH INDUSTRIES | PLOT 15 , TAJ NAGAR, NEAR VINAYAKA NAGAR, KADAPA | KADAPA | 516001 | Andhra Pradesh | India FS ED&I CSP South Team ENERPRO ENGINEERING SOLUTIONS Vijayawada | Makineni Jayashankar ENERPRO ENGINEERING SOLUTIONS VIJAYAWADA | Enerpro Engineering Solutions - 500012682 | SERVO DRIVE NOT WORKING | Repair |  | 9- Service Validated | 2023-09-07 05:03 |  |  | 265 | INR | 265 | Industrial Automation Ops
WO-11200793 | 103742370 | 2023-09-05 16:12 | 2023-09-02 |  | 2023-09-02 17:49 | ATV320U22N4C | ATV320U22N4C | ATV320U22N4C | HL2113561154 | Faulty Drive SDP Machines Sr-ATV320U22N4C Sr. No. - HL2113561154 | 2023-09-02 | 2023-09-12 16:48 | No | Warranty | SDP Machine tools | ajayser road kajipura | AJMER | 305005 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | checked the Vfd found display not showing , hence faulty replaced . ATV320U22N4C - 1 nos Email : | Repair |  | 9- Service Validated | 2023-09-12 16:52 |  |  | 160 | INR | 160 | Industrial Automation Ops
WO-11208882 | 103705949 | 2023-09-04 11:38 | 2023-09-04 |  | 2023-09-04 10:20 | ATV320U40N4C | ATV320U40N4C | ATV320U40N4C | HL2135753023 | VFD Not Getting ON ATV320U40N4C - 1 No Serial No : HL2135753023 | 2023-09-04 | 2023-09-07 11:05 | No | Warranty | V S Granites | Sy.No 79/4 Devagana Halli Kundana Hobli Devana Halli | Bangalore | 562110 | Karnataka | India FS ED&I CSP South Team Vamtech Energy Solutions Private Limited Bengaluru | BalaMurugan Venkadaswamy Vamtech Energy Solutions Private Limited Bengaluru | VAMTECH Energy Solutions (P) Limited | being visited site drive is not working its showing error and requesting for new drive email id:madeenaelectricals786@gmail.com | Repair |  | 9- Service Validated | 2023-09-08 11:15 |  |  | 50 | INR | 50 | Industrial Automation Ops
WO-11208877 | 103698750 | 2023-09-04 10:48 | 2023-09-04 |  | 2023-09-04 10:16 | ATV320U75N4C | ATV320U75N4C | ATV320U75N4C | HL2239700047 | Comaplint - VW3A3607 Steer Engineering HL2239700047 ATV320U75N4C | 2023-09-04 | 2023-09-07 16:00 | No | Warranty | PAC systems and solutions (Pooja power controls) | NO : 371 & 372, 1ST Floor, 10th Cross Road, 4th Phase, Peenya Industrial Area, Bangalore | Bangalore | 560058 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Mohammad Riyaz_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site- pooja power products, checked the customer reported drive the problem found was error ILF comes, we removed and checked the option card in other drive, same ILF error repeats. So we had booked the option card directly to pooja power products. | Repair |  | 9- Service Validated | 2023-09-07 18:55 |  |  | 30 | INR | 30 | Industrial Automation Ops
WO-11209515 | 103753787 | 2023-09-04 16:23 | 2023-09-04 |  | 2023-09-04 10:39 | ATV310HU22N4E | ATV310HU22N4E | ATV310HU22N4E | 8B2308343109 | Complaint 09-04 ATV310HU22N4E Serial No. 8B2308343109 | 2023-09-04 | 2023-09-04 16:35 | No | Warranty | SONI ELECTRICAL & ELECTRONICS(13431) | 5,GURU NANAK MARKET FOCAL POINT NEAR UPPER INDIA STEELS | Ludhiana | 141001 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | checked the vfd found internally flash. Hence faulty, replaced. ATV310HU22N4E - 1 Nos. Email : id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-05 11:24 |  |  | 25 | INR | 25 | Industrial Automation Ops
WO-11210298 | 103746829 | 2023-09-04 10:59 | 2023-09-04 |  | 2023-09-04 10:51 | ATV320U55N4C | ATV320U55N4C | ATV320U55N4C |  | Product : ATV320U55N4C Ser. No. : HL2243783130 Problem : No display Customer : RAJPUROHIT ENGINEERS, Shed No- 2708/A/1 Near Shree Ram Ice Factory, Beside Gayatri Weigh Bridge, Phase IV, GIDC Estate, Vatva, Ahmedabad 382445, Contact Person : Mr. Nitin Solanki - 9925002119. | 2023-09-04 | 2023-09-04 16:30 | No | Warranty | RAJPUROHITENGINEERS | Shed No- 2708/A/1 Near Shree Ram Ice Factory, Beside Gayatri Weigh Bridge, Phase IV, GIDC Estate, Vatva, null | Ahmedabad | 382445 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Mistri Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physically observed ok. ATV320U55N4C SR NO : HL22437831305.5KW, v3.5ie46, Observed as per customer drive no display so we checked recfitier section ok.. so we checked igbt section found output l2 phase short. so we open the drive for primary analysis no any flashing observed. sowe checked runtime 495m, powerontime 2355h acc 0.5 so we checked fault history 4 times igbt short ckt 4 times motot short ckt . customer using the drive hoising application bring . as per customer motor ok. so free replacement for customer satisfaction. | Repair |  | 9- Service Validated | 2023-09-04 16:30 | =S= Consig Fill up 226019083 |  | 10 | INR | 10 | Industrial Automation Ops
WO-11211057 | 103759552 | 2023-09-05 10:45 | 2023-09-04 |  | 2023-09-04 13:48 | ATV610D22N4 | ATV610D22N4 | ATV610D22N4 | 4001000JM230401744 | Drive display issue ATV610D22N4 , Serial No:- 4001000JM230401744 | 2023-09-04 | 2023-09-12 10:31 | No | Warranty | Polyplex Corporation Ltd | Lohia Head Road Village Amau District- Udham Singh Nagar | Khatima | 262308 | Uttarakhand | India FS ED&I CSP North Team Saffron Automation Delhi | Deepak Pal_Saffron Automation Delhi | Saffron Automation(18001) | Check the drive and and found drive is power up and working is ok, But drive HMI display is not working. We replace the faulty HMI with new. Mail Id. khtssu1@polyplex.com | Repair |  | 9- Service Validated | 2023-09-13 10:03 |  |  | 306 | INR | 306 | Industrial Automation Ops
WO-11211090 | 103758536 | 2023-09-06 10:55 | 2023-09-04 |  | 2023-09-04 13:54 | ATV310HU40N4E | ATV310HU40N4E | ATV310HU40N4E | 8B2229490253 | Replacement of AC Drive ATV310HU40N4E-4.0 kW (5.0 HP) ATV310HU40N4E 8B2229490253 | 2023-09-04 | 2023-09-13 14:10 | No | Warranty | Super Electricals | Super Electricals Opposite Tata Motors Kelwa District Rasabndh Rajasthan Pincode :-- 313334 | Rajsamand | 313334 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | Checked the vfd found not power up, Hence faulty replaced. ATV310HU40N4E - 1 nos Email : | Repair |  | 9- Service Validated | 2023-09-13 16:22 |  |  | 330 | INR | 330 | Industrial Automation Ops
WO-11211127 | 103759976 | 2023-09-05 11:03 | 2023-09-04 |  | 2023-09-04 14:15 | ATV310HU22N4E | ATV310HU22N4E | ATV310HU22N4E | 8B2235093042 | ATV310HU22N4E, 8B2235093042, Not Powering on, | 2023-09-04 | 2023-09-05 12:30 | No | Warranty | Natural Food chain | Sanpera | Sonipat | 131039 | Haryana | India FS ED&I CSP North Team Saffron Automation Delhi | Yavnish Tyagi Saffron Automation Delhi | Saffron Automation(18001) | Check the drive and found drive static test is ok, after provide the input supply and found drive is power up and show ready. Rotate the joy dial only up and down and REF and 800 Code. We replace the faulty drive with new. | Repair |  | 9- Service Validated | 2023-09-07 08:38 |  |  | 79 | INR | 79 | Industrial Automation Ops
WO-11211236 | 103755020 | 2023-09-04 15:37 | 2023-09-04 | Hence, This site is closed as no product related issue on site. | 2023-09-04 14:58 | ATS480C59Y | ATS480C59Y | ATS480C59Y | WX23103AA274001 | COMPLAINT: Soft Starter Working Issue @ Godrej Agrovet Ltd - ATS480C59Y. WX23103AA274001 | 2023-09-04 | 2023-09-04 18:30 | No | Warranty | Godrej Agrovet Limited | E-1/4/2, Near Bharat Forge,MIDC, Baramati null | Pune | 413133 | Maharashtra | India FS ED&I CSP West Team Alliance Controls Pvt Ltd Pune | Rohit Srivastav_Alliance Controls Pvt. Ltd | Alliance Controls Pvt. Ltd. (7966) | We visited at site and discussed with customer and taken proper shutdown .(1) We have checked cold test and found Ok.(2) We have checked continuty with Earthing I/P and O/P and observed O/P section 73/C2 terminal getting continuty with panel body earthing .(3) We have removed one by one connecton and checked it that we found Nut near B-phase it may cause during Busbar connection or Motor cable connection . We removed nut and assembled again and taken trial with small motor found Ok & Working Fine.(Siemens make motor , 22kw , 415VD , 40A , 1465rpm , 50HZ)(4) Taken trial with earthing motor .(siemens make motor, 250KW , 448A , 991rpm , 415VD , 50HZ ) and found O/P voltage and O/P current found Balanced ..(5) Hence, This site is closed as no product related issue on site. | Repair |  | 9- Service Validated | 2023-09-05 11:55 |  |  | 116 | INR | 116 | Industrial Automation Ops
WO-11211368 | 103765643 | 2023-09-05 11:10 | 2023-09-04 | We have inspected the VFD During the cold test, VFD Input section in unhealthy position. We have connected the external 24VDC to the VFD Control card and collected the data As per the VFD Error data_ VFD got a Ground short circuit @ 2/9/2023 15:36 We have measured the voltage at Ground to body: 0.188V We have collected all required details and forwarding to the SE technical team. As early as possible we will update you. | 2023-09-04 15:55 | ATV930D18N4 | ATV930D18N4 | ATV930D18N4 | 4023100JM221203339 | ATV930D18N4 4023100JM221203339 Qty:1 P: Not Powering up M/S GLOSTER CABLES LIMITED (GCL) 5-3-372A 2ND FLOOR RASHTRAPATI RD HYDER BASTI SECUNDERABAD TELANGANA 500003 Krishna 8374075805 tarun@coronet.in | 2023-09-04 | 2023-09-06 12:47 | No | Warranty | GLOSTER CABLES LIMITED (GCL) | 5-3-372A, 2ND FLOOR, RASHTRAPATI RD, HYDER BASTI, SECUNDERABAD | SECUNDERABAD | 500003 | Telangana | India FS ED&I CSP South Team ENERPRO ENGINEERING SOLUTIONS Vijayawada | Makineni Jayashankar ENERPRO ENGINEERING SOLUTIONS VIJAYAWADA | Enerpro Engineering Solutions - 500012682 | VFD NOT WORKING | Repair |  | 9- Service Validated | 2023-09-06 12:50 |  |  | 232 | INR | 232 | Industrial Automation Ops
WO-11211721 | 103766488 | 2023-09-05 14:58 | 2023-09-04 |  | 2023-09-04 17:42 | TM241CEC24U | TM241CEC24U | TM241CEC24U | 8B23040001867 | RE: Complaint 07-02, Case: 102159356, [ thread::H9HlzSvPeCeixCmz-HrjSj4:: ] TM241CEC24U Serial No. 8B23040001867 | 2023-09-04 | 2023-09-09 11:55 | No | Warranty | D.S.G. PAPER PVT. LTD. | 7957/5, Ranbir Marg, Model Town GSTIN: 03AACCD1450A1ZN | Patiala | 147001 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | checked the plc found not power up. hence faulty, replaced. TM241CEC24U - 1 Nos. Email: id not provided by the customer | Repair |  | 9- Service Validated | 2023-09-09 11:57 |  |  | 120 | INR | 120 | Industrial Automation Ops
WO-11211746 | 103766636 | 2023-09-04 18:03 | 2023-09-04 |  | 2023-09-04 17:51 | ATV310HD15N4E | ATV310HD15N4E | ATV310HD15N4E | 882234371025 | RE: VFD 310 issueM/S Vetfar Pharmaceuticals Private Limited, Plot No K-37, Midc Tarapur, Kalode Naka, - Boisar, Boisar, Palghar, Maharashtra, 401506 Site person name and contact details. Vipul Patil : 8698712284 | 2023-09-04 | 2023-09-06 14:14 | No | Warranty | Vetfar Pharmaceutical | Plot k37, Bachu Bhai Dube Industrial Estate | Palghar | 401506 | Maharashtra | India FS ED&I CSP West Team R P Electrical Mumbai | Digambar Vishe R P Electrical Mumbai | R P Electrical | Checked ATV310HD15N4E for drive not working also display was blank. took thyristor test found Not oK. Dis-assemble the drive to check internally found components burnt on power board also impact can be seen on IGBT. braking resistor connected was heated then the drive display was showing and drive not work as per customer. Also checked and found the braking resistor cable burnt and insulation melt suspect loose connection. As the drive found burnt warranty has been void. | Repair |  | 9- Service Validated | 2023-09-06 14:21 |  |  | 92 | INR | 92 | Industrial Automation Ops
WO-11213612 | 103767515 | 2023-09-05 14:28 | 2023-09-05 |  | 2023-09-05 09:45 | ATV340D18N4E | ATV340D18N4E | ATV340D18N4E | HL221795053 | Repeat issue KINDLY DO NEEDFUL AS OUR EFFLUENT LOAD IS HUGE FOR PROCESS. Following is the Factory address: Shrivinayak Chemex Pvt Ltd. Plot no. T-11 MIDC Boisar-401506 Mob.no.: 9860497544 | 2023-09-05 | 2023-09-13 14:59 | No | Warranty | Shrivinayak Chemex Pvt Ltd. | Plot No. T-11, MIDC, Tarapur | Boisar | 401506 | Maharashtra | India FS ED&I CSP West Team R P Electrical Mumbai | Digambar Vishe R P Electrical Mumbai | R P Electrical | Checked ATV340D18N4E for showing internal error 21. Checked drive thoroughly 2 times earlier as well. The error get reset but shown again after a day or two. Opened the drive to checked internally but No physically damage can be seen. Assembel the drive then given supply drive run properly. for 4-5 times then again the error was shown. Power cables and communication cables have different path. Drive need to be replace. 2) In 2nd visit replace the drive. Now Took operation found working Ok. | Repair |  | 9- Service Validated | 2023-09-13 15:01 | =S= Consig Fill up 226031618 |  | 90 | INR | 90 | Industrial Automation Ops
WO-11213663 | 103769529 | 2023-09-06 11:59 | 2023-09-05 |  | 2023-09-05 10:18 | ATV930D15N4 | ATV930D15N4 | ATV930D15N4 | 4023000JM223501430 | Complain for faulty VFD at JSPL, Punjipathra Warranty Model No. ? ATV930D15N4 Serial no. ? 4023000JM223501430 Issue:VFD display is not switched On when Power up to drive Customer Name ? M/s Jindal Steel PVt Ltd Location ? Jindal Industrial Park, Punjipathra, Raigarh Contact Person ? Mr. Sudip Sain Contact No ? 9109122331 | 2023-09-05 | 2023-09-20 12:00 | No | Warranty | Jindal Steel & Power Ltd. | Plot No-201-204, Steel Structural Division, Jindal Industrial Park, Punjipatra null | Raigarh | 496109 | chhattisgarh | India FS ED&I CSP East Team SOMDEV & COMPANY RAIPUR | SOUMYA BEHERA_SOMDEV & COMPANY RAIPUR | Somdev & Company | the vfd is not workimng so we replace the same. | Repair |  | 9- Service Validated | 2023-09-21 11:07 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 311 | INR | 311 | Industrial Automation Ops
WO-11213679 | 103780478 | 2023-09-06 16:05 | 2023-09-05 |  | 2023-09-05 10:30 | ATV930C13N4C | ATV930C13N4C | ATV930C13N4C | 4031000N22204005 | Re: Fw: schneider altivar 930 service regarding [ thread::7-krSa0Cc86DntdxOKmj1T4:: ] ATV930C13N4C SNO. : 4031000N2220400548 | 2023-09-05 | 2023-09-06 16:10 | No | Warranty | Udaipur mineral Development Syndicate | Golcha Group Near Railway station | DAUSA | 303303 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | Checked the vfd found Terminal burnt due to loose termination and vfd found out of warranty from serial number Hence no replacement given to customer. Email : id not provided by customer. | Repair |  | 9- Service Validated | 2023-09-07 15:30 |  |  | 65 | INR | 65 | Industrial Automation Ops
WO-11215811 | 103788701 | 2023-09-06 11:11 | 2023-09-05 |  | 2023-09-05 14:08 | ATS22C41 | ATS22C41 | ATS22C41 | 882238226003 | Site person contact detai : Mr B D Manna ( Mob 7407027401, 8172064619) Site address:. M/s Geo Miller & Co. Pvt. Ltd. C/o The Project Manager, Payjal-II Aish Bagh Water Works Campus Water Works RD, Lucknow , U.P.226004 repeat issue | 2023-09-05 | 2023-09-06 17:31 | No | Warranty | Geo Miller & Co. Pvt. Ltd. | C/O The Executive Engineer Lakshmi Taal Pariyogna, Hazaribagh Paudhsala 26 MLD STP, Badagaon Darwaja Dahar, Dhimariyana, | Jhansi | 284001 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Abhishek Patel Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | Checked and found soft starter having bypass contactor stuck, so we remove , now soft starter working fine. | Repair |  | 9- Service Validated | 2023-09-06 17:36 |  |  | 330 | INR | 330 | Industrial Automation Ops
WO-11216063 | 103785636 | 2023-09-08 14:19 | 2023-09-05 |  | 2023-09-05 15:28 | ATV930D15N4 | ATV930D15N4 | ATV930D15N4 | JM214305981 | SCHNEIDER MAKE VFD ATV930D15N4 JM214305981 | 2023-09-05 | 2023-09-11 13:14 | No | Warranty | SIWANSH AGRO INDUSTRIES | 1121, DP, 1401, 1509 Rice Maniana Rd, Tohana, | FATEHABAD | 125120 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Ram Ashish Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the VFD found EEPROM Control fault, display showing. Hence faulty replaced. VX4BT900200 - 1 Nos. VX4B900100 - 1 Nos. email : id not provided by the customer. | Repair |  | 9- Service Validated | 2023-09-11 13:19 |  |  | 165 | INR | 165 | Industrial Automation Ops
WO-11216073 | 103783668 | 2023-09-06 11:03 | 2023-09-05 |  | 2023-09-05 15:35 | ATV310HU55N4E | ATV310HU55N4E | ATV310HU55N4E | 8B22030970 | Schneider Drive ATV 310 not working ATV310HU55N4E (5.5 KW) S No :- 8B2203097043 | 2023-09-05 | 2023-09-13 16:20 | No | Warranty | M.G. Contractors | Fabrication Unit Ambala Badhauli Camp,Kalpi-Naraingarh Road Near E-max College | Ambala | 134003 | Haryana | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Ram Ashish Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the vfd found internally burnt & its DVR also found damaged. Hence faulty replaced. ATV310HU55N4E - 1 Nos. email : harjitsingh.singh1989@gmail.com | Repair |  | 8- Service Completed | 2023-09-16 16:24 |  |  | 51 | INR | 51 | Industrial Automation Ops
WO-11216084 | 103792259 | 2023-09-05 17:50 | 2023-09-05 |  | 2023-09-05 15:42 | ATV340D18N4 | ATV340D18N4 | ATV340D18N4 |  | Approved by Abhishek Saxena ATV340D18N4 Qty: 1 P: INF 8 ERROR DISPLAYING IN THE DRIVE WHEN POWERING ON INNOVATEC SYSTEMS Sree Annapoorna 75 E Arokiasamy Rd R.S. Puram Coimbatore, Tamil Nadu 641002. Mr. Asarudin 7358024116 | 2023-09-05 | 2023-09-05 17:55 | No | Warranty | INNOVATEC SYSTEMS | Sree Annapoorna 75 E Arokiasamy Rd R.S. Puram | Coimbatore | 641002 | Tamil Nadu | India FS ED&I CSP South Team Power Pro Engineering Services Coimbatore | KV ARUNKUMAR_POWER PRO ENGINEERIG SERVICES COIMBATORE | Powerpro Engineering Services | we have visited the site and inspected we found vfd INF8 fault to power issue sice the product is OW so we cannot provided the free replacement for this | Repair |  | 9- Service Validated | 2023-09-05 17:56 |  |  | 0 | INR | 0 | Industrial Automation Ops
WO-11216308 | 103786344 | 2023-09-07 14:12 | 2023-09-05 |  | 2023-09-05 17:29 | ATV930D45N4 | ATV930D45N4 | ATV930D45N4 | JM223400410) | Attend Customer Complaint Urgently- M/s Triveni engineering (ATV930D45N4 SR. NO.-JM223400410) | 2023-09-05 | 2023-09-07 14:14 | No | Warranty | Triveni engineering | CETP Plant 4, Punayata, Pali null | Pali | 306401 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | Checked the vfd found working ok. Email : id not provided by customer . | Repair |  | 9- Service Validated | 2023-09-07 15:34 |  |  | 305 | INR | 305 | Industrial Automation Ops
WO-11216355 | 103783639 | 2023-09-05 18:11 | 2023-09-05 |  | 2023-09-05 17:56 | ATS22C11Q | ATS22C11Q | ATS22C11Q | 8B221326510 | Re: Phase Electricals- Complain- ATS22C11Q 8B2213265100 - Under Warranty, Case: 102597485, [ thread::OxNJ3ydEfD-yWNi6BDAU3T4:: ] | 2023-09-05 | 2023-09-07 17:10 | No | Warranty | Pandesara Infra Structure Ltd. | Tirupati Circle SachinMagdalla State Highway Vadod Village Pandesara | Surat | 394150 | Gujarat | India FS ED&I CSP West Team SHIV SAI ELECTRICALS Vapi | SHIVAM LAD SHIV SAI ELECTRICALS VAPI | shivsai electricals | AS PER SITE VISIT WE CHECK THE PRODUC OK ON VISUAL INSPECTION.DURNING CONTROL POWER SUPPLY OFF CONDITION OK.WE CONCLUDE ATS22C11Q AS HARDWAER HAS NO ISSUE.AFTER THAT NO SCNIEDER PRODUCT ISSUE.SO WE CLOSED THE CASE. | Repair |  | 9- Service Validated | 2023-09-07 17:12 |  |  | 141 | INR | 141 | Industrial Automation Ops
WO-11219330 | 103813024 | 2023-09-06 17:26 | 2023-09-06 |  | 2023-09-06 10:27 | ATV340U15N4E | ATV340U15N4E | ATV340U15N4E | 4049300HL231661014 | REQUEST FOR ON-SITE COMPLAINT REPAIR / REPLACEMENT AGAINST FAULTY DRIVE ATV340U15N4E 4049300HL231661014 | 2023-09-06 | 2023-09-08 17:33 | No | Warranty | AMT TECHNO | 23, Durga Industrial Estate, Near Jain Temple, NH-08, Sankarda, | VADODARA | 391350 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Nijesh Patel_Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physically observed ok. check the igbt and rectifer section observed ok. we give supply 3 display getting on but inf6 observed. we open the drive for visual inspection observed ok. and clean redbar connect and connect. after we again 3 supply observed infl error 26 we offf the supply and on the supply agian infm ( observed ( internal error 22 ) one again off the supply and wait after on the supply ( internal error 22 ) for customer satisfaction free replacement | Repair |  | 9- Service Validated | 2023-09-08 17:34 | =S= Consig Fill up 226023548 |  | 125 | INR | 125 | Industrial Automation Ops
WO-11221271 | 103815484 | 2023-09-06 12:41 | 2023-09-06 | We founded VFD is showing F031 Error. we have tried for the factory reset.. VDF is not responding through keypad. replaced the new VFD. | 2023-09-06 12:13 | ATV310H075N4E | ATV310H075N4E | ATV310H075N4E | 8B2241445051 | ATV310H075N4E, 8B2241445051, F031 error continuous factory reset is not possible. | 2023-09-06 | 2023-09-11 13:21 | No | Warranty | Signode India Ltd | Rudraram village, Patancheru Mandal, Sangareddy Dist | Rudraram village | 5032329 | Telangana | India FS ED&I CSP South Team ENERPRO ENGINEERING SOLUTIONS Vijayawada | Makineni Jayashankar ENERPRO ENGINEERING SOLUTIONS VIJAYAWADA | Enerpro Engineering Solutions - 500012682 | VFD NOT WORKING | Repair |  | 9- Service Validated | 2023-09-11 13:23 |  |  | 232 | INR | 232 | Industrial Automation Ops
WO-11221613 | 103817465 | 2023-09-06 17:01 | 2023-09-06 |  | 2023-09-06 14:01 | XB5AW33B5 | XB5AW33B5 | XB5AW33B5 |  | Item : XB5AW33B5 SO: 300790328 Qty: 1 no issue : lens has broken , Quality issue. Purushotham P : Cell : +91 9591211666 SITE Address : WIRTZ MANUFACTURING INDIA PVT LTD PLOT 164, SY NO. 129 & 240 KIADB INDUSTRIAL AREA, JIGANI LINK ROAD BOMMASANDRA, BANGALORE, KARNATAKA -560105 | 2023-09-06 | 2023-09-13 13:18 | No | Warranty | Wirtz Manufacturing India Pvt Ltd | Plot No 164, Kiadb Industrial Area Bommasandra ?Jigani Link Road null | Bangalore | 560105 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | C Gunasekaran_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported illuminated push button, the problem found was cap came out from the push button. Customer purchased 11 out of that 4nos came out. Customer requested to replace the remaining 7nos on goodwill basis, to avoid future failure. So we arranged for the replacement and after replacing found working ok. | Repair |  | 9- Service Validated | 2023-09-13 13:39 |  |  | 30 | INR | 30 | Industrial Automation Ops
WO-11221632 | 103814359 | 2023-09-06 17:34 | 2023-09-06 | Visited site at 11/09/2023 but No any concern person at site. so talk with Mr sharma ji ,( AP INDUSTRY ) After customer confrim site will be visited. so we close the case. | 2023-09-06 14:06 | ATV930D30N4 | ATV930D30N4 | ATV930D30N4 | 4023300JM214604120 | COMPLAINT NO REQUIRED # ?ATV930D30N4 SERIAL NO # 4023300JM214604120 | 2023-09-06 | 2023-09-11 14:32 | No | Warranty | Dinesh Chandra R Agrawal infracon | 2nd & 4th Floor, 1, Sardar Patel Ring Rd | Ahmedabad | 382440 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Nijesh Patel_Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physically observed ok. check the igbt and rectifier section ok. powerup the drive and check the parameter and install the motor name plate parameter. and trial taken and when give a stop command crane move reverse and forward slightly runtime 99.3h, number of stats = 10340. take a somove and dbr photograph . customer use this drive for long travelling operation with four motor. as per talk with mr dipak patel and change the parameter motor control type svuv and check with warranty . then trial taken working but problem remain same. DBR 16.2 9.3KW, change the motor control type . then trial taken working but problem remain same. so as per my observation no problem in drive problem due to motor or extended. so suggested to customer and please check the motor and revert back. | Repair |  | 9- Service Validated | 2023-09-11 14:33 |  |  | 0 | INR | 0 | Industrial Automation Ops
WO-11223648 | 103847069 | 2023-09-07 15:04 | 2023-09-07 |  | 2023-09-07 10:42 | VZ3N1321 | VZ3N1321 | VZ3N1321 |  | Approval by Abhishek Saxena ATV630C25N4 Qty:1 P: Drive issue @arunt please book the ZVO for VZ3N1321 approval mail sent to you AIA ENGINEERING Ltd K2 Kerala Unit 103/104/115 to 118,Kerala GIDC Estate Taluka Bavala,Kerala,Gujarat 382240 Contact :- hithaishi 8951802146. | 2023-09-07 | 2023-09-25 15:22 | No | Warranty | AIA Engineering Ltd | 103,104,115,116,GIDC, Kerala, Bavla Bagodara Road, Tal: Bavla, Dist: Ahmedabad | Ahmedabad | 380051 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Mistri Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physically obsrved ok. check the igbt and rectifier section ok. but busbar broken observed. so change the input ls busbar and power up the drive. give a run command with a motor condition ok working satisfactory. | Repair |  | 9- Service Validated | 2023-09-25 15:25 | =S= Consig Fill up 226034116 |  | 60 | INR | 60 | Industrial Automation Ops
WO-11224947 | 103850013 | 2023-09-07 21:16 | 2023-09-07 |  | 2023-09-07 14:55 | ATV310HU22N4E | ATV310HU22N4E | ATV310HU22N4E | 8B2308724063 | ATV310HU22N4E 8B2308724063 Qty:1 P: Not working Ecosys Efficiencies Pvt Ltd B 40 Nandkishore Indl Estate Near Paper Box Off Mahakali Caves Road Andheri-E Mumbai Mumbai-400093 Maharashtra India. Contact Person: Mrs Roopam, 9892049856 | 2023-09-07 | 2023-09-08 14:23 | No | Warranty | Ecosys Efficiencies Pvt. Ltd. | B-40, Nandkishore Industrial Estate, Near Paper Box, Off Mahakali Caves Rd, Andheri-E, | Mumbai | 400093 | Maharashtra | India FS ED&I CSP West Team R P Electrical Mumbai | Digambar Vishe R P Electrical Mumbai | R P Electrical | Checked ATV310H22N4E for not working issue. Given supply to check and drive turn ON. So connected motor of 1 HP to check further. Motor run properly. No issue found. Drive found Ok. | Repair |  | 9- Service Validated | 2023-09-08 14:28 |  |  | 15 | INR | 15 | Industrial Automation Ops
WO-11229410 | 103859714 | 2023-09-08 16:55 | 2023-09-08 |  | 2023-09-08 13:02 | ATV630D37N4Z | ATV630D37N4Z | ATV630D37N4Z | 88220888019 | Address DelhiJal board baba colony, Burari, near shamshaan ghat 110036, Delhi Delhi, India VFD not working ATV630D37N4Z : 2, 88220888019 | 2023-09-08 | 2023-09-12 10:29 | No | Warranty | Macro Cosmic Engineers PVT. LTD. | DelhiJal board baba colony, Burari, near shamshaan ghat null | Delhi | 110036 | Delhi | India FS ED&I CSP North Team Saffron Automation Delhi | Ashok Bhati_Saffron Automation Delhi | Saffron Automation(18001) | Check the drive and found drive static test is ok . After providing the input supply drive power up and show NLP fault. We change the control card and check the drive on load and found vibration in motor. Test for diagnostic and found IGBT not ok with motor. We replace the faulty drive with new. | Repair |  | 9- Service Validated | 2023-09-12 18:12 |  |  | 32 | INR | 32 | Industrial Automation Ops
WO-11229489 | 103846529 | 2023-09-08 21:05 | 2023-09-08 |  | 2023-09-08 13:35 | HMIET6400 | HMIET6400 | HMIET6400 | HL2305210100120 | HMIET6400 HL2305210100120 Qty:1 P: Touch screen failure VINAYAKA CONTROLS AND INSTRUMENTATION No 55,Annaporneshwari layout, Karihobanahalli main road, Nagasandra post,Bangalore Urban-560058 pno:8904040473 | 2023-09-08 | 2023-09-13 11:50 | No | Warranty | Vinayaka Controls & Instrumentation | Peenya 2nd Stage 10th Main Road, Balajinagar Bangalore Karnataka 560 058 | Bangalore | 560058 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | MANOJ GANESAN SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | I had visited the site and checked the customer reported the problem found was HMI display touch is not working we given the 24v DC touch is not working so We had zvo booked for the replacement | Repair |  | 9- Service Validated | 2023-09-15 07:55 |  |  | 35 | INR | 35 | Industrial Automation Ops
WO-11229649 | 103880966 | 2023-09-08 18:35 | 2023-09-11 | we have observed the DO's. DO Modules output working okay as per the system. during working I/O Status shows red indication. we have explained the I/O red indication status details as per the manual guidelines. | 2023-09-08 14:30 | BMXDDO1602 | BMXDDO1602 | BMXDDO1602 | 8B224003495 | DOP: 7/11/2022 BMXDDO1602 8B224003495, 8B224003494, 8B224003415, 8B224003489 P: All the DO modules gives error/fault red indication but operates satisfactorily as required. Magesh +919962633359 Spinmax Tyres Pvt Ltd 333,334 & 335 Kandwada Village Rd, Near Chevella, Telangana 501503 | 2023-09-08 | 2023-09-12 16:05 | No | Warranty | Spinmax Tyres Pvt Ltd | 333,334 & 335 Kandwada Village Rd, Near Chevella, null | K.V.Rangareddy | 501503 | Telangana | India FS ED&I CSP South Team ENERPRO ENGINEERING SOLUTIONS Vijayawada | Makineni Jayashankar ENERPRO ENGINEERING SOLUTIONS VIJAYAWADA | Enerpro Engineering Solutions - 500012682 | DO Modules showing red indication. | Repair |  | 9- Service Validated | 2023-09-12 16:10 |  |  | 243 | INR | 243 | Industrial Automation Ops
WO-11232782 | 103793943 | 2023-09-09 15:27 | 2023-09-09 |  | 2023-09-09 10:02 | ATS22D75Q | ATS22D75Q | ATS22D75Q | 8B2313804089 | ATS22D75Q 8B2313804089 Qty:1 P: Display issue Hytech Private Limited Subodh Kumar Biswal 119A, Mancheswar Industrial Estate, Bhubaneswar 7008663575 | 2023-09-09 | 2023-09-09 18:40 | No | Warranty | Hytech Pvt Ltd | PLOT NO-119A, MANCHESWAR INDUSTRIAL AREA | BHUBANESWAR | 751010 | Odisha | India FS ED&I CSP East Team UNIVERSAL ELECTRIC POWER SOLUTION BHUBANESWAR | RAMESH PRABHAT_UNIVERSAL ELECTRIC POWER SOLUTION BHUBANESWAR | Universal Electric Power Solution(500012032) | issue resolved at site | Repair |  | 9- Service Validated | 2023-09-09 18:44 |  |  | 18 | INR | 18 | Industrial Automation Ops
WO-11246967 | 103951590 | 2023-09-12 15:22 | 2023-09-12 |  | 2023-09-12 12:29 | Modicon X80 | BMXCPS4002H | BMXCPS4002H | 8B185100980 | Fwd: Faulty Power Supply, Case: 101123230, [ | 2023-09-12 | 2023-09-21 14:44 | No | Warranty | Oriental Automation Systems Pvt. Ltd | Shree Sai Sukrutha Complex, Door#181, 2nd Floor, Opposite to BDA Complex, Nagarbhavi 2nd Stage, Outer Ring Road, | Bangalore | 560072 | Karnataka | India FS ED&I CSP South Team Vamtech Energy Solutions Private Limited Bengaluru | BalaMurugan Venkadaswamy Vamtech Energy Solutions Private Limited Bengaluru | VAMTECH Energy Solutions (P) Limited | Being we checked and giving supply the device client power on and checked any flash over or any physical damage will be supplied same device as per warranty basis Pradeep pradeep@09aspl.com | Repair |  | 9- Service Validated | 2023-09-21 15:02 | Hi Team, Material booked zfre Zvo : 226056781 |  | 0 | INR | 0 | Industrial Automation Ops
WO-11247054 | 103924404 | 2023-09-12 15:38 | 2023-09-12 |  | 2023-09-12 13:11 | LXM26DU10M3X | LXM26DU10M3X | LXM26DU10M3X | P10WXH232201296 | Complaint for LXM26DU10M3X 22/8/2022 LXM26DU10M3X serial number P10WXH232201296 | 2023-09-12 | 2023-09-18 15:44 | No | Warranty | V Packaging Solutions | Garhi Chaukhandi, Sec-67,Noida, GB Nagar, | Noida | 201301 | Uttar Pradesh | India FS ED&I CSP North Team Saffron Automation Delhi | Deepak Pal_Saffron Automation Delhi | Saffron Automation(18001) | Check the LXM servo Drive and found static test is ok with PA+. Give single phase input supply drive is power up but blank display. Try to reset the drive and found keypad also not working. We replace the faulty drive with new. | Repair |  | 8- Service Completed | 2023-09-18 17:14 |  |  | 18 | INR | 18 | Industrial Automation Ops
WO-11247627 | 103954793 | 2023-09-14 11:17 | 2023-09-12 |  | 2023-09-12 14:57 | ATS22C14Q | ATS22C14Q | ATS22C14Q | 8B2201864116 | RE: Schneider Make SOFT STARTER ATS22C14Q -8B2201864116 [ thread::0DbnvzLfcEyqCQlLlKdzcz4:: ] | 2023-09-12 | 2023-09-27 17:03 | No | Warranty | Water Treatment Plant | NEAR AIIMS WATER TREATMENT PLANT ,KASOL SADAR null | Bilaspur | 174012 | Himachal Pradesh | India FS ED&I CSP North Team Sharma Electric Works Chandigarh | Karnail Singh Sharma Electric Chandigarh | Sharma Electric works(1003) | Checked the soft starter found SSCR Error due to Y pole By Pass contactor Short. Hence faulty need replacement. As per telephonic conversation with customer he will inform us on saturday for site visit. ATS22C14Q - 1 Nos. email : info.chd@reckersautomation.com | Repair |  | 8- Service Completed | 2023-09-27 17:13 |  |  | 125 | INR | 125 | Industrial Automation Ops
WO-11248068 | 103961506 | 2023-09-12 17:53 | 2023-09-12 |  | 2023-09-12 17:16 | XCMD2110L1 | XCMD2110L1 | XCMD2110L1 |  | DOP: 26/11/2022 XCMD2110L1 Qty- 02 NO'S P: No Signal Passing Sun Manufacturing Solutions No.371 & 372, 10th cross road 4th phase Peenya Indl. Area, Bangalore-560058 Mr. Arun Mob No. : 8884559336 | 2023-09-12 | 2023-09-19 15:24 | No | Warranty | Pooja Power Products (1385) | 371 & 372, First floor, 10th cross, 4th phase, Penya industrial area null | Bangalore | 560055 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | C Gunasekaran_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | As per our site visit,we checked customer having problem with limit switch and that product not handling by schneider now,so we unable to arrange the replacement. | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-19 22:30 |  |  | 35 | INR | 35 | Industrial Automation Ops
WO-11251813 | 103991571 | 2023-09-13 12:55 | 2023-09-13 | We have observed the TV310 VFD DISPLAY NOT COMING. We have checked the input and Ground values. observed within the range. | 2023-09-13 10:47 | ATV310H075N4E | ATV310H075N4E | ATV310H075N4E | 8B2242065199 | ATV310H075N4E 8B2242065199 NO DISPLAY 8074756598: IMRAN Badsha immu0473@gmail.com MUBARAK STOME EXPERT HN-3-223 / 4, NANDYAL Betamcherla Andhra Pradesh 518599 | 2023-09-13 | 2023-09-15 19:16 | No | Warranty | Mubarak Stone Exports | HN-3-223 / 4, NANDYAL Betamcherla null | KURNOOL | 518599 | Andhra Pradesh | India FS ED&I CSP South Team ENERPRO ENGINEERING SOLUTIONS Vijayawada | SK SIRAJUDDIN_ENERPRO ENGINEERING SOLUTIONS VIJAYAWADA | Enerpro Engineering Solutions - 500012682 | VFD NOT WORKING | Repair |  | 9- Service Validated | 2023-09-15 19:20 |  |  | 136 | INR | 136 | Industrial Automation Ops
WO-11253396 | 103994670 | 2023-09-13 17:10 | 2023-09-13 |  | 2023-09-13 14:23 | ATV340D30N4E | ATV340D30N4E | ATV340D30N4E | 40503008822857000 | Complaint no Required ATV340 30 KW VFD - APCO BANDRA ATV340D30N4E 40503008822857012 | 2023-09-13 | 2023-09-14 16:49 | No | Warranty | Apco infratech pvt ltd | Bandra Reclamation, Opposite MSRDC office next to Lilavati Hospital | Mumbai | 400050 | Maharashtra | India FS ED&I CSP West Team R P Electrical Mumbai | Digambar Vishe R P Electrical Mumbai | R P Electrical | Checked ATV340D30N4E of SCF3. Took thyristor test found Ok. Disassemble the drive to check internally. No physically damage can be seen on the power board and control card. Suspected control cord issue. so replace the control cord with new control cord. Turn on the drive. Loaded parameter. Took trial found working Ok. | Repair |  | 9- Service Validated | 2023-09-14 16:54 |  |  | 26 | INR | 26 | Industrial Automation Ops
WO-11253397 | 103992482 | 2023-09-15 12:57 | 2023-09-13 |  | 2023-09-13 14:24 | PFXGP4402WADW | PFXGP4402WADW | PFXGP4402WADW | 138814B368806 | PFXGP4402WADW 138814B368806 DOM: (11/21) Qty: 1 P: Display fault Roots industries India Pvt Ltd Automotive Division Kadhirinaickenpalayam Road , Coimbatore - 641017 Kalees waran M 9600902745 | 2023-09-13 | 2023-09-19 18:48 | No | Warranty | Roots Industries India Ltd-Horn Division | Thoppampatty, Kathirnaickenpalayam Road | Coimbatore | 641017 | Tamil Nadu | India FS ED&I CSP South Team Power Pro Engineering Services Coimbatore | KV ARUNKUMAR_POWER PRO ENGINEERIG SERVICES COIMBATORE | Powerpro Engineering Services | WE HAVE VISTED THE SITE AND INSPECTED WE FOUND TOUCH DISPLAY COLOUR BLUR ISSUE DUE TO INTERNAL HARDWARE ISSUE WE HAVE ARRAGING FOR FREE REPLACEMENT FOR THIS AND COLLECTED THE DETAILS AND INFORMED TO CUSTOMER | Repair |  | 9- Service Validated | 2023-09-19 18:50 |  |  | 21 | INR | 21 | Industrial Automation Ops
WO-11253695 | 103996763 | 2023-09-13 17:58 | 2023-09-13 |  | 2023-09-13 16:19 | ATV310HU15N4E | ATV310HU15N4E | ATV310HU15N4E | 8B2250407060 | Complaint for ATV310HU15N4E 8B2250407060 | 2023-09-13 | 2023-09-16 17:30 | No | Warranty | Jagson India | near bmg mall, Khasapura PALI NARNAUL ROAD | Rewari | 123401 | Haryana | India FS ED&I CSP North Team Saffron Automation Delhi | Yavnish Tyagi Saffron Automation Delhi | Saffron Automation(18001) | Check the drive and found drive have static test is ok. After providing the input supply drive not show display. We replace the faulty drive with new. Mail Id. sales.starksolutions@gmail.com | Repair |  | 9- Service Validated | 2023-09-16 18:04 |  |  | 128 | INR | 128 | Industrial Automation Ops
WO-11253764 | 104000707 | 2023-09-13 17:28 | 2023-09-13 | product is needed to be replaced .ATV320U22N4C - 01Nos | 2023-09-13 16:47 | ATV320U22N4C | ATV320U22N4C | ATV320U22N4C | HL2249814339 | Complaint for ATV320U22N4C Sr No-(21)HL2249814339 2 DRIVES . | 2023-09-13 | 2023-09-18 11:39 | No | Warranty | SAHIL INDUSTRIES | plot no B-90, 5 STAR MIDC KAGAL, HALSAVADE, TAL- HATKANGALE | KOLHAPUR | 416216 | Maharashtra | India FS ED&I CSP West Team Alliance Controls Pvt Ltd Pune | Rohit Srivastav_Alliance Controls Pvt. Ltd | Alliance Controls Pvt. Ltd. (7966) | We visited at site & done as per below following point :- (1) We checked cold test and found IGBT section ok with respect to PA+/PC- and thyristor section L1 & L2 open with respect to PA+ & ok with respect to Pc- .(2) Given 3 ? supply 415VAC and found display ON & NLP fault on display . We checked control 24VDC & 10VDC and found ok . Power DC checked found 591.2VDC (3) Taken somove backup file in it we found power ON time :- 515Hr , Motor run time :- 12Hr and last error found supply under voltage fault .(4) We open VFD to checked burnt mark or damage marks in it we found burnt marks near IPM section .(5) Attached photographs with this SIR .(6) As per discussion with Mr. Kiran Borse Sir this product is needed to be replaced .ATV320U22N4C - 01Nos | Repair |  | 9- Service Validated | 2023-09-18 11:40 | =S= Consig Fill up 226056917 |  | 233 | INR | 233 | Industrial Automation Ops
WO-11253889 | 104003223 | 2023-09-13 17:36 | 2023-09-13 |  | 2023-09-13 17:32 | ATV320D15N4C | ATV320D15N4C | ATV320D15N4C | HL2310766057 | VFD NOT WORKING | 2023-09-13 | 2023-09-14 10:11 | No | Warranty | PSP PROJECTS | ProjectUdhyan Marg, Behind Hcg Hospital, Mithakhali Six Road | AHMEDABA | 380009 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Mohammad Aasif Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physically observed ok. check the igbt and rectifier but l1 l3 short with pc- check the pa+ and pb observed ok. also l1 and l3 short observed. check the runtime = 2h, ontime = 67h, fault motor short ckt, in running condition. acc = 1.08 rcc = 0.8 sec , check the input supply ry = 401 . 4b = 400 , br = 403v , pe = 233.1v, ve =1.0 observed. check the motor resistance ry = 0.6y, yb =0.6 br = 0.r, re 4e be = ol observed. application hoisting DBR 6kw ,40 r, open the drive for primary inspection but at power board r373 resistance burnt oberved. customer use drive input side 25a mcb ( schneider ) take a panel photograph motor connection photo and somove file for further action. further action taken by schneier. | Repair |  | 8- Service Completed | 2023-09-18 10:12 |  |  | 17 | INR | 17 | Industrial Automation Ops
WO-11256811 | 104001926 | 2023-09-14 10:06 | 2023-09-14 | Hence, This case is closed. | 2023-09-14 09:28 | ATV320U11N4C | ATV320U11N4C | ATV320U11N4C | HL2308784139 | 1. ATV320U11N4C SR.NO -HL2308784139 Qty: 1 P: VFD has an ON/OFF Problem. 2. ATV320U55N4C SR.NO- HL2307083108 Qty : 1 P: VFD has an ON/OFF Problem. Excellent Handling Systems Private Limited PLOT NO PAP-W -116/117 CHAKAN MIDC AREA PHASE 2 VARALE CHAKAN TAL KHED PUNE - 410501 Contact person- Ms.Swati Thakare (7972122339) | 2023-09-14 | 2023-09-14 12:00 | No | Warranty | Excellent Handling Systems Private Limited | PLOT NO PAP-W -116/117 ,CHAKAN MIDC AREA, PHASE 2 VARALE CHAKAN TAL KHED | PUNE | 410501 | Maharashtra | India FS ED&I CSP West Team Alliance Controls Pvt Ltd Pune | Shmabhu Bone_Alliance Controls Pvt. Ltd | Alliance Controls Pvt. Ltd. (7966) | (1) Visited on site & checked VFD in cold test , found it's Reetifier & IGBT section Ok with respect to PA/+ & PC/- Terminal .(2) Applied 3 phase to drive Input , that before first checked cable tightness of VFD & found that PO Terminal screw in loose condition . It tightness properly & then checked VFD found it in ready status . No 'NLP' message showing on display . Also taken trial with no load , found drive working Ok . There is no problem observed with drive . Hence, This case is closed. | Repair |  | 9- Service Validated | 2023-09-14 16:01 |  |  | 7 | INR | 7 | Industrial Automation Ops
WO-11259260 | 104005938 | 2023-09-15 15:10 | 2023-09-14 |  | 2023-09-14 15:54 | ATV930D75N4 | ATV930D75N4 | ATV930D75N4 | 4023700JM225101026 | COMPLAINT FORM_CANDOUR ATV930D75N4 4023700JM225101026 Invoice Date - 19-04-2023 | 2023-09-14 | 2023-09-16 16:51 | No | Warranty | CANDOUR TECHNOLOGIES | MAIN DELHI ROHTAK ROAD, VILLAGE JAKHODA | Bahadurgarh | 124507 | Haryana | India FS ED&I CSP North Team Saffron Automation Delhi | Yavnish Tyagi Saffron Automation Delhi | Saffron Automation(18001) | Check the drive and found drive static test and open from PC- to V terminal. Dis-assemble the drive and flash on IGBT and rectifier unit and snubber board. Control card and Power card are ok. Open the fan assembly from Drive and found duct and heat sink is completely choke. Drive installation condition and last error/fault was ignored. We replacement cannot be provided, hence reject the drive and close the complete. Customer not signature the report. Mail Id. accounts1@balajiswitchgears.com | Repair |  | 8- Service Completed | 2023-09-16 17:39 |  |  | 64 | INR | 64 | Industrial Automation Ops
WO-11264272 | 103965497 | 2023-09-15 11:57 | 2023-09-15 |  | 2023-09-15 11:09 | ATV610D90N4 | ATV610D90N4 | ATV610D90N4 | 4001600JM22150299 | Dear Sir Please find the attached complaint registration form and VFD ATV610D90N4 4001600JM221502996 | 2023-09-15 | 2023-09-16 10:05 | No | Warranty | ACCUMAX LAB DEVICES | 194/6/2, DANTALI INDUSTRIAL ESTATE, GOTA-VADSAR ROAD DANTALI null | Gandhinagar | 382721 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Ritesh Prajapati_Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physicallly observed ok. SAFF obsered on the drive. remote control and clean ribbon cable power board and control card with help of cleaner trial taken drive stuck rdy. afrer 15 min drive trip on scf1 motor short ckt fault. recycle the power problem remain same scf1 after 2 to 3 recycle main supply rdy. install new control card and paste programe free replacement of the control card. replace from asc stock. | Repair |  | 9- Service Validated | 2023-09-18 10:07 | =S= Consig Fill up 226060586 |  | 50 | INR | 50 | Industrial Automation Ops
WO-11264372 | 104036361 | 2023-09-15 12:23 | 2023-09-15 |  | 2023-09-15 12:06 | ATV630D90N4 | ATV630D90N4 | ATV630D90N4 | 4005600JM22320018 | service compliant-vanitec 4005600JM223200186 ATV630D90N4 | 2023-09-15 | 2023-09-20 11:48 | No | Warranty | Vanitec | 183, KUTCHERY ROAD EXTENSION, VALIYAMPET, Vaniyambadi | Vaniyambadi | 635751 | Tamil Nadu | India FS ED&I CSP South Team Star Automations Chennai | Ezhilarasan k Star Automations Chennai | Star Automations | Problem reported by customer : Internal error 8 occurring Visited the site and checked the drive ATV630D90N4 physically and it was good. Module test was taken from the drive both input and output values are noted. Somove backup was took from the drive we just dismantle and reassemble the control card section. Again was facing a issue on control card terminal there was some internal error. As per manual rectification we need to change control card terminal this changes are done as like observation purpose. Control card need to be replace and fault HMI we suggest customer to send the courier. | Repair |  | 9- Service Validated | 2023-09-23 16:48 |  |  | 446 | INR | 446 | Industrial Automation Ops
WO-11264542 | 104038420 | 2023-09-15 14:53 | 2023-09-15 |  | 2023-09-15 12:48 | ATV340D18N4E | ATV340D18N4E | ATV340D18N4E | 4050100HL204233010 | INTERNAL ERROR21 IN SCHNIDER MAKE VFD ATV340D18N4E 18.5 KW 25 HP E ATV340D18N4E 4050100HL204233010 | 2023-09-15 | 2023-09-16 12:13 | No | Warranty | ECO MECHATRONICS AUTOMATION | Plat No. 6/D And 10/C Sector-B Sanwer Road | Indore | 452015 | Madhya Pradesh | India FS ED&I CSP West Team ABR Technical Service Indore | Lalu Sen_ABR Tecneical Services Indore | ABR Technical Services (9574) | Reached at site and checked (at panel builder office) as per customer VFD show ?error 21? so we collect VFD for testing purpose checked VFD at office :- we checked its IGBT/ rectifier section (value noted ) then giving 3 phase supply and found its display showing internal error 21 ? then we check PA to PC voltage :- 600VAC then we remove control card cleaning and reinstalled control card and again giving 3 phase supply but found same fault showing and as per DOM VFD out of warranty so we required distribution invoice but customer not provide distribution invoice so product is to out of warranty so now we are close this case . We collected so move file :- 1. run time :- 7028984 second (81 days) 2.Power ON time :- 41608432 second (481 days) 3.Last fault history :- internal error 21 4 . ACC / DCC :- 3 sec As per DOM VFD out of warranty so we are close this case. | Repair |  | 9- Service Validated | 2023-09-18 12:14 |  |  | 0 | INR | 0 | Industrial Automation Ops
WO-11264565 | 104055261 | 2023-09-15 18:09 | 2023-09-15 |  | 2023-09-15 12:54 | ATV610C16N4 | ATV610C16N4 | ATV610C16N4 | N222230051 | Re: Sr No - N2222300510 , ATV610C16N4, Case: 103618171, [ thread::JtAoaBxncQmQO7qYgu8h-j4:: ] | 2023-09-15 | 2023-09-28 16:24 | No | Warranty | Aarti Green Tech Ltd | Industrial Area model Township Plot #5 Phase 1 Sector 30 B | Rohtak | 124001 | Haryana | India FS ED&I CSP North Team Saffron Automation Delhi | Deepak Pal_Saffron Automation Delhi | Saffron Automation(18001) | Check the drive and found drive static test ok. Powered up the control card by external 24v Dc and found ok. Dis-assemble the drive and found filter board fuse open and flash on snubber board and power board is not visible flash. Environment condition its dusty and humidity. We replace the faulty spare with new. Now drive is working ok. We suggest to customer please improve the site condition otherwise next time found same condition we not consider in warranty. | Repair |  | 8- Service Completed | 2023-09-28 18:10 |  |  | 114 | INR | 114 | Industrial Automation Ops
WO-11265022 | 104063665 | 2023-09-20 11:02 | 2023-09-15 | NA | 2023-09-15 15:53 | 140CPU67160 | 140CPU67160 | 140CPU67160 | 21070914438 | Tata Steel Limited - Hooghly Met Coke Division Kindly release a WO under assessment-Inspection category. Product reference - Quantum CPU part code 140CPU67160 S/N-21070914438 Communication & Module Healthiness check requirement. Site details: Tata Steel Limited - Hooghly Met Coke Division, Haldia Oil Refinery, Patikhali - Haldia, West Bengal- 721606 104063665 Contact Person: Mr. Soumyajit Basak, M: 9262290349 Customer mail ID : soumyajit.basak@tatasteel.com | 2023-09-15 | 2023-09-26 16:00 | No | Commercial Action - Service Ops | TATA Steel Ltd | TATA Steel Ltd HMC Division Pathikhali, | Haldia | 721606 | West Bengal | India FS ED&I CSP East Team B.D Electroservices Kolkata | RAHUL RAY_B.D Electroservices Kolkata | B.D Electroservices(500017330) | During the site visit i have tested CCS CCR WT LCR 182 row 1 3 4 and which feeder earth pit also test. After testing the electronic earthpit found all earthpit averge value is greater then 1 OHm so requested to customer to solve the earthing issue. | Assessment/ Inspection | Data Collection | 8- Service Completed | 2023-09-26 11:28 |  | Safety Instruction to our FSR: 1. Minimum 2 FSRs required for the job, if; a. Job activity is more than 4 hrs. b. Need to manually lift any part, box or other object more than 18 kgs (maximum limit with two person is 36 kgs) c. MV break fix call for resolution d. MV Preventive maintenance e. For LV Preventive maintenance if breaker is greater than/equal to 800 amps 2. Apply LOTO to deenergize and isolate equipment before starting work (Energized work is limited to only voltage and current measurements, troubleshooting and diagnostic testing) 3. Risk Assessment to control hazards and wear required PPEs 4. Apply withdrawal rights if required | 127 | INR | 127 | Industrial Automation Ops
WO-11275098 | 104079595 | 2023-09-18 13:27 | 2023-09-18 |  | 2023-09-18 10:14 | ABL2REM24100K | ABL2REM24100K | ABL2REM24100K | 8A-2022-W25 | Complain ABL2REM24100K) 8A-2022-W25 | 2023-09-18 | 2023-09-18 16:19 | No | Warranty | SHIVAM ELECTRIC CO | 1728 / G/F/ 04,SURVEY NO : 2879, VADA POLE, NR HAJIRA NI POLE, KHADIA, AHMEDABAD | Ahmedebad | 380001 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Mistri Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physically osberved ok. ABL2REM24100K SR NO : 8A2021W36 observed as per customer smps not working. so we open the front cover and checked the fuse ok. so we open the pcb but no any flashing observed. so dust observed at fan and pc band body. so we give the supply and checked dl u found 24 v dc. so as per sr no out of warranty so no replacement. | Repair |  | 8- Service Completed | 2023-09-18 16:19 |  |  | 15 | INR | 15 | Industrial Automation Ops
WO-11276856 | 104086008 | 2023-09-18 13:27 | 2023-09-18 |  | 2023-09-18 12:38 | ABL2REM24100K | ABL2REM24100K | ABL2REM24100K | 8A2222W12 | ABL2REM24100K, 3606481277473, 8A 2222 W12, No Output | 2023-09-18 | 2023-09-20 14:24 | No | Warranty | Krishna Electricals | Shop no. 1, Gali no. 4A, Krishna Colony Opp. sec 25, | Faridabad | 121004 | Haryana | India FS ED&I CSP North Team Saffron Automation Delhi | Deepak Pal_Saffron Automation Delhi | Saffron Automation(18001) | Check the power supply and found power supply have output issue. We replace the faulty power supply with new. Mail Id. krishyadav1989@gmail.com | Repair |  | 8- Service Completed | 2023-09-20 14:24 |  |  | 48 | INR | 48 | Industrial Automation Ops
WO-11277351 | 104091944 | 2023-09-18 17:14 | 2023-09-18 |  | 2023-09-18 16:37 | ATV310HU30N4E | ATV310HU30N4E | ATV310HU30N4E | 8b2229382143 | ATV310HU30N4E 8b2229382143 NOT WORKING | 2023-09-18 | 2023-09-20 09:58 | No | Warranty | Maven Automation | Plot No. 298, Road No. 4, Kathwada GIDC, | Ahmedabad | 382430 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Mistri Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physically observed okl check the igbt and rectifer section ok. but poweer capacitor leakage observed . open the drive for primary inspection but no any short ckt observed. check the runtime : 4.68 ontime : 48.28 acc 3.0 dcc 3.0 fault f030 f017 application : boaster application. drive damage due to the electrical voltage . only onetime free replacement for customer satisfaction. | Repair |  | 9- Service Validated | 2023-09-20 09:59 | =S= Consig Fill up 226070530 |  | 15 | INR | 15 | Industrial Automation Ops
WO-11279306 | 104092528 | 2023-09-19 10:27 | 2023-09-19 |  | 2023-09-19 10:05 | LXM32AD72N4 | LXM32AD72N4 | LXM32AD72N4 | 322402392303.03.22 | Servo drive shows alarm 7701 LXM32AD72N4 Srn.-3224023923, DOM-03.03.22 | 2023-09-19 | 2023-09-21 09:53 | No | Warranty | Crust n Crump Food innovation | Block no.32, Kinfra small Industrial Park 4Nellad Muvattupuza null | ERNAKULAM | 686669 | Kerala | India FS South2 ED&I CSP PrinterPeople Cochin | Vysakht PrinterPeople Cochin | PRINTER PEOPLE-COCHIN | site visit done servo drive panel message alarm7701 unit placed in non dusty area no arc or flash over found in drive and wiring. Input is normal supplier is sending replacement as per customer. need clarity on that to intend. replacement handed over to customer representative . new seial no 360648216220 | Repair |  | 9- Service Validated | 2023-09-21 16:59 | Hi Team, Material booked zfre Zvo : 226071053 |  | 0 | INR | 0 | Industrial Automation Ops
WO-11279341 | 104032816 | 2023-09-19 18:54 | 2023-09-19 | During the earlier inspection, VFD was damaged due to an external issue. Based on the Sales approval booking the ZVO. | 2023-09-19 10:28 | ATV930D18N4 | ATV930D18N4 | ATV930D18N4 | 4023100JM221203339 | Request for WO creation for replacement of VFD drive | 2023-09-19 | 2023-09-20 12:34 | No | Warranty | GLOSTER CABLES LIMITED (GCL) | 5-3-372A, 2ND FLOOR, RASHTRAPATI RD, HYDER BASTI, SECUNDERABAD | SECUNDERABAD | 500003 | Telangana | India FS ED&I CSP South Team ENERPRO ENGINEERING SOLUTIONS Vijayawada | Makineni Jayashankar ENERPRO ENGINEERING SOLUTIONS VIJAYAWADA | Enerpro Engineering Solutions - 500012682 | VFD DISPLAY ISSUE | Repair |  | 9- Service Validated | 2023-09-21 07:54 |  |  | 213 | INR | 213 | Industrial Automation Ops
WO-11280101 | 104084490 | 2023-09-20 13:40 | 2023-09-19 |  | 2023-09-19 11:14 | ATV610D22N4 | ATV610D22N4 | ATV610D22N4 | 4001000jm231304463 | ATC610D22N4 drive complain 4001000jm231304463 ATV610D22N4 | 2023-09-19 | 2023-09-21 12:29 | No | Warranty | M/S-Shree Balaji Rice Mill | Sullar Gharat Road, Sullar | Sangrur | 148035 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | checked the vfd found SCF1 fault showing due to mouse cutted the wires . Hence faulty, email : id not provided by the customer. | Repair |  | 8- Service Completed | 2023-09-21 12:42 |  |  | 120 | INR | 120 | Industrial Automation Ops
WO-11280114 | 104086468 | 2023-09-19 20:12 | 2023-09-19 |  | 2023-09-19 11:27 | LXM32CD30N4 | LXM32CD30N4 | LXM32CD30N4 | 01.11.2021 | Service Engineer Visit Under Warranty LXM32CD30N4 01.11.2021 | 2023-09-19 | 2023-09-21 11:37 | No | Warranty | Bhala brothers | maujipur near radio station Fatwah null | Patna | 803201 | Bihar | India FS ED&I CSP East Team Vidya Enterprises Lucknow | Rana Ranjan_Vidya Enterprises Lucknow | Vidya Enterprises | As per customer complaint visited the site and check the servo drive display found FLT0771. Inspect the drive found heavy dust inside the servo drive. Check the supply found OK. Open the drive found flash over on board. Photo enclosed. We observe and found short circuit and some component are damage. Motor not check. As discuss with internal team due to heavy dust this case is escalated to Schneider | Repair |  | 8- Service Completed | 2023-09-21 11:37 |  |  | 0 | INR | 0 | Industrial Automation Ops
WO-11280224 | 104095433 | 2023-09-22 09:51 | 2023-09-19 |  | 2023-09-19 12:11 | ATV312HU40N4412 | ATV312HU40N4412 | ATV312HU40N4412 |  | ATV312HU40N4412 8B2048680023 Qty:1 P: No display in VFD and Motor not running. Dharma Munda Village: Nawatoli Block: Raidih Dist: Gumla State: Jharkhand Site Incharge: Firoz Minj Contact No: 9102075714 | 2023-09-19 | 2023-09-22 12:46 | No | Warranty | Firoz Minj Firoz Minj | Dharma Munda Village: Nawatoli Block: Raidih Dist: Gumla | Gumla | 835232 | Jharkhand | India FS ED&I CSP East Team UNIVERSAL ELECTRIC POWER SOLUTION BHUBANESWAR | Banty Kumar_UNIVERSAL ELECTRIC POWER SOLUTION BHUBANESWAR | Universal Electric Power Solution(500012032) | product out of warranty | Repair |  | 8- Service Completed | 2023-09-23 12:51 |  |  | 312 | INR | 312 | Industrial Automation Ops
WO-11280391 | 104095983 | 2023-09-20 13:41 | 2023-09-19 |  | 2023-09-19 13:09 | ATV930D30N4 | ATV930D30N4 | ATV930D30N4 | 4023300JM223210079 | ATV930D30N4 SR.NO. - 4023300JM223210079 Qty:1 P: Not getting power supply SANT FOODS PVT.LTD. # Village -Kahangarh Gharanchon Patran Pin code:-147105 Contact :- Mr. Rahul ji ji- 9501598000 | 2023-09-19 | 2023-09-30 13:07 | No | Warranty | SANT FOODS PVT.LTD. | # Village -Kahangarh Gharanchon Patran null | Patiala | 147105 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | checked the vfd found not power up due to flash over found on power board and dc board. hence faulty, replaced. VX4DCPD30N4 - 1 Nos. VX4PPD30N4 - 1 Nos. Email : id not provided by the customer | Repair |  | 8- Service Completed | 2023-09-30 13:54 |  |  | 140 | INR | 140 | Industrial Automation Ops
WO-11284977 | 104122495 | 2023-09-20 12:41 | 2023-09-20 |  | 2023-09-20 11:23 | ATS22C41Q | ATS22C41Q | ATS22C41Q | 21WX230748800 | 220 KW SOFT STARTER COMPLAINT ATS22C41Q 21WX2307488001 | 2023-09-20 | 2023-09-25 13:24 | No | Warranty | Nutral Powertech | Plot No. 7 - 8, Somnath Industrial | Ahmedabad | 382435 | Gujarat | India FS ED&I CSP West Team Anik Engineering Ahmedabad | Kashyap Mistri Anik Engineering Ahmedabad | Anik Engineering (554) | Visited the site and checked the product found physically observed ok. according to customer sscr fault in display we checked the continuty between l1 & l1 l2 & t2 l3 & t3 observed l2 t2 shorted. we open the soft starter and checked the relay observed relay y pole stuck. we checked t he all relay obsered physically ok but spartk observed on power contct. we replace the relay 3 Nos and trial taken working ok. give only one time free replacement. we suggest to customer please control t1f and earther soft starter body. customer not set parameter according to motor number plate. we check voltage on control card and terminal for customer satisfaction only one t ime free replacemnt. | Repair |  | 9- Service Validated | 2023-09-25 13:26 | 226078945 |  | 125 | INR | 125 | Industrial Automation Ops
WO-11286022 | 104155235 | 2023-09-20 17:49 | 2023-09-20 |  | 2023-09-20 16:46 | XB5AW33G1N | XB5AW33G1N | XB5AW33G1N |  | XB5AW33G1N : 110 VAC ILLUMINATED PB :10 NOS : NOT working in condition. Sl no 10-2020-W-11-2. Kindly check invoice at site Gadre Marine Export Private Limited MATERIALS PLOT NO. IP- 32 &IP- 33 Mangalore Special Economic Zone Bajpe,post& village Mangaluru Taluk, Dakshina kannada district Karnataka 574142 Prathiksha 7892528314 | 2023-09-20 | 2023-09-25 16:00 | No | Warranty | Gadre Marine Export Pvt Ltd | Plot #IT- 32 & IT-33 | Mangalore | 574142 | Karnataka | India FS ED&I CSP South Team SREE LAKSHMI ELECTRICAL SERVICES Bangalore | C Gunasekaran_SREE LAKSHMI ELECTRICAL SERVICES Bangalore | Sree Lakshmi Electrical Services - (500012533) | we had requested customer to send the defective to our, after checking the problem found was -A9KF71216-screw threading issue at 1&2 terminal, screw missing at 1 terminal. - A9KR11240- not getting trip thru test button. replacement done by alpha electricals. so we had arranged for the replacement and sent thru courier. | Repair |  | 9- Service Validated | 2023-09-25 20:55 |  |  | 250 | INR | 250 | Industrial Automation Ops
WO-11289196 | 104146537 | 2023-09-21 16:12 | 2023-09-21 |  | 2023-09-21 09:48 | ABLP1A24100 | ABLP1A24100 | ABLP1A24100 | 8A214701235 | LMW COMPLAINT REGISTRATION FORM 20092023 - REG., ABLP1A24100 - 1 NO SL NO. 8A214701235 | 2023-09-21 | 2023-09-25 13:02 | No | Warranty | Lakshmi Electrical Control Systems | 399, ARASUR, AVINASHI Road null | Coimbatore | 641407 | Tamil Nadu | India FS ED&I CSP South Team Power Pro Engineering Services Coimbatore | KV ARUNKUMAR_POWER PRO ENGINEERIG SERVICES COIMBATORE | Powerpro Engineering Services | WE HAVE VISITED THE SITE AND INSPECTE WE FOUND SMPS FOUND POWER ON ISSUE WE HAVE COLLECTED THE DETAILS FOR ARRAGING FOR FREE REPALCEMENT FOR THIS AND COLLECTED THE DEFECTIVE | Repair |  | 9- Service Validated | 2023-09-25 13:04 | Hi Team, Material booked zfre Zvo : 226082420 |  | 21 | INR | 21 | Industrial Automation Ops
WO-11290239 | 104059400 | 2023-09-21 14:43 | 2023-09-21 |  | 2023-09-21 13:06 | ATV610D22N4 | ATV610D22N4 | ATV610D22N4 | 4001000JM224106788 | ERVICE ENGINEER URGENTLY AT KANSAI NEROLAC HOSUR SITE Kindly arrange to depute the service Engineer for ATV610D22N4 VFD failure issue at Kansai Nerolac Hosur Site. Please find attached Sr. No. and photos, Please find below the link to download the supporting details ? https://we.tl/t-CEWA4xeoeD Channel partner: Electrocare India Pvt Ltd Invoice No: 9008297081/Dt: 21.10.2022 Sr No: 4001000JM224106788 Ref: ATV610D22N4 | 2023-09-21 | 2023-09-21 11:23 | No | Warranty | AC ELECTROMECH ENGINEERS | Plot No.E-17,SIPCOT Ind Complex, Phase-2,Expansion-2 KRISHNAGIRI null | HOSUR | 635001 | Tamil Nadu | India FS ED&I CSP South Team Vamtech Energy Solutions Private Limited Bengaluru | BalaMurugan Venkadaswamy Vamtech Energy Solutions Private Limited Bengaluru | VAMTECH Energy Solutions (P) Limited | Being communication issue its solved drive to PLZ Is solved Ganesh Email Id:mallaganesh@nerolac.com | Assessment/ Inspection | Data Collection | 9- Service Validated | 2023-09-22 11:26 | Assign to Vamtech |  | 45 | INR | 45 | Industrial Automation Ops
WO-11290389 | 104172942 | 2023-09-22 15:23 | 2023-09-21 |  | 2023-09-21 14:00 | ATS22C41Q | ATS22C41Q | ATS22C41Q | 88223822200 | Soft_Starter_Showing- OHF_Fault 882238222007 ATS22C41Q | 2023-09-21 | 2023-09-23 14:07 | No | Warranty | Shapoorji Pallonji And Co. Pvt.Ltd. | 95 MLD STP, Gausabad, Ramtirth Road | Amritsar | 143005 | Punjab | India FS ED&I CSP North Team Ananyaa Electricals LUDHIANA | Harwinder Singh Ananyaa Electrical Ludhiana | Ananyaa Electricals(P) | Checked the soft starter found Showing OHF Fault due to by pass contactor faulty. Hence faulty replaced. VY1F22E3220V - 1 Nos. email : sapan.sinha1@shapoorji.com | Repair |  | 8- Service Completed | 2023-09-23 14:09 |  |  | 150 | INR | 150 | Industrial Automation Ops
WO-11293859 | 104185246 | 2023-09-22 10:44 | 2023-09-22 | This is not manufacture issue. | 2023-09-22 09:47 | STBCPS2111 | STBCPS2111 | STBCPS2111 |  | DOP: 21/7/2022 STBCPS2111 Qty:1 P: Not Working Nish Techno Projects Pvt. Ltd. C20/2- Road No. 15, Hojiwala Industrial Estate, At: Vanz, Sachin-Palasana Road, Surat ? 394230 Mr.Sujoy Chakraborty(8866401846) Mr.Dharmesh Chavda(9909972815) sujoy@groupnish.com | 2023-09-22 | 2023-09-23 17:25 | No | Warranty | Nish Techno Projects Pvt. Ltd. | C20/2- Road No. 15 Hojiwala Industrial Estate At: Vanz ,Sachin-Plasana Road, | Surat | 394210 | Gujarat | India FS ED&I CSP West Team VARDHAMAN ELECTROSOFT Vadodara | MAHENDRA SINGH VARDHAMAN ELECTROSOFT Vadodara | VARDHAMAN ELECTROSOFT | we visited the site and check the CPS2111 . when we connect 24 volts there was no power . when we open it was burnt from inside . the reasone for this damage is sort circuit . | Repair |  | 8- Service Completed | 2023-09-23 17:26 |  |  | 60 | INR | 60 | Industrial Automation Ops
WO-11293894 | 104154859 | 2023-09-23 10:56 | 2023-09-22 |  | 2023-09-22 10:06 | ATV310HU55N4E | ATV310HU55N4E | ATV310HU55N4E | 8B2236523003 | Problem in VFD ATV310HU55N4E 8B2236523003 | 2023-09-22 | 2023-09-23 13:38 | No | Warranty | The Courtyard by Marriot | near AMBEDKAR PARK Rail Vihar Colony Phase 3rd Taramandal Nauka Vihar Road null | GORAKHPUR | 273017 | Uttar Pradesh | India FS ED&I CSP North Team Sunpower Systems Lucknow | Aman Khare_Sun Power Systems Lucknow | Sunpower Systems ( 7565 ) | VFD having communication issue, so we resolved , now VFD working fine . | Repair |  | 8- Service Completed | 2023-09-25 13:43 |  |  | 280 | INR | 280 | Industrial Automation Ops
WO-11293903 | 104187904 | 2023-09-23 15:02 | 2023-09-22 |  | 2023-09-22 10:13 | ATV310HU22N4E | ATV310HU22N4E | ATV310HU22N4E |  | DOP: 4/10/2022 ATV310HU22N4E Qty:1 P: DISPLAY ISSUE - NOTHING IS COMING ON DISPLAY BONY STONE COMPANY G-1-410A ROAD NO-6 IPIA NEAR GOMTI DHARM KANTA KOTA, Pincode - 324005 Bony Bansal 9829960438 | 2023-09-22 | 2023-09-28 16:07 | No | Warranty | BONY STONE COMPANY | G-1-410A ROAD NO-6 IPIA NEAR GOMTI DHARM KANTA null | Kota | 324005 | Rajasthan | India FS ED&I CSP North Team Sharma Electric Works Jaipur | Rajan Singh_Sharma Electric Jaipur | Sharma Electric Works | Checked the vfd found display not showing, Hence faulty replaced. ATV310HU22N4E - 1 nos Email : id not provided by customer . | Repair |  | 8- Service Completed | 2023-09-28 16:10 |  |  | 250 | INR | 250 | Industrial Automation Ops
WO-11311214 | 104278410 | 2023-09-27 12:55 | 2023-09-26 |  | 2023-09-26 17:58 | HMIGXU5512 | HMIGXU5512 | HMIGXU5512 | WX76960211160116 | Warning: Email body is too large and was truncated at 32 000 characters. Information may have been lost. P margin-top:0;margin-bottom:0; Schneider CC Team, Greetings from Coronet Engg. !!!!; Subject :: Silverton Pulp & Paper Pvt. Ltd., Muzaffarnagar- Product ::HMIGXU5512 _WX76960220850154 (HMI- D.O.M-2208); PROBLEM- Touch pad Hanging Issue/Touch pad NOT WORKING Today customer has complained HMIGXU5512 Show the Touch pad Hanging Issue/Touch pad Hanging Issue . You are requested to look in this matter and arrange to solve this issue ASAP as Its a process industry ? ? Checklist For Complaint Registration 1 Name Of Customer Silverton Pulp & Paper Pvt. Ltd. 2 Site Address PM1; 9 Th, KM Bhopa Road, Muzaffarnagar-251002, Uttar Pradesh, India E-Mail Id MOHAN@CORONET.IN 3 Name Of Contact Person At Site Mr.Vinod Kumar 4 Contact Phone / Mob. No: +919837281051 5 Defective Product Details HMIGXU5512 _WX76960220850154 (HMI- D.O.M-2208); 6 Nature Of Defect PROBLEM- Touch pad Hanging Issue 7 Shutdown Availability If Applicable Yes 8 Warranty Status Yes 9 Commissioned / Installed Date 2023 10 Serial No: Or Dom Of The Product WX76960220850154 (HMI- D.O.M-2208); 11 Name & Phone No: Of Person Registering The Complaint Mohan Sharma ( +91-9910050281) AS UNDER THE WARRANTY FOR REPAIR/ REPLACEMENT JOB, WE ARE REQUESTED TO CC TEAM PLEASE LOOK IN THIS MATTER AND ARRANGE TO SOLVE THIS ISSUE ASAP. Thanks for your patience and kind support as always !!!! ??????? ????? ?????, ???? ????? !!! ????? ?? ?? ?????? ? | 2023-09-26 | 2023-09-29 14:36 | No | Warranty | Silverton Pulp and Paper Mill Ltd | 9th KM, BHOPA ROAD,MUZAFFARNAGAR- 251001 | MUZAFFARNAGAR | 251001 | Uttar Pradesh | India FS ED&I CSP North Team Saffron Automation Delhi | Deepak Pal_Saffron Automation Delhi | Saffron Automation(18001) | Check the HMI and found physical condition is ok. Tested the touch panel screen and found operating currently and also performed the calibration test and found ok. We suggest the customer kindly capture a video of HMI hanging in future. Provide earthing to the panel. Mail id. mohan@coronet.in | Repair |  | 8- Service Completed | 2023-09-29 14:51 |  |  | 1 | INR | 1 | Industrial Automation Ops
WO-11173006 | 103592220 | 2023-08-29 11:10 | 2023-08-28 | There is no need to replace the switches. | 2023-08-28 14:30 | IN8401_N | IN8401_N | IN8401_N |  | Model : Zencelo switches--10 nos Invoice : 22 Nov 2022---radhika cables &switchgear Not operating Model : Zencelo switches--10 nos Invoice : 22 Nov 2022---radhika cables &switchgear Not operating Site : Ashwariyam Confort gold, Nr Khandoba Temple , Chichwad, Pune 411019 Rohan Paladey : 8698079147 | 2023-08-28 | 2023-09-01 11:44 | No | Warranty | Rohan Paladey | Ashwariyam Confort gold, Nr Khandoba Temple , Chichwad | Pune | 411019 | Maharashtra | India FS ED&I CSP West Team Alliance Controls Pvt Ltd Pune | Shmabhu Bone_Alliance Controls Pvt. Ltd | Alliance Controls Pvt. Ltd. (7966) | Remove only coverplate and resolved issue. There is no need to replace the switches. | Repair |  | 9- Service Validated | 2023-09-04 11:46 |  |  | 10 | INR | 10 | ENM HOME DISTRIBUTION
WO-11195218 | 103618077 | 2023-09-01 19:07 | 2023-09-01 |  | 2023-09-01 16:59 | ATV310HU15N4E | ATV310HU15N4E | ATV310HU15N4E | 2241268322 | Regarding VFD repair/ replacement Model ATV310HU15N4E QTY 01 NO SERIAL NO 8B2241268322 ISSUE - ERROR F015 | 2023-09-01 | 2023-09-16 19:19 | No | Warranty | Swornim boutique hotel pvt. Ltd. | Near Tangal Chowk Naxal | Kathmandu | 4460 | Bagmati | India FS ED&I CSP East Team Vidya Enterprises Lucknow | Rana Ranjan_Vidya Enterprises Lucknow | Vidya Enterprises | Yesterday Our Engineer Shubrat connected with customer and online support to them but drive display show F015. i. e. output phase loss. Disconnect the motor and closed the fault in drive setting and run the drive but no output voltage shows in drive. We rest the drive and perform the auto tuning but drive again show F015 fault. As discuss with Deepak sir Drive IGBT is faulty. So, replace the drive. We book the drive at dealer address and told to customer we delivered the drive at India border only after that they will clear the material from border. As discuss with customer they replaced the drive from his stock and once faulty drive delivered at border then we will delivered to them new drive at border. So this case is closed in system | Repair |  | 9- Service Validated | 2023-09-16 19:19 |  |  | 350 | INR | 350 | Industrial Automation